## Sheet1
Baseline: Average 22 to 26 degrees celcius
Floor | DEK Name | Equipment Name | No. of CRACs (Running) | No. of CRACs (N) | (N+1) | Cooling Cap (Kw) | Min Avg Temperature | Maximum Avg Temperature | Average Temperature
7F | 7-CRACRm-CRAC-01 | Main CRAC 7F-1 | 1 | 1 | N+1 | 105.48 | 25.5 | 26.6 | 25.9472
| 7-CRACRm-CRAC-02 | Main CRAC 7F-2 | 1 | 1 |  | 105.48 | 26 | 27.1 | 26.5342
| 7-CRACRm-CRAC-03 | Main CRAC 7F-3 | 1 | 1 |  | 105.48 | 26 | 27.1 | 26.6127
| 7-CRACRm-CRAC-04 | Main CRAC 7F-4 | 1 | 1 |  | 105.48 | 25.9 | 27 | 26.5516
6F | 6-CRACRm-CRAC-01 | Main CRAC 6F-1 | 1 | 1 | N+1 | 105.48 | 19.5 | 28 | 26.5629
| 6-CRACRm-CRAC-02 | Main CRAC 6F-2 | 1 | 1 |  | 105.48 | 24.3 | 27.7 | 26.4688
| 6-CRACRm-CRAC-03 | Main CRAC 6F-3 | 1 | 1 |  | 105.48 | 17 | 27 | 21.191
| 6-CRACRm-CRAC-04 | Main CRAC 6F-4 | 1 | 1 |  | 105.48 | 24.9 | 27.5 | 26.1913
| 6-DaHall 1-CRAC-01 | Aux. CRAC 6F-1 | 1 | 1 |  | 70.32 | 13.9 | 26.3 | 24.474
| 6-DaHall 1-CRAC-02 | Aux. CRAC 6F-2 | 1 | 1 |  | 70.32 | 14.1 | 26.1 | 24.5131
| 6-DaHall 1-CRAC-03 | Aux. CRAC 6F-3 | 1 | 1 |  | 70.32 | 14.8 | 26 | 24.6252
5F | 5-CRACRm-CRAC-01 | Main CRAC 5F-1 | 1 | 1 | N+1 | 105.48 | 24 | 25.5 | 24.8661
| 5-CRACRm-CRAC-02 | Main CRAC 5F-2 | 1 | 1 |  | 105.48 | 24.4 | 25.9 | 25.2212
| 5-CRACRm-CRAC-03 | Main CRAC 5F-3 | 1 | 1 |  | 105.48 | 24.5 | 26.4 | 25.2522
| 5-CRACRm-CRAC-04 | Main CRAC 5F-4 | 1 | 1 |  | 105.48 | 24.1 | 26 | 24.8441
| 5-DaHall 1-CRAC-13 | CF CRAC-#01 | 0 | 1 | Dedicated CRAC | 32.55 | 25.3 | 33.5 | 32.5988
| 5-DaHall 1-CRAC-14 | CF CRAC-#02 | 0 | 1 |  | 32.55 | 23.4 | 27.2 | 26.0237
| 5-DaHall 1-CRAC-01 | LG CRAC-#01 | 0 | 1 | Dedicated CRAC | 32.55 | 21.8 | 32.7 | 31.1019
| 5-DaHall 1-CRAC-02 | LG CRAC-#02 | 1 | 1 |  | 32.55 | 22.5 | 27.8 | 26.1375
| 5-DaHall 1-CRAC-03 | LG CRAC-#03 | 0 | 1 |  | 32.55 | 17.8 | 29.5 | 27.9365
| 5-DaHall 1-CRAC-04 | LG CRAC-#04 | 1 | 1 |  | 32.55 | 21.4 | 26.9 | 24.7035
| 5-DaHall 1-CRAC-05 | LG CRAC-#05 | 0 | 1 |  | 32.55 | 20.3 | 24.4 | 21.5622
| 5-DaHall 1-CRAC-06 | LG CRAC-#06 | 1 | 1 |  | 32.55 | 21.2 | 24.2 | 23.4274
| 5-DaHall 1-CRAC-07 | LG CRAC-#07 | 0 | 1 |  | 32.55
| 5-DaHall 1-CRAC-08 | LG CRAC-#08 | 0 | 1 |  | 32.55 | 18.4 | 99.5 | 22.3828
| 5-DaHall 1-CRAC-09 | LG CRAC-#09 | 0 | 1 |  | 32.55 | 18.4 | 25.1 | 23.9772
| 5-DaHall 1-CRAC-10 | LG CRAC-#10 | 0 | 1 |  | 32.55 | 17.7 | 29.2 | 21.6094
| 5-DaHall 1-CRAC-11 | LG CRAC-#11 | 0 | 1 |  | 32.55 | 21.2 | 25.6 | 22.483
| 5-DaHall 1-CRAC-12 | LG CRAC-#12 | 0 | 1 |  | 32.55 | 19 | 23.8 | 21.8755
| 5-DaHall 1-CRAC-15 | Aux. CRAC 5F-1 | 0 | 1 | Dedicated CRAC | 24.4 | 27.5 | 30 | 28.6699
| 5-DaHall 1-CRAC-16 | Aux. CRAC 5F-2 | 0 | 1 |  | 24.4 | 26 | 28.5 | 27.1018
4F | 4-CRACRm-CRAC-01 | Main CRAC 4F-1 | 1 | 1 | N+1 | 105.48 | 24.8 | 26 | 25.5658
| 4-CRACRm-CRAC-02 | Main CRAC 4F-2 | 1 | 1 |  | 105.48 | 24.6 | 25.8 | 25.3429
| 4-CRACRm-CRAC-03 | Main CRAC 4F-3 | 1 | 1 |  | 105.48 | 23.9 | 25.8 | 24.9473
| 4-CRACRm-CRAC-04 | Main CRAC 4F-4 | 1 | 1 |  | 105.48 | 24 | 25.7 | 24.9622
| 4-DaHall 1-CRAC-05 | Aux.E_CRAC 4F-1 | 1 | 1 |  | 65 | 26.1 | 28.3 | 27.2362
| 4-DaHall 1-CRAC-06 | Aux.E_CRAC 4F-2 | 1 | 1 |  | 65 | 24 | 26 | 24.5167
| 4-DaHall 1-CRAC-02 | Aux. CRAC 4F-1 | 1 | 1 | Dedicated CRAC | 16.3 | 23.5 | 26 | 24.534
| 4-DaHall 1-CRAC-03 | Aux. CRAC 4F-2 | 1 | 1 |  | 16.3 | 21 | 24.5 | 22.9177
| 4-DaHall 1-CRAC-04 | Aux. CRAC 4F-3 | 1 | 1 |  | 16.3 | 18 | 29.5 | 26.9536
| 4-DaHall 1-CRAC-01 | Aux. CRAC 4F-4 | 1 | 1 |  | 35 | 24 | 26 | 24.8555 | Not connected with FMS
Baseline: Average 30 to 70 % RH
Floor | DEK Name | Equipment Name | No. of CRACs (Running) | No. of CRACs (N) | (N+1) | Cooling Cap (Kw) | Min Avg Humidity | Maximum Avg Humidity | Average Humidity
7F | 7-CRACRm-CRAC-01 | Main CRAC 7F-1 | 1 | 1 | N+1 | 105.48 | 24.1 | 46.6 | 36.8759 |  | 7-1 Collecting integrated data
| 7-CRACRm-CRAC-02 | Main CRAC 7F-2 | 1 | 1 |  | 105.48 | 24.5 | 46.8 | 37.0041 |  | 7-2 Collecting integrated data
| 7-CRACRm-CRAC-03 | Main CRAC 7F-3 | 1 | 1 |  | 105.48 | 25.7 | 45.6 | 36.9845 |  | 7-3 Collecting integrated data
| 7-CRACRm-CRAC-04 | Main CRAC 7F-4 | 1 | 1 |  | 105.48 | 23.2 | 44.2 | 35.1567 |  | 7-4 Collecting integrated data
6F | 6-CRACRm-CRAC-01 | Main CRAC 6F-1 | 1 | 1 | N+1 | 105.48 | 22.8 | 73.8 | 37.2518 |  | 6-1,6-2 Collecting integrated data
| 6-CRACRm-CRAC-02 | Main CRAC 6F-2 | 1 | 1 |  | 105.48 | 22.8 | 53.2 | 37.1754 |  | 6-1,6-2 Collecting integrated data
| 6-CRACRm-CRAC-03 | Main CRAC 6F-3 | 1 | 1 |  | 105.48 | 37.3 | 66 | 49.8404 |  | 6-3,6-4 Collecting integrated data
| 6-CRACRm-CRAC-04 | Main CRAC 6F-4 | 1 | 1 |  | 105.48 | 24 | 47.5 | 40.0735 |  | 6-3,6-4 Collecting integrated data
5F | 5-CRACRm-CRAC-01 | Main CRAC 5F-1 | 1 | 1 | N+1 | 105.48 | 22.5 | 45.8 | 38.1955 |  | 5-1 Collecting integrated data
| 5-CRACRm-CRAC-02 | Main CRAC 5F-2 | 1 | 1 |  | 105.48 | 21.9 | 44.3 | 37.0747 |  | 5-2 Collecting integrated data
| 5-CRACRm-CRAC-03 | Main CRAC 5F-3 | 1 | 1 |  | 105.48 | 20.9 | 39.5 | 34.9621 |  | 5-3 Collecting integrated data
| 5-CRACRm-CRAC-04 | Main CRAC 5F-4 | 1 | 1 |  | 105.48 | 21.5 | 40.6 | 35.8811 |  | 5-4 Collecting integrated data
| 5-DaHall 1-CRAC-13 | CF CRAC-#01 | 0 | 1 | 1 | 32.55 | 25.8 | 31.6 | 26.3544 | Stand-by CRAC
| 5-DaHall 1-CRAC-14 | CF CRAC-#02 | 0 | 1 | 1 | 32.55 | 27.8 | 30.6 | 28.5075 | Stand-by CRAC
| 5-DaHall 1-CRAC-01 | LG CRAC-#01 | 0 | 1 | 1 | 32.55 | 24.4 | 31.6 | 25.3086 | Stand-by CRAC
| 5-DaHall 1-CRAC-02 | LG CRAC-#02 | 1 | 1 | 1 | 32.55 | 29 | 32.8 | 30.6905
| 5-DaHall 1-CRAC-03 | LG CRAC-#03 | 0 | 1 | 1 | 32.55 | 24.4 | 32.5 | 25.4504 | Stand-by CRAC
| 5-DaHall 1-CRAC-04 | LG CRAC-#04 | 1 | 1 | 1 | 32.55 | 28.6 | 32.8 | 31.682
| 5-DaHall 1-CRAC-05 | LG CRAC-#05 | 0 | 1 | 1 | 32.55 | 30.1 | 32.5 | 31.8392 | Stand-by CRAC
| 5-DaHall 1-CRAC-06 | LG CRAC-#06 | 1 | 1 | 1 | 32.55 | 30.7 | 32.6 | 31.3433
| 5-DaHall 1-CRAC-07 | LG CRAC-#07 | 0 | 1 | 1 | 32.55 |  |  |  | Stand-by CRAC
| 5-DaHall 1-CRAC-08 | LG CRAC-#08 | 0 | 1 | 1 | 32.55 | 28.4 | 29.9 | 29.6307 | Stand-by CRAC
| 5-DaHall 1-CRAC-09 | LG CRAC-#09 | 0 | 1 | 1 | 32.55 | 26.3 | 30.6 | 26.9354 | Stand-by CRAC
| 5-DaHall 1-CRAC-10 | LG CRAC-#10 | 0 | 1 | 1 | 32.55 | 25.6 | 34 | 30.626 | Stand-by CRAC
| 5-DaHall 1-CRAC-11 | LG CRAC-#11 | 0 | 1 | 1 | 32.55 | 27.7 | 30.4 | 29.3824 | Stand-by CRAC
| 5-DaHall 1-CRAC-12 | LG CRAC-#12 | 0 | 1 | 1 | 32.55 | 27 | 30.2 | 28.3196 | Stand-by CRAC
| 5-DaHall 1-CRAC-15 | Aux. CRAC 5F-1 | 0 | 1 | 1 | 24.4 | 26 | 27.5 | 26.9184 | Stand-by CRAC
| 5-DaHall 1-CRAC-16 | Aux. CRAC 5F-2 | 0 | 1 | 1 | 24.4 | 25.5 | 27.5 | 26.5598 | Stand-by CRAC
4F | 4-CRACRm-CRAC-01 | Main CRAC 4F-1 | 1 | 1 | N+1 | 105.48 | 25.7 | 39.7 | 35.1904 |  | 4-1 Collecting integrated data
| 4-CRACRm-CRAC-02 | Main CRAC 4F-2 | 1 | 1 |  | 105.48 | 28.7 | 42.6 | 38.2749 |  | 4-2 Collecting integrated data
| 4-CRACRm-CRAC-03 | Main CRAC 4F-3 | 1 | 1 |  | 105.48 | 27.4 | 45.8 | 40.4476 |  | 4-3 Collecting integrated data
| 4-CRACRm-CRAC-04 | Main CRAC 4F-4 | 1 | 1 |  | 105.48 | 27 | 45.3 | 40.0883 |  | 4-4 Collecting integrated data
| 4-DaHall 1-CRAC-05 | Aux.E_CRAC 4F-1 | 1 | 1 |  | 65 | 30.6 | 40.6 | 37.4748
| 4-DaHall 1-CRAC-06 | Aux.E_CRAC 4F-2 | 1 | 1 |  | 65 | 29 | 30 | 29.3224
| 4-DaHall 1-CRAC-02 | Aux. CRAC 4F-1 | 1 | 1 | Dedicated CRAC | 16.3 | 30.5 | 34.5 | 31.6917
| 4-DaHall 1-CRAC-03 | Aux. CRAC 4F-2 | 1 | 1 |  | 16.3 | 31 | 40.5 | 34.6198
| 4-DaHall 1-CRAC-04 | Aux. CRAC 4F-3 | 1 | 1 |  | 16.3 | 28 | 45 | 30.1265
| 4-DaHall 1-CRAC-01 | Aux. CRAC 4F-4 | 1 | 1 |  | 35 | 31.5 | 50.1 | 44.6172 | Not connected with FMS
6F | 6-DaHall 1-CRAC-01 | Aux. CRAC 6F-1 | 1 | 1 |  | 70.32 | 25.2 | 56.1 | 38.4457
| 6-DaHall 1-CRAC-02 | Aux. CRAC 6F-2 | 1 | 1 |  | 70.32 | 25 | 56.2 | 37.5179
| 6-DaHall 1-CRAC-03 | Aux. CRAC 6F-3 | 1 | 1 |  | 70.32 | 24.9 | 55.1 | 37.8711
Note: To ensure all temperature sensors are at the cold aisle
Hot standby according to current load +20%
| Device Name | 4/F |  | 5/F |  | 6/F |  | 7/F
|  | Average Temp. | Ave Hum. | Average Temp. | Ave Hum. | Average Temp. | Ave Hum. | Average Temp. | Ave Hum.
TH-01-01
TH-01-02
TH-01-03
TH-01-04
TH-01-05
TH-01-06
TH-01-07
TH-01-08
TH-01-09
TH-01-10
TH-01-11
TH-01-12
TH-01-13
TH-01-14
TH-01-15
TH-01-16
TH-02-01
TH-02-02
TH-02-03
TH-02-04
TH-02-05
TH-02-06
TH-02-07
TH-02-08
TH-02-09
TH-02-10
TH-02-11
TH-02-12
TH-02-13
TH-02-14
TH-02-15
TH-02-16
TH-03-01
TH-03-02
TH-03-03
TH-03-04
TH-03-05
TH-03-06
TH-03-07
TH-03-08
TH-03-09
TH-03-10
TH-03-11
TH-03-12
TH-03-13
TH-03-14
TH-03-15
TH-03-16
TH-04-01
TH-04-02
TH-04-03
TH-04-04
TH-04-05
TH-04-06
TH-04-07
TH-04-08
TH-04-09
TH-04-10
TH-04-11
TH-04-12
TH-04-13
TH-05-01
TH-05-02
TH-05-03
TH-05-04
TH-05-05
TH-05-06
TH-05-07
TH-05-08
TH-05-09
TH-05-10
TH-05-11
TH-05-12
Note on D51: KhaRam Lee: 1 : Duty 0 : Cold standby
Note on D102: [스레드 댓글] 사용 중인 버전의 Excel에서 이 스레드 댓글을 읽을 수 있지만 파일을 이후 버전의 Excel에서 열면 편집 내용이 모두 제거됩니다. 자세한 정보: https://go.microsoft.com/fwlink/?linkid=870924. 댓글: Decreased indoor humidity due to inflow of low-humidity air from outside during the main CRAC replacement work period was recorded.
Note on F102: [스레드 댓글] 사용 중인 버전의 Excel에서 이 스레드 댓글을 읽을 수 있지만 파일을 이후 버전의 Excel에서 열면 편집 내용이 모두 제거됩니다. 자세한 정보: https://go.microsoft.com/fwlink/?linkid=870924. 댓글: Decreased indoor humidity due to inflow of low-humidity air from outside during the main CRAC replacement work period was recorded.