## Sheet1
Date : 2023-12-01 ~ 2023-12-31
Baseline: Average 22 to 26 degrees celcius
Floor | DEK Name | Equipment Name | No. of CRACs (Running) | No. of CRACs (N) | (N+1) | Cooling Cap (Kw) | Min Avg Temperature | Maximum Avg Temperature | Average Temperature
7F | 7-CRACRm-CRAC-01 | Main CRAC 7F-1 | 1 | 1 | N+1 | 105.48 | 25.3 | 26.5 | 25.9386
| 7-CRACRm-CRAC-02 | Main CRAC 7F-2 | 1 | 1 |  | 105.48 | 25.7 | 27 | 26.4457
| 7-CRACRm-CRAC-03 | Main CRAC 7F-3 | 1 | 1 |  | 105.48 | 19.2 | 27.1 | 26.5828
| 7-CRACRm-CRAC-04 | Main CRAC 7F-4 | 1 | 1 |  | 105.48 | 25.3 | 27.2 | 26.5692
6F | 6-CRACRm-CRAC-01 | Main CRAC 6F-1 | 1 | 1 | N+1 | 105.48 | 23.2 | 27.8 | 26.9071
| 6-CRACRm-CRAC-02 | Main CRAC 6F-2 | 1 | 1 |  | 105.48 | 19 | 27.5 | 26.7555
| 6-CRACRm-CRAC-03 | Main CRAC 6F-3 | 1 | 1 |  | 105.48 | 17.3 | 24.6 | 20.1888
| 6-CRACRm-CRAC-04 | Main CRAC 6F-4 | 1 | 1 |  | 105.48 | 24.8 | 28 | 26.9358
| 6-DaHall 1-CRAC-01 | Aux. CRAC 6F-1 | 1 | 1 |  | 70.32 | 23 | 25.3 | 24.5022
| 6-DaHall 1-CRAC-02 | Aux. CRAC 6F-2 | 1 | 1 |  | 70.32 | 23.3 | 25.4 | 24.6264
| 6-DaHall 1-CRAC-03 | Aux. CRAC 6F-3 | 1 | 1 |  | 70.32 | 23.6 | 25.5 | 24.7997
5F | 5-CRACRm-CRAC-01 | Main CRAC 5F-1 | 1 | 1 | N+1 | 105.48 | 24.1 | 25.5 | 24.7713
| 5-CRACRm-CRAC-02 | Main CRAC 5F-2 | 1 | 1 |  | 105.48 | 24.5 | 25.8 | 25.0793
| 5-CRACRm-CRAC-03 | Main CRAC 5F-3 | 1 | 1 |  | 105.48 | 24.4 | 25.9 | 25.0237
| 5-CRACRm-CRAC-04 | Main CRAC 5F-4 | 1 | 1 |  | 105.48 | 24 | 25.4 | 24.5619
| 5-DaHall 1-CRAC-13 | CF CRAC-#01 | 0 | 1 | Dedicated CRAC | 32.55 | 27.9 | 33.2 | 32.6372
| 5-DaHall 1-CRAC-14 | CF CRAC-#02 | 0 | 1 |  | 32.55 | 23.6 | 27.2 | 26.1223
| 5-DaHall 1-CRAC-01 | LG CRAC-#01 | 0 | 1 | Dedicated CRAC | 32.55 | 21.8 | 30.5 | 28.7192
| 5-DaHall 1-CRAC-02 | LG CRAC-#02 | 1 | 1 |  | 32.55 | 22.5 | 28.1 | 25.2719
| 5-DaHall 1-CRAC-03 | LG CRAC-#03 | 0 | 1 |  | 32.55 | 19.3 | 28.8 | 27.1781
| 5-DaHall 1-CRAC-04 | LG CRAC-#04 | 1 | 1 |  | 32.55 | 22.9 | 25.6 | 24.0537
| 5-DaHall 1-CRAC-05 | LG CRAC-#05 | 0 | 1 |  | 32.55 | 20.8 | 25.2 | 21.6316
| 5-DaHall 1-CRAC-06 | LG CRAC-#06 | 1 | 1 |  | 32.55 | 21.5 | 24.8 | 23.6089
| 5-DaHall 1-CRAC-07 | LG CRAC-#07 | 0 | 1 |  | 32.55 | 17.3 | 27 | 19.993
| 5-DaHall 1-CRAC-08 | LG CRAC-#08 | 0 | 1 |  | 32.55 | 19.5 | 23.3 | 21.9057
| 5-DaHall 1-CRAC-09 | LG CRAC-#09 | 0 | 1 |  | 32.55 | 18.9 | 25 | 21.1101
| 5-DaHall 1-CRAC-10 | LG CRAC-#10 | 0 | 1 |  | 32.55 | 20.7 | 30.5 | 22.163
| 5-DaHall 1-CRAC-11 | LG CRAC-#11 | 0 | 1 |  | 32.55 | 22.2 | 25 | 23.3883
| 5-DaHall 1-CRAC-12 | LG CRAC-#12 | 0 | 1 |  | 32.55 | 19.1 | 22.6 | 20.6455
| 5-DaHall 1-CRAC-15 | Aux. CRAC 5F-1 | 0 | 1 | Dedicated CRAC | 24.4 | 27.5 | 30 | 28.4047
| 5-DaHall 1-CRAC-16 | Aux. CRAC 5F-2 | 0 | 1 |  | 24.4 | 26 | 28.5 | 26.9187
4F | 4-CRACRm-CRAC-01 | Main CRAC 4F-1 | 1 | 1 | N+1 | 105.48 | 24.8 | 26 | 25.4745
| 4-CRACRm-CRAC-02 | Main CRAC 4F-2 | 1 | 1 |  | 105.48 | 24.4 | 25.7 | 25.1753
| 4-CRACRm-CRAC-03 | Main CRAC 4F-3 | 1 | 1 |  | 105.48 | 23.8 | 25.8 | 24.9077
| 4-CRACRm-CRAC-04 | Main CRAC 4F-4 | 1 | 1 |  | 105.48 | 23.7 | 25.7 | 24.967
| 4-DaHall 1-CRAC-05 | Aux.E_CRAC 4F-1 | 1 | 1 |  | 65 | 25.9 | 28.3 | 27.0936
| 4-DaHall 1-CRAC-06 | Aux.E_CRAC 4F-2 | 1 | 1 |  | 65 | 24 | 26 | 24.4032
| 4-DaHall 1-CRAC-02 | Aux. CRAC 4F-1 | 1 | 1 | Dedicated CRAC | 16.3 | 23 | 25.5 | 24.3123
| 4-DaHall 1-CRAC-03 | Aux. CRAC 4F-2 | 1 | 1 |  | 16.3 | 15.5 | 25 | 23.0787
| 4-DaHall 1-CRAC-04 | Aux. CRAC 4F-3 | 1 | 1 |  | 16.3 | 19 | 30 | 29.2389
| 4-DaHall 1-CRAC-01 | Aux. CRAC 4F-4 | 1 | 1 |  | 35 | 23.7 | 26.3 | 24.8802 | Not connected with FMS
Baseline: Average 30 to 70 % RH
Floor | DEK Name | Equipment Name | No. of CRACs (Running) | No. of CRACs (N) | (N+1) | Cooling Cap (Kw) | Min Avg Humidity | Maximum Avg Humidity | Average Humidity
7F | 7-CRACRm-CRAC-01 | Main CRAC 7F-1 | 1 | 1 | N+1 | 105.48 | 18.6 | 43.6 | 35.7942 |  | 7-1 Collecting integrated data
| 7-CRACRm-CRAC-02 | Main CRAC 7F-2 | 1 | 1 |  | 105.48 | 19.2 | 43.9 | 36.1182 |  | 7-2 Collecting integrated data
| 7-CRACRm-CRAC-03 | Main CRAC 7F-3 | 1 | 1 |  | 105.48 | 20.4 | 62.5 | 35.7434 |  | 7-3 Collecting integrated data
| 7-CRACRm-CRAC-04 | Main CRAC 7F-4 | 1 | 1 |  | 105.48 | 17.5 | 40.6 | 33.7511 |  | 7-4 Collecting integrated data
6F | 6-CRACRm-CRAC-01 | Main CRAC 6F-1 | 1 | 1 | N+1 | 105.48 | 10.8 | 45.5 | 34.4641 |  | 6-1,6-2 Collecting integrated data
| 6-CRACRm-CRAC-02 | Main CRAC 6F-2 | 1 | 1 |  | 105.48 | 11.8 | 63.5 | 33.599 |  | 6-1,6-2 Collecting integrated data
| 6-CRACRm-CRAC-03 | Main CRAC 6F-3 | 1 | 1 |  | 105.48 | 16.8 | 71.6 | 50.1407 |  | 6-3,6-4 Collecting integrated data
| 6-CRACRm-CRAC-04 | Main CRAC 6F-4 | 1 | 1 |  | 105.48 | 10.9 | 44.1 | 37.2394 |  | 6-3,6-4 Collecting integrated data
5F | 5-CRACRm-CRAC-01 | Main CRAC 5F-1 | 1 | 1 | N+1 | 105.48 | 15.1 | 42.4 | 37.111 |  | 5-1 Collecting integrated data
| 5-CRACRm-CRAC-02 | Main CRAC 5F-2 | 1 | 1 |  | 105.48 | 14.5 | 41.2 | 36.0862 |  | 5-2 Collecting integrated data
| 5-CRACRm-CRAC-03 | Main CRAC 5F-3 | 1 | 1 |  | 105.48 | 12.3 | 40.8 | 34.673 |  | 5-3 Collecting integrated data
| 5-CRACRm-CRAC-04 | Main CRAC 5F-4 | 1 | 1 |  | 105.48 | 12.9 | 42.2 | 35.7571 |  | 5-4 Collecting integrated data
| 5-DaHall 1-CRAC-13 | CF CRAC-#01 | 0 | 1 | 1 | 32.55 | 25.9 | 29.4 | 26.3274 | Stand-by CRAC
| 5-DaHall 1-CRAC-14 | CF CRAC-#02 | 0 | 1 | 1 | 32.55 | 27.7 | 30.4 | 28.419 | Stand-by CRAC
| 5-DaHall 1-CRAC-01 | LG CRAC-#01 | 0 | 1 | 1 | 32.55 | 25.7 | 31.6 | 26.6997 | Stand-by CRAC
| 5-DaHall 1-CRAC-02 | LG CRAC-#02 | 1 | 1 | 1 | 32.55 | 29.4 | 33.1 | 31.271
| 5-DaHall 1-CRAC-03 | LG CRAC-#03 | 0 | 1 | 1 | 32.55 | 24.7 | 31.5 | 25.8939 | Stand-by CRAC
| 5-DaHall 1-CRAC-04 | LG CRAC-#04 | 1 | 1 | 1 | 32.55 | 30.6 | 32.8 | 31.8222
| 5-DaHall 1-CRAC-05 | LG CRAC-#05 | 0 | 1 | 1 | 32.55 | 29.6 | 32.3 | 31.8027 | Stand-by CRAC
| 5-DaHall 1-CRAC-06 | LG CRAC-#06 | 1 | 1 | 1 | 32.55 | 30.5 | 32.3 | 31.1751
| 5-DaHall 1-CRAC-07 | LG CRAC-#07 | 0 | 1 | 1 | 32.55 | 25.3 | 32.2 | 29.6672 | Stand-by CRAC
| 5-DaHall 1-CRAC-08 | LG CRAC-#08 | 0 | 1 | 1 | 32.55 | 28.9 | 30 | 29.9236 | Stand-by CRAC
| 5-DaHall 1-CRAC-09 | LG CRAC-#09 | 0 | 1 | 1 | 32.55 | 26.4 | 30.5 | 28.6705 | Stand-by CRAC
| 5-DaHall 1-CRAC-10 | LG CRAC-#10 | 0 | 1 | 1 | 32.55 | 24.9 | 31.5 | 30.2107 | Stand-by CRAC
| 5-DaHall 1-CRAC-11 | LG CRAC-#11 | 0 | 1 | 1 | 32.55 | 27.8 | 30.2 | 28.8082 | Stand-by CRAC
| 5-DaHall 1-CRAC-12 | LG CRAC-#12 | 0 | 1 | 1 | 32.55 | 27.9 | 30.2 | 29.2064 | Stand-by CRAC
| 5-DaHall 1-CRAC-15 | Aux. CRAC 5F-1 | 0 | 1 | 1 | 24.4 | 26 | 27.5 | 27.0878 | Stand-by CRAC
| 5-DaHall 1-CRAC-16 | Aux. CRAC 5F-2 | 0 | 1 | 1 | 24.4 | 25.5 | 27 | 26.6492 | Stand-by CRAC
4F | 4-CRACRm-CRAC-01 | Main CRAC 4F-1 | 1 | 1 | N+1 | 105.48 | 18.9 | 39.9 | 34.5901 |  | 4-1 Collecting integrated data
| 4-CRACRm-CRAC-02 | Main CRAC 4F-2 | 1 | 1 |  | 105.48 | 22.3 | 43.6 | 37.9529 |  | 4-2 Collecting integrated data
| 4-CRACRm-CRAC-03 | Main CRAC 4F-3 | 1 | 1 |  | 105.48 | 21 | 45.9 | 39.5063 |  | 4-3 Collecting integrated data
| 4-CRACRm-CRAC-04 | Main CRAC 4F-4 | 1 | 1 |  | 105.48 | 20.5 | 45.7 | 39.0151 |  | 4-4 Collecting integrated data
| 4-DaHall 1-CRAC-05 | Aux.E_CRAC 4F-1 | 1 | 1 |  | 65 | 25.7 | 40.1 | 37.0983
| 4-DaHall 1-CRAC-06 | Aux.E_CRAC 4F-2 | 1 | 1 |  | 65 | 29 | 30 | 29.3689
| 4-DaHall 1-CRAC-02 | Aux. CRAC 4F-1 | 1 | 1 | Dedicated CRAC | 16.3 | 30 | 34 | 31.6194
| 4-DaHall 1-CRAC-03 | Aux. CRAC 4F-2 | 1 | 1 |  | 16.3 | 30.5 | 55 | 33.9665
| 4-DaHall 1-CRAC-04 | Aux. CRAC 4F-3 | 1 | 1 |  | 16.3 | 28 | 44 | 28.2216
| 4-DaHall 1-CRAC-01 | Aux. CRAC 4F-4 | 1 | 1 |  | 35 | 24.7 | 49.8 | 43.4218 | Not connected with FMS
6F | 6-DaHall 1-CRAC-01 | Aux. CRAC 6F-1 | 1 | 1 |  | 70.32 | 13.3 | 44.3 | 35.8912
| 6-DaHall 1-CRAC-02 | Aux. CRAC 6F-2 | 1 | 1 |  | 70.32 | 13.5 | 42.8 | 35.0665
| 6-DaHall 1-CRAC-03 | Aux. CRAC 6F-3 | 1 | 1 |  | 70.32 | 13.1 | 41.3 | 34.9207
Note: To ensure all temperature sensors are at the cold aisle
Hot standby according to current load +20%
| Device Name | 4/F |  | 5/F |  | 6/F |  | 7/F
|  | Average Temp. | Ave Hum. | Average Temp. | Ave Hum. | Average Temp. | Ave Hum. | Average Temp. | Ave Hum.
TH-01-01
TH-01-02
TH-01-03
TH-01-04
TH-01-05
TH-01-06
TH-01-07
TH-01-08
TH-01-09
TH-01-10
TH-01-11
TH-01-12
TH-01-13
TH-01-14
TH-01-15
TH-01-16
TH-02-01
TH-02-02
TH-02-03
TH-02-04
TH-02-05
TH-02-06
TH-02-07
TH-02-08
TH-02-09
TH-02-10
TH-02-11
TH-02-12
TH-02-13
TH-02-14
TH-02-15
TH-02-16
TH-03-01
TH-03-02
TH-03-03
TH-03-04
TH-03-05
TH-03-06
TH-03-07
TH-03-08
TH-03-09
TH-03-10
TH-03-11
TH-03-12
TH-03-13
TH-03-14
TH-03-15
TH-03-16
TH-04-01
TH-04-02
TH-04-03
TH-04-04
TH-04-05
TH-04-06
TH-04-07
TH-04-08
TH-04-09
TH-04-10
TH-04-11
TH-04-12
TH-04-13
TH-05-01
TH-05-02
TH-05-03
TH-05-04
TH-05-05
TH-05-06
TH-05-07
TH-05-08
TH-05-09
TH-05-10
TH-05-11
TH-05-12
Note on D51: KhaRam Lee: 1 : Duty 0 : Cold standby
Note on D102: [스레드 댓글] 사용 중인 버전의 Excel에서 이 스레드 댓글을 읽을 수 있지만 파일을 이후 버전의 Excel에서 열면 편집 내용이 모두 제거됩니다. 자세한 정보: https://go.microsoft.com/fwlink/?linkid=870924. 댓글: Decreased indoor humidity due to inflow of low-humidity air from outside during the main CRAC replacement work period was recorded.
Note on F102: [스레드 댓글] 사용 중인 버전의 Excel에서 이 스레드 댓글을 읽을 수 있지만 파일을 이후 버전의 Excel에서 열면 편집 내용이 모두 제거됩니다. 자세한 정보: https://go.microsoft.com/fwlink/?linkid=870924. 댓글: Decreased indoor humidity due to inflow of low-humidity air from outside during the main CRAC replacement work period was recorded.