## 7층_랙별_계통_및_부하량
7층 전송 및 고객 랙별 부하 사용내역 | [56 empty] | 미디어꾼 | 계약용량 | 시간당 전력량 | 남은 전력량 | 전력초과여부 | 피크값 | 평균값 | 0
[41 empty] | 2023년 기준 | [16 empty] | 0 | 0 | 0 | 미사용 랙 | 0 | #DIV/0!
구분 | DEKR NO. | BAY NAME | RACK NAME | 계약용량 | 전원구성 |  | DEK차단기명칭 |  | DEK차단기명칭 (NEW) |  | 차단기 정보(수정) | [7 empty] | Fuse/차단기 정보 |  | IPD/2차분전반 사용정보 |  | 2차 분전반/정류기 정보 |  | 1차 분전반 사용정보 |  | 1차 분전반 정보 |  | 배전반 정보 |  | TR 정보 |  | 계측값 |  |  | 월 유효전력량 |  | kW(전월최대유효전력) | 월간 사용전력량[kWh] | RACK별 장비명 | 비고 | 시간당 전력량 | 남은 전력량 | 전력초과여부 | 사용초과 고객 수 |  | 적정함 | 미사용 랙 | 구분 | DEKR NO. | BAY NAME | RACK NAME | 계약용량 | DEK차단기명칭 (NEW) |  | 계측값 |  |  | 월 유효전력량 |  | 월간 사용전력량[kWh] | kW(전월최대유효전력) | 월간 사용전력량[kWh] | RACK별 장비명 | 비고
구분 |  |  |  | kW | AC | DC | A | B | A | B | A |  |  |  | B |  |  |  | A | B | A | B | A | B | A | B | A | B | A | B | A | B | A전원 | B전원 | 합계 | A전원 | B전원 | [7 empty] | 31 |  | 48 | 144 |  |  |  |  | kW | A | B | A전원 | B전원 | 합계 | A전원 | B전원
SJT | 정류기실 |  | SJT 정류기1 | 50 | ○ |  | 7-1-A4-225-6 |  | 7-DaHall 1-PDU-03-225-6 |  | 380 | 225 | PDU-03 | 6 |  |  |  |  | A: 7-1-A4-06 / 4P 225A; A: 7-1-A4 (4P 400A); A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 159.1216; 합계: 159.1216; A전원: 23753.8 | 32.356 | 23753.8 |  |  | 31.9272 | 18.0728 | 적정함 |  |  |  |  | 찾을 수 없음 |  |  |  |  | 찾을 수 없음 |  | 찾을 수 없음
|  |  | SJT 정류기2 | 50 | ○ |  |  | 7-1-B4-150-1 |  | 7-DaHall 1-PDU-04-150-1 |  |  |  |  | 380 | 150 | PDU-04 | 1 | B: 7-1-B4-01 / 3P 150A; B: 7-1-B4 (4P 400A); B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 141.4083; 합계: 141.4083; B전원: 20745.1 | 28.323 | 20745.1 |  |  | 27.8832 | 22.1168 | 적정함
회의실 |  |  | TEST_BED |  |  | ○ | 7-1-A-4-35-32 | 7-1-B-4-35-32 | 7-DaHall 1-A-4-35-32 | 7-DaHall 1-B-4-35-32 | 48 | 35 | A-4 | 32 | 48 | 35 | B-4 | 32 | IPD A-4-32 / 35A | IPD B-4-32 / 35A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | TEST_BED 장비 |  | 0 | 0 | 미사용 랙
| A111 |  |  | 2.2 | ○ |  | 7-1-A2-30-37 | 7-1-B2-30-37 | 7-DaHall 1-PDU-01-30-37 | 7-DaHall 1-PDU-02-30-37 | 220 | 30 | PDU-01 | 37 | 220 | 30 | PDU-02 | 37 | A: U3-7A-37 / 2P 30A; B: U3-7B-37 / 2P 30A; A: U3-7A(U7-5A) 4P 300A; B: U3-7B(U7-6B) 4P 300A; A: LV-7A #05 / 3P 320A (U7-5A); B: LV-7B #06 / 3P 320A (U7-6B); A전원: 0; B전원: 0.0040889; 합계: 0.0040889; A전원: 0; B전원: 0 | 0.093 | 0 | TEST_BED 계측기/노트북 전원 |  | 0 | 2.2 | 무부하 랙
| A207 | 538 BAY | 538B_NOKIA1830 |  |  | ○ | 7-1-A-4-100-58 | 7-1-B-4-100-58 | 7-DaHall 1-A-4-100-58 | 7-DaHall 1-B-4-100-58 | 48 | 100 | A-4 | 58 | 48 | 100 | B-4 | 58 | IPD A-4-58 / 100A | IPD B-4-58 / 100A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| A208 | 537 BAY | 537B_NOKIA1830 |  |  | ○ | 7-1-A-4-100-56 | 7-1-B-4-35-56 | 7-DaHall 1-A-4-100-56 | 7-DaHall 1-B-4-35-56 | 48 | 100 | A-4 | 56 | 48 | 35 | B-4 | 56 | IPD A-4-56 / 100A | IPD B-4-56 / 35A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| A209 | 536 BAY | 536B_NOKIA1830 |  |  | ○ | 7-1-A-4-50-59 | 7-1-B-4-50-59 | 7-DaHall 1-A-4-50-59 | 7-DaHall 1-B-4-50-59 | 48 | 50 | A-4 | 59 | 48 | 50 | B-4 | 59 | IPD A-4-59 / 50A | IPD B-4-59 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| A210 | 535 BAY | 536B_NOKIA1830, PSS-8 |  |  | ○ | 7-1-A-4-50-25 | 7-1-B-4-50-25 | 7-DaHall 1-A-4-50-25 | 7-DaHall 1-B-4-50-25 | 48 | 50 | A-4 | 25 | 48 | 50 | B-4 | 25 | IPD A-4-25 / 50A | IPD B-4-25 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | 노키아1830_PSS 8 ('21.09.14 전기투입) |  | 0 | 0 | 미사용 랙
|  | 443 BAY | [35 empty] | 0 | 0 |  |  | 0 | 0 | 미사용 랙
|  | 442 BAY | [35 empty] | 0 | 0 |  |  | 0 | 0 | 미사용 랙
|  | 441 BAY | [35 empty] | 0 | 0 |  |  | 0 | 0 | 미사용 랙
| A307 | 440 BAY | 440B_CN6500 |  |  | ○ | 7-1-B-4-100-31 | 7-1-A-4-100-31 | 7-DaHall 1-B-4-100-31 | 7-DaHall 1-A-4-100-31 | 48 | 100 | B-4 | 31 | 48 | 100 | A-4 | 31 | IPD B-4-31 / 100A | IPD A-4-31 / 100A | IPD B-4 | IPD A-4 | 정류기 B -48V 1400A | 정류기 A -48V 1400A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| A308 | 439 BAY | 439B_CN6500 |  |  | ○ | 7-1-B-4-100-30 | 7-1-A-4-100-30 | 7-DaHall 1-B-4-100-30 | 7-DaHall 1-A-4-100-30 | 48 | 100 | B-4 | 30 | 48 | 100 | A-4 | 30 | IPD B-4-30 / 100A | IPD A-4-30 / 100A | IPD B-4 | IPD A-4 | 정류기 B -48V 1400A | 정류기 A -48V 1400A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| A309 | 437 BAY | 437B(上)_코위버P7200 |  |  | ○ | 7-1-A-4-100-29 | 7-1-B-4-100-29 | 7-DaHall 1-A-4-100-29 | 7-DaHall 1-B-4-100-29 | 48 | 100 | A-4 | 29 | 48 | 100 | B-4 | 29 | IPD A-4-29 / 100A | IPD B-4-29 / 100A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | 코위버P7200 |  | 0 | 0 | 미사용 랙
|  |  | 437B(下)_텔레필드_FM700 |  |  | ○ | 7-1-A-4-35-34 | 7-1-B-4-35-34 | 7-DaHall 1-A-4-35-34 | 7-DaHall 1-B-4-35-34 | 48 | 35 | A-4 | 34 | 48 | 35 | B-4 | 34 | IPD A-4-34 / 35A | IPD B-4-34 / 35A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | 텔레필드_FM700 | 2021/06/10 전원신규 구성 및 투입 | 0 | 0 | 미사용 랙
| A310 | 436 BAY | 436B_코위버P7200 |  |  | ○ | 7-1-A-4-100-3 | 7-1-B-4-100-3 | 7-DaHall 1-A-4-100-3 | 7-DaHall 1-B-4-100-3 | 48 | 100 | A-4 | 3 | 48 | 100 | B-4 | 3 | IPD A-4-03 / 100A | IPD B-4-03 / 100A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| A402 | 343 BAY | Sejong Telecom Inc. |  |  | ○ | 7-1-A-4-50-41 | 7-1-B-4-50-41 | 7-DaHall 1-A-4-50-41 | 7-DaHall 1-B-4-50-41 | 48 | 50 | A-4 | 41 | 48 | 50 | B-4 | 41 | IPD A-4-41 / 50A | IPD B-4-41 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  | DC 전원 미사용 | 0 | 0 | 미사용 랙
[5 empty] | ○ | [13 empty] | A: U3-7A-05 / 2P 30A (342Bay 인출) |  | 0 |  | 342Bay에서 1개 전원 인출사용 중 | 0 | 0 | 무부하 랙
| A403 | 342 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-B2-30-3 | 7-1-A2-30-5 | 7-DaHall 1-PDU-01-30-5 | 7-DaHall 1-PDU-02-30-3 | 220 | 30 | PDU-02 | 3 | 220 | 30 | PDU-01 | 5 | U3-7B-03 / 2P 30A | U3-7A-05 / 2P 30A | [6 empty] | U3-7B(U7-6B) 4P 300A | U3-7A(U7-5A) 4P 300A | LV-7B #06 / 3P 320A (U7-6B) | LV-7A #05 / 3P 320A (U7-5A) | TR-7B 1000kVA | TR-7A 1000kVA | 4.9726 | 5.2018 | 10.1744 | 753.8 | 688.7 | 1.987 | 1442.5 | 인터넷팀 장비 |  | 1.9388 | -0.33884 | 사용초과 | Sejong Telecom Inc. | A403
| A404 | 341 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A1-30-40 | 7-1-B1-30-38 | 7-DaHall 1-RPP-01-30-40 | 7-DaHall 1-RPP-02-30-38 | 220 | 30 | RPP-01 | 40 | 220 | 30 | RPP-02 | 38 | UPS A1-40 / 2P 30A | UPS B1-38 / 2P 30A | UPS 출력분전반 A1 #40 | UPS 출력분전반 B1 #38 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 4.7992 | 4.9175 | 9.7167 | 757.2 | 772.1 | 2.152 | 1529.3 | 인터넷팀 장비(MAN POP) |  | 2.0555 | -0.45551 | 사용초과 | Sejong Telecom Inc. | A404
| A405 | 340 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A1-20-25 | 7-1-A1-30-20 | 7-DaHall 1-RPP-01-20-25 | 7-DaHall 1-RPP-01-30-20 | 220 | 20 | RPP-01 | 25 | 220 | 30 | RPP-01 | 20 | UPS A1-25 / 2P 20A | UPS A1-20 / 2P 30A | UPS 출력분전반 A1 #25 | UPS 출력분전반 A1 #20 | UPS 출력 분전반A1, 4P 400A |  | UPS 출력 분전반A, #01 4P 225A |  | UPS 출력 배전반A, 4P 400A |  | LV-7A #06 / 3P 320A (U7-6A) |  | TR-7A 1000kVA |  | 1.5116 | 1.4935 | 3.0052 | 242.7 | 231.6 | 0.662 | 474.3 | 인터넷팀 장비 | 인터넷운영팀 MAN Rack #2, A & B전원 | 0.6375 | 0.9625 | 적정함
| A406 | 339 BAY | 339B_CN4200 |  |  | ○ | 7-1-B-4-35-46 | 7-1-A-4-35-42 | 7-DaHall 1-B-4-35-46 | 7-DaHall 1-A-4-35-42 | 48 | 35 | B-4 | 46 | 48 | 35 | A-4 | 42 | IPD B-4-46 / 35A | IPD A-4-42 / 35A | IPD B-4 | IPD A-4 | 정류기 B -48V 1400A | 정류기 A -48V 1400A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| A407 | 338 BAY | Sejong Telecom Inc. |  |  | ○ | 7-1-A-4-35-43 | 7-1-B-4-50-47 | 7-DaHall 1-A-4-35-43 | 7-DaHall 1-B-4-50-47 | 48 | 35 | A-4 | 43 | 48 | 50 | B-4 | 47 | IPD A-4-43 / 35A | IPD B-4-47 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
|  |  |  | 1.6 | ○ | [13 empty] | A: UPS A1-25 / 2P 20A (340Bay에서 인출) |  | 0 |  | 340Bay에서 1개 전원 인출사용 중 | 0 | 1.6 | 무부하 랙
| A408 | 337 BAY | Sejong Telecom Inc. |  |  | ○ | 7-1-A-4-35-44 | 7-1-B-4-35-48 | 7-DaHall 1-A-4-35-44 | 7-DaHall 1-B-4-35-48 | 48 | 35 | A-4 | 44 | 48 | 35 | B-4 | 48 | IPD A-4-44 / 35A | IPD B-4-48 / 35A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
|  |  |  | 1.6 | ○ |  |  | 7-1-B2-30-8 |  | 7-DaHall 1-PDU-02-30-8 |  |  |  |  | 220 | 30 | PDU-02 | 8 | B: U3-7B-08 / 2P 30A; B: U3-7B(U7-6B) 4P 300A; B: LV-7B #06 / 3P 320A (U7-6B); B: TR-7B 1000kVA; B전원: 0; 합계: 0; B전원: 0 | 0 | 0 |  |  | 0 | 1.6 | 무부하 랙
| A409 | 336 BAY | 336B_CN4200 |  |  | ○ | 7-1-A-4-35-50 | 7-1-B-4-35-50 | 7-DaHall 1-A-4-35-50 | 7-DaHall 1-B-4-35-50 | 48 | 35 | A-4 | 50 | 48 | 35 | B-4 | 50 | IPD A-4-50 / 35A | IPD B-4-50 / 35A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| A410 | 335 BAY | 335B_CN4200 |  |  | ○ | 7-1-A-4-50-46 | 7-1-B-4-50-49 | 7-DaHall 1-A-4-50-46 | 7-DaHall 1-B-4-50-49 | 48 | 50 | A-4 | 46 | 48 | 50 | B-4 | 49 | IPD A-4-46 / 50A | IPD B-4-49 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| A411 | 334 BAY | 334B_CN4200 |  |  | ○ | 7-1-A-4-35-54 | 7-1-B-4-35-54 | 7-DaHall 1-A-4-35-54 | 7-DaHall 1-B-4-35-54 | 48 | 35 | A-4 | 54 | 48 | 35 | B-4 | 54 | IPD A-4-54 / 35A | IPD B-4-54 / 35A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| A502 | 244 BAY | 244B_코위버CWDM |  |  | ○ | 7-1-A-4-50-26 | 7-1-B-4-50-26 | 7-DaHall 1-A-4-50-26 | 7-DaHall 1-B-4-50-26 | 48 | 50 | A-4 | 26 | 48 | 50 | B-4 | 26 | IPD A-4-26 / 50A | IPD B-4-26 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| A503 | 243 BAY | 243B_코위버CWDM |  |  | ○ | 7-1-A-4-50-28 | 7-1-B-4-50-28 | 7-DaHall 1-A-4-50-28 | 7-DaHall 1-B-4-50-28 | 48 | 50 | A-4 | 28 | 48 | 50 | B-4 | 28 | IPD A-4-28 / 50A | IPD B-4-28 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| A504 | 242 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-9 | 7-1-B2-30-9 | 7-DaHall 1-PDU-01-30-9 | 7-DaHall 1-PDU-02-30-9 | 220 | 30 | PDU-01 | 9 | 220 | 30 | PDU-02 | 9 | U3-7A-09 / 2P 30A | U3-7B-09 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 5.8963 | 5.8618 | 11.7581 | 950.1 | 946.7 | 2.931 | 1896.8 | 인터넷팀 장비 |  | 2.5495 | -0.94946 | 사용초과 | Sejong Telecom Inc. | A504
| A505 | 241 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-7 | 7-1-B2-30-7 | 7-DaHall 1-PDU-01-30-7 | 7-DaHall 1-PDU-02-30-7 | 220 | 30 | PDU-01 | 7 | 220 | 30 | PDU-02 | 7 | U3-7A-07 / 2P 30A | U3-7B-07 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 5.9719 | 5.7373 | 11.7092 | 950.5 | 910.4 | 2.694 | 1860.9 | 인터넷팀 장비 |  | 2.5012 | -0.90121 | 사용초과 | Sejong Telecom Inc. | A505
| A506 | 240 BAY | 240B_코위버CWDM |  |  | ○ | 7-1-A-4-50-27 | 7-1-B-4-50-57 | 7-DaHall 1-A-4-50-27 | 7-DaHall 1-B-4-50-57 | 48 | 50 | A-4 | 27 | 48 | 50 | B-4 | 57 | IPD A-4-27 / 50A | IPD B-4-57 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  | PDP 2개 | 0 | 0 | 미사용 랙
[6 empty] | ○ | 7-1-A-4-50-33 | 7-1-B-4-50-33 | 7-DaHall 1-A-4-50-33 | 7-DaHall 1-B-4-50-33 | 48 | 50 | A-4 | 33 | 48 | 50 | B-4 | 33 | IPD A-4-33 / 50A | IPD B-4-33 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| A507 | 239 BAY | 239B_OSN7500 |  |  | ○ | 7-1-A-4-50-10 | 7-1-B-4-50-43 | 7-DaHall 1-A-4-50-10 | 7-DaHall 1-B-4-50-43 | 48 | 50 | A-4 | 10 | 48 | 50 | B-4 | 43 | IPD A-4-10 / 50A | IPD B-4-43 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  | IPD 3개 | 0 | 0 | 미사용 랙
[6 empty] | ○ | 7-1-A-4-50-11 | 7-1-B-4-50-44 | 7-DaHall 1-A-4-50-11 | 7-DaHall 1-B-4-50-44 | 48 | 50 | A-4 | 11 | 48 | 50 | B-4 | 44 | IPD A-4-11 / 50A | IPD B-4-44 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
[6 empty] | ○ | 7-1-A-4-50-18 | 7-1-B-4-50-45 | 7-DaHall 1-A-4-50-18 | 7-DaHall 1-B-4-50-45 | 48 | 50 | A-4 | 18 | 48 | 50 | B-4 | 45 | IPD A-4-18 / 50A | IPD B-4-45 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| A508 | 238 BAY | 238B_동원DWDM |  |  | ○ | 7-1-A-4-50-45 | 7-1-B-4-50-51 | 7-DaHall 1-A-4-50-45 | 7-DaHall 1-B-4-50-51 | 48 | 50 | A-4 | 45 | 48 | 50 | B-4 | 51 | IPD A-4-45 / 50A | IPD B-4-51 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| A509 | 237 BAY | 237B_CN4200 |  |  | ○ | 7-1-A-4-35-52 | 7-1-B-4-35-52 | 7-DaHall 1-A-4-35-52 | 7-DaHall 1-B-4-35-52 | 48 | 35 | A-4 | 52 | 48 | 35 | B-4 | 52 | IPD A-4-52 / 35A | IPD B-4-52 / 35A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| A510 | 236 BAY | 236B_CN4200 |  |  | ○ | 7-1-A-4-35-53 | 7-1-B-4-35-53 | 7-DaHall 1-A-4-35-53 | 7-DaHall 1-B-4-35-53 | 48 | 35 | A-4 | 53 | 48 | 35 | B-4 | 53 | IPD A-4-53 / 35A | IPD B-4-53 / 35A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B111 |  | DEK, 층간 Patch Cabinet
| B114 |  | DEK, 층간 Patch Cabinet
| B202 | 532 BAY | 532B_코위버1664 |  |  | ○ | 7-1-A-3-50-47 | 7-1-B-3-50-47 | 7-DaHall 1-A-3-50-47 | 7-DaHall 1-B-3-50-47 | 48 | 50 | A-3 | 47 | 48 | 50 | B-3 | 47 | IPD A-3-47 / 50A | IPD B-3-47 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B203 | 531 BAY | 531B_코위버1664 |  |  | ○ | 7-1-A-3-50-46 | 7-1-B-3-50-46 | 7-DaHall 1-A-3-50-46 | 7-DaHall 1-B-3-50-46 | 48 | 50 | A-3 | 46 | 48 | 50 | B-3 | 46 | IPD A-3-46 / 50A | IPD B-3-46 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B204 | 530 BAY | 530B_코위버1664 |  |  | ○ | 7-1-A-3-50-44 | 7-1-B-3-50-44 | 7-DaHall 1-A-3-50-44 | 7-DaHall 1-B-3-50-44 | 48 | 50 | A-3 | 44 | 48 | 50 | B-3 | 44 | IPD A-3-44 / 50A | IPD B-3-44 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B206 |  | Sejong Telecom Inc.('23.10.12 투입) | 2.2 | ○ |  | 7-1-A2-30-48 | 7-1-B2-30-48 | 7-DaHall 1-PDU-01-30-48 | 7-DaHall 1-PDU-02-30-48 | 220 | 30 | PDU-01 | 48 | 220 | 30 | PDU-02 | 48 | U3-7A-48 / 2P 30A | U3-7B-48 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.2292 | 2.6815 | 4.9107 | 357.1 | 421.2 | 1.483 | 778.3 | SJT | '23.10.12 투입 | 1.0461 | 1.1539 | 적정함
| B207 | 527 BAY | 527B_코위버1664 |  |  | ○ | 7-1-A-3-50-41 | 7-1-B-3-50-41 | 7-DaHall 1-A-3-50-41 | 7-DaHall 1-B-3-50-41 | 48 | 50 | A-3 | 41 | 48 | 50 | B-3 | 41 | IPD A-3-41 / 50A | IPD B-3-41 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B208 | 526 BAY | 526B_코위버1664 |  |  | ○ | 7-1-A-3-50-10 | 7-1-B-3-50-10 | 7-DaHall 1-A-3-50-10 | 7-DaHall 1-B-3-50-10 | 48 | 50 | A-3 | 10 | 48 | 50 | B-3 | 10 | IPD A-3-10 / 50A | IPD B-3-10 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B209 | 525 BAY | 525B_코위버1664 |  |  | ○ | 7-1-A-3-50-7 | 7-1-B-3-50-7 | 7-DaHall 1-A-3-50-7 | 7-DaHall 1-B-3-50-7 | 48 | 50 | A-3 | 7 | 48 | 50 | B-3 | 7 | IPD A-3-07 / 50A | IPD B-3-07 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B210 | 524 BAY | 524B_코위버1664 |  |  | ○ | 7-1-A-3-50-6 | 7-1-B-3-50-6 | 7-DaHall 1-A-3-50-6 | 7-DaHall 1-B-3-50-6 | 48 | 50 | A-3 | 6 | 48 | 50 | B-3 | 6 | IPD A-3-06 / 50A | IPD B-3-06 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B211 | 523 BAY | 523B_코위버3264 |  |  | ○ | 7-1-A-3-50-5 | 7-1-B-3-50-5 | 7-DaHall 1-A-3-50-5 | 7-DaHall 1-B-3-50-5 | 48 | 50 | A-3 | 5 | 48 | 50 | B-3 | 5 | IPD A-3-05 / 50A | IPD B-3-05 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B216 |  |  |  |  | ○ | 7-1-A-2-50-48 | 7-1-B-2-50-48 | 7-DaHall 1-A-2-50-48 | 7-DaHall 1-B-2-50-48 | 48 | 50 | A-2 | 48 | 48 | 50 | B-2 | 48 | IPD A-2-48 / 50A | IPD B-2-48 / 50A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | 드림라인 장비 |  | 0 | 0 | 미사용 랙
| B217 |  | Sejong Telecom Inc. |  |  | ○ | 7-1-A-2-35-47 | 7-1-B-2-35-47 | 7-DaHall 1-A-2-35-47 | 7-DaHall 1-B-2-35-47 | 48 | 35 | A-2 | 47 | 48 | 35 | B-2 | 47 | IPD A-2-47 / 35A | IPD B-2-47 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | SKT/SKB장비 | PDP 2개 ?? | 0 | 0 | 미사용 랙
[5 empty] | ○ | [13 empty] | A: UPS A1-07 / 2P 20A (518Bay에서 인출) | 0 | 0 |  |  | 0 | 0 | 무부하 랙
[6 empty] | ○ | 7-1-A-2-35-53 | 7-1-B-2-35-53 | 7-DaHall 1-A-2-35-53 | 7-DaHall 1-B-2-35-53 | 48 | 35 | A-2 | 53 | 48 | 35 | B-2 | 53 | IPD A-2-53 / 35A | IPD B-2-53 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B218 |  | Sejong Telecom Inc. |  |  | ○ | 7-1-A-2-16-44 | 7-1-B-2-16-46 | 7-DaHall 1-A-2-16-44 | 7-DaHall 1-B-2-16-46 | 48 | 16 | A-2 | 44 | 48 | 16 | B-2 | 46 | IPD A-2-44 / 16A | IPD B-2-46 / 16A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | 드림라인 장비 |  | 0 | 0 | 미사용 랙
[5 empty] | ○ | [13 empty] | A: UPS A1-07 / 2P 20A (517Bay에서 인출) | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| B219 |  | Sejong Telecom Inc. |  |  | ○ | 7-1-A-2-35-58 | 7-1-B-2-35-58 | 7-DaHall 1-A-2-35-58 | 7-DaHall 1-B-2-35-58 | 48 | 35 | A-2 | 58 | 48 | 35 | B-2 | 58 | IPD A-2-58 / 35A | IPD B-2-58 | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | SKB장비 |  | 0 | 0 | 미사용 랙
|  |  |  | 2.2 | ○ |  | 7-1-A1-20-7 |  | 7-DaHall 1-RPP-01-20-7 |  | 220 | 20 | RPP-01 | 7 |  |  |  |  | A: UPS A1-07 / 2P 20A; A: UPS 출력분전반 A1 #07; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 0 | 0 | 0 |  |  | 0 | 2.2 | 무부하 랙
| B222 | 514 BAY | 514B_LGU+장비 |  |  | ○ | 7-1-A-2-50-23 | 7-1-B-2-50-23 | 7-DaHall 1-A-2-50-23 | 7-DaHall 1-B-2-50-23 | 48 | 50 | A-2 | 23 | 48 | 50 | B-2 | 23 | IPD A-2-23 / 50A | IPD B-2-23 | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | LGU+장비 |  | 0 | 0 | 미사용 랙
| B223 | 513 BAY | 513B_SKB장비 |  |  | ○ | 7-1-A-2-50-7 | 7-1-B-2-50-7 | 7-DaHall 1-A-2-50-7 | 7-DaHall 1-B-2-50-7 | 48 | 50 | A-2 | 7 | 48 | 50 | B-2 | 7 | IPD A-2-07 / 50A | IPD B-2-07 | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | SKB장비 |  | 0 | 0 | 미사용 랙
| B224 | 512 BAY | Digital Edge | 2.2 | ○ | [13 empty] | B: 회로 조사 실패, B1 PNL 의심 / 413Bay 상부에서 숨어버림; 합계: 0 |  | 0 | 7F-5F UTP PATCH |  | 0 | 2.2 | 무부하 랙
| B225 | 511 BAY | 511B_LGU+장비 |  |  | ○ | 7-1-A-2-35-62 | 7-1-B-2-35-62 | 7-DaHall 1-A-2-35-62 | 7-DaHall 1-B-2-35-62 | 48 | 35 | A-2 | 62 | 48 | 35 | B-2 | 62 | IPD A-2-62 / 35A | IPD B-2-62 | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | LGU+장비 | PDP 1개, 장비직결 1개 | 0 | 0 | 미사용 랙
[6 empty] | ○ | 7-1-A-2-35-63 | 7-1-B-2-35-63 | 7-DaHall 1-A-2-35-63 | 7-DaHall 1-B-2-35-63 | 48 | 35 | A-2 | 63 | 48 | 35 | B-2 | 63 | IPD A-2-63 / 35A | IPD B-2-63 | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B306 | 427 BAY | 427B_ZTE POTN |  |  | ○ | 7-1-A-3-50-57 | 7-1-B-3-50-57 | 7-DaHall 1-A-3-50-57 | 7-DaHall 1-B-3-50-57 | 48 | 50 | A-3 | 57 | 48 | 50 | B-3 | 57 | IPD A-3-57 / 50A | IPD B-3-57 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  | IPD 2개 | 0 | 0 | 미사용 랙
[6 empty] | ○ | 7-1-A-3-50-58 | 7-1-B-3-50-58 | 7-DaHall 1-A-3-50-58 | 7-DaHall 1-B-3-50-58 | 48 | 50 | A-3 | 58 | 48 | 50 | B-3 | 58 | IPD A-3-58 / 50A | IPD B-3-58 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B307 | 426 BAY | 426B_ZTE POTN |  |  | ○ | 7-1-A-3-100-1 | 7-1-B-3-100-1 | 7-DaHall 1-A-3-100-1 | 7-DaHall 1-B-3-100-1 | 48 | 100 | A-3 | 1 | 48 | 100 | B-3 | 1 | IPD A-3-01 / 100A | IPD B-3-01 / 100A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  | IPD 3개 | 0 | 0 | 미사용 랙
[6 empty] | ○ | 7-1-A-3-100-2 | 7-1-B-3-100-2 | 7-DaHall 1-A-3-100-2 | 7-DaHall 1-B-3-100-2 | 48 | 100 | A-3 | 2 | 48 | 100 | B-3 | 2 | IPD A-3-02 / 100A | IPD B-3-02 / 100A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
[6 empty] | ○ | 7-1-A-3-50-3 | 7-1-B-3-50-3 | 7-DaHall 1-A-3-50-3 | 7-DaHall 1-B-3-50-3 | 48 | 50 | A-3 | 3 | 48 | 50 | B-3 | 3 | IPD A-3-03 / 50A | IPD B-3-03 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B308 | 425 BAY | 425B_ZTE POTN |  |  | ○ | 7-1-A-3-50-42 | 7-1-B-3-50-42 | 7-DaHall 1-A-3-50-42 | 7-DaHall 1-B-3-50-42 | 48 | 50 | A-3 | 42 | 48 | 50 | B-3 | 42 | IPD A-3-42 / 50A | IPD B-3-42 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  | IPD 2개 | 0 | 0 | 미사용 랙
[6 empty] | ○ | 7-1-A-3-50-43 | 7-1-B-3-50-43 | 7-DaHall 1-A-3-50-43 | 7-DaHall 1-B-3-50-43 | 48 | 50 | A-3 | 43 | 48 | 50 | B-3 | 43 | IPD A-3-43 / 50A | IPD B-3-43 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B309 | 424 BAY | 424B_ZTE385 |  |  | ○ | 7-1-A-3-50-27 | 7-1-B-3-50-27 | 7-DaHall 1-A-3-50-27 | 7-DaHall 1-B-3-50-27 | 48 | 50 | A-3 | 27 | 48 | 50 | B-3 | 27 | IPD A-3-27 / 50A | IPD B-3-27 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B310 | 423 BAY | 423B_코위버1664 |  |  | ○ | 7-1-A-3-50-26 | 7-1-B-3-50-26 | 7-DaHall 1-A-3-50-26 | 7-DaHall 1-B-3-50-26 | 48 | 50 | A-3 | 26 | 48 | 50 | B-3 | 26 | IPD A-3-26 / 50A | IPD B-3-26 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B315 | 420 BAY | 420B_DOTS |  |  | ○ | 7-1-A-3-35-53 | 7-1-B-3-35-52 | 7-DaHall 1-A-3-35-53 | 7-DaHall 1-B-3-35-52 | 48 | 35 | A-3 | 53 | 48 | 35 | B-3 | 52 | IPD A-3-53 / 35A | IPD B-3-52 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B316 | 419 BAY | Sejong Telecom Inc. |  |  | ○ | 7-1-A-2-35-52 | 7-1-B-2-35-52 | 7-DaHall 1-A-2-35-52 | 7-DaHall 1-B-2-35-52 | 48 | 35 | A-2 | 52 | 48 | 35 | B-2 | 52 | IPD A-2-52 / 35A | IPD B-2-52 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | SKB장비 |  | 0 | 0 | 미사용 랙
[5 empty] | ○ | [13 empty] | A: 1회로 사용(차단기 정보 조사 실패; 합계: 0 |  | 0 |  | 1회로. 차단기 정보 파악 불가 | 0 | 0 | 무부하 랙
| B317 | 418 BAY | 418B_SKB장비 |  |  | ○ | 7-1-A-2-35-49 | 7-1-B-2-35-49 | 7-DaHall 1-A-2-35-49 | 7-DaHall 1-B-2-35-49 | 48 | 35 | A-2 | 49 | 48 | 35 | B-2 | 49 | IPD A-2-49 / 35A | IPD B-2-49 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | SKB장비 |  | 0 | 0 | 미사용 랙
| B319 | 416 BAY | 416B_Patch |  | X | X | [32 empty] | 0 | 7F-5F OJC PATCH |  | 0 | 0 | 미사용 랙
| B320 | 415 BAY | 415B_Patch |  | X | X | [32 empty] | 0 | 7F-5F OJC PATCH |  | 0 | 0 | 미사용 랙
| B322 | 414 BAY | 414B_드림라인 |  |  | ○ | 7-1-A-2-35-10 | 7-1-B-2-35-10 | 7-DaHall 1-A-2-35-10 | 7-DaHall 1-B-2-35-10 | 48 | 35 | A-2 | 10 | 48 | 35 | B-2 | 10 | IPD A-2-10 / 35A | IPD B-2-10 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | 드림라인 장비 |  | 0 | 0 | 미사용 랙
| B323 | 413 BAY | Sejong Telecom Inc. |  | ○ | [13 empty] | A: U3-7A-08 / 2P 30A (405Bay 인출) | 0 | 0 | 7F-5F UTP PATCH | 405Bay에서 1회로 연결 사용 중 | 0 | 0 | 무부하 랙
| B402 | 331 BAY | 코위버 ROADM |  |  | ○ | 7-1-A-3-100-60 | 7-1-B-3-100-60 | 7-DaHall 1-A-3-100-60 | 7-DaHall 1-B-3-100-60 | 48 | 100 | A-3 | 60 | 48 | 100 | B-3 | 60 | IPD A-3-60 / 100A | IPD B-3-60 / 100A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  | 2022.02.10 전기구성 | 0 | 0 | 미사용 랙
| B403 | 330 BAY | 코위버 ROADM |  |  | ○ | 7-1-A-3-100-28 | 7-1-B-3-100-28 | 7-DaHall 1-A-3-100-28 | 7-DaHall 1-B-3-100-28 | 48 | 100 | A-3 | 28 | 48 | 100 | B-3 | 28 | IPD A-3-28 / 100A | IPD B-3-28 / 100A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  | 2022.02.10 전기구성 | 0 | 0 | 미사용 랙
| B404 | 329 BAY | 329B_ZTE385 |  |  | ○ | 7-1-A-3-50-15 | 7-1-B-3-50-15 | 7-DaHall 1-A-3-50-15 | 7-DaHall 1-B-3-50-15 | 48 | 50 | A-3 | 15 | 48 | 50 | B-3 | 15 | IPD A-3-15 / 50A | IPD B-3-15 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B405 | 328 BAY | 328B_ZTE385 |  |  | ○ | 7-1-A-3-50-16 | 7-1-B-3-50-16 | 7-DaHall 1-A-3-50-16 | 7-DaHall 1-B-3-50-16 | 48 | 50 | A-3 | 16 | 48 | 50 | B-3 | 16 | IPD A-3-16 / 50A | IPD B-3-16 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B406 | 327 BAY | 327B_ZTE385 |  |  | ○ | 7-1-A-3-50-17 | 7-1-B-3-50-17 | 7-DaHall 1-A-3-50-17 | 7-DaHall 1-B-3-50-17 | 48 | 50 | A-3 | 17 | 48 | 50 | B-3 | 17 | IPD A-3-17 / 50A | IPD B-3-17 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B407 | 326 BAY | 326B_코위버1664 |  |  | ○ | 7-1-A-3-35-23 | 7-1-B-3-35-24 | 7-DaHall 1-A-3-35-23 | 7-DaHall 1-B-3-35-24 | 48 | 35 | A-3 | 23 | 48 | 35 | B-3 | 24 | IPD A-3-23 / 35A | IPD B-3-24 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B408 | 325 BAY | 325B_코위버CWDM |  |  | ○ | 7-1-A-3-100-59 | 7-1-B-3-100-59 | 7-DaHall 1-A-3-100-59 | 7-DaHall 1-B-3-100-59 | 48 | 100 | A-3 | 59 | 48 | 100 | B-3 | 59 | IPD A-3-59 / 100A | IPD B-3-59 / 100A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  | 2012.02.09 설치 | 0 | 0 | 미사용 랙
| B409 | 324 BAY | [16 empty] | A: TR-7A 1000kVA |  | 0 |  |  | 0 | 0 | 미사용 랙
| B410 | 323 BAY |  |  |  | ○ | [12 empty] | A: TR-7A 1000kVA |  | 0 |  |  | 0 | 0 | 미사용 랙
| B411 | 322 BAY | Sejong Telecom Inc. |  | ○ |  | 7-1-A2-30-29 |  | 7-DaHall 1-PDU-01-30-29 |  | 220 | 30 | PDU-01 | 29 |  |  |  |  | A: U3-7A-29 / 2P 30A; A: U3-7A (U7-5A) 4P 300A; A: LV-7A #05 / 3P 320A (U7-5A); A: TR-7A 1000kVA; A전원: 0.003338; 합계: 0.003338; A전원: 0 | 0.079 | 0 | PTN 7200 UTP PATCH 예정 |  | 0 | 0 | 무부하 랙
| B415 | [37 empty] | 0 |  |  | 0 | 0 | 미사용 랙 | bar: A to B; A전원 to B전원
| B416 | 318 BAY | Digital Edge | 2.2 | ○ |  | 7-1-A2-30-18 | 7-1-B2-30-18 | 7-DaHall 1-PDU-01-30-18 | 7-DaHall 1-PDU-02-30-18 | 220 | 30 | PDU-01 | 18 | 220 | 30 | PDU-02 | 18 | U3-7A-18 / 2P 30A | U3-7B-18 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.7558 | 1.7399 | 3.4957 | 272 | 269.3 | 0.899 | 541.3 | 전기투입 : '22.02.24 | DEKR Networks Cabinet('22.02.09) | 0.72755 | 1.4724 | 적정함
| B417 | 317 BAY | Digital Edge | 2.2 | ○ |  | 7-1-A2-30-20 | 7-1-B2-30-20 | 7-DaHall 1-PDU-01-30-20 | 7-DaHall 1-PDU-02-30-20 | 220 | 30 | PDU-01 | 20 | 220 | 30 | PDU-02 | 20 | U3-7A-20 / 2P 30A | U3-7B-20 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.8689 | 1.9885 | 3.8574 | 291.1 | 313.9 | 1.065 | 605 | 전기투입 : '22.02.24 | DEKR Networks Cabinet('22.02.09) | 0.81317 | 1.3868 | 적정함
| B418 | 316 BAY | Digital Edge | 2.2 | ○ |  | 7-1-A2-30-22 | 7-1-B2-30-22 | 7-DaHall 1-PDU-01-30-22 | 7-DaHall 1-PDU-02-30-22 | 220 | 30 | PDU-01 | 22 | 220 | 30 | PDU-02 | 22 | U3-7A-22 / 2P 30A | U3-7B-22 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.7334 | 1.9621 | 3.6955 | 269.4 | 307.8 | 0.799 | 577.2 | 전기투입 : '22.02.24 | DEKR Networks Cabinet('22.02.09) | 0.77581 | 1.4242 | 적정함
| B419 | 315 BAY | Digital Edge | 2.2 | ○ |  | 7-1-A2-30-24 | 7-1-B2-30-24 | 7-DaHall 1-PDU-01-30-24 | 7-DaHall 1-PDU-02-30-24 | 220 | 30 | PDU-01 | 24 | 220 | 30 | PDU-02 | 24 | U3-7A-24 / 2P 30A | U3-7B-24 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.7407 | 2.2777 | 5.0184 | 426.1 | 343 | 1.223 | 769.1 | 전기투입 : '22.02.24 | DEKR Networks Cabinet('22.02.09) | 1.0337 | 1.1663 | 적정함
| B420 | 314 BAY | Digital Edge | 2.2 | ○ |  | 7-1-A2-30-26 | 7-1-B2-30-26 | 7-DaHall 1-PDU-01-30-26 | 7-DaHall 1-PDU-02-30-26 | 220 | 30 | PDU-01 | 26 | 220 | 30 | PDU-02 | 26 | U3-7A-26 / 2P 30A | U3-7B-26 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 3.4165 | 3.6147 | 7.0312 | 523.4 | 558.8 | 1.476 | 1082.2 | 전기투입 : '22.02.24 | DEKR Networks Cabinet('22.02.09) | 1.4546 | 0.74543 | 적정함
| B421 | 313 BAY | Digital Edge | 2.2 | ○ |  | 7-1-A2-30-28 | 7-1-B2-30-28 | 7-DaHall 1-PDU-01-30-28 | 7-DaHall 1-PDU-02-30-28 | 220 | 30 | PDU-01 | 28 | 220 | 30 | PDU-02 | 28 | U3-7A-28 / 2P 30A | U3-7B-28 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 5.5626 | 5.7776 | 11.3402 | 846 | 884.5 | 2.356 | 1730.5 | 전기투입 : '22.02.24 | DEKR Networks Cabinet('22.02.09) | 2.3259 | -0.12594 | 사용초과 | Digital Edge | B421
| B422 | 312 BAY | Digital Edge | 2.2 | ○ |  | 7-1-A2-30-40 | 7-1-B2-30-40 | 7-DaHall 1-PDU-01- 30AT-40 | 7-DaHall 1-PDU-02- 30AT-40 | 220V | 30AT | PDU-01 | 40 | 220V | 30AT | PDU-02 | 40 | A: U3-7A(U7-5A) 4P 300A; B: U3-7B(U7-6B) 4P 300A; A: LV-7A #05 / 3P 320A (U7-5A); B: LV-7B #06 / 3P 320A (U7-6B); A: TR-7A 1000kVA; B: TR-7B 1000kVA; A전원: 3.3906; B전원: 3.0254; 합계: 6.416; A전원: 482.4; B전원: 446.3 | 1.404 | 928.7 |  |  | 1.2483 | 0.95175 | 적정함
| B423 | 311 BAY | Digital Edge | 2.2 | ○ |  | 7-1-A2-30-38 | 7-1-B2-30-38 | 7-DaHall 1-PDU-01- 30AT-38 | 7-DaHall 1-PDU-02- 30AT-38 | 220V | 30AT | PDU-01 | 38 | 220V | 30AT | PDU-02 | 38 | A: U3-7A(U7-5A) 4P 300A; B: U3-7B(U7-6B) 4P 300A; A: LV-7A #05 / 3P 320A (U7-5A); B: LV-7B #06 / 3P 320A (U7-6B); A: TR-7A 1000kVA; B: TR-7B 1000kVA; A전원: 2.808; B전원: 3.8721; 합계: 6.6801; A전원: 396.7; B전원: 551.5 | 1.382 | 948.2 |  |  | 1.2745 | 0.92554 | 적정함
| B424 |  |  | 2.2 | ○ |  | 7-1-A2-30-36 | 7-1-B2-30-36 | 7-DaHall 1-PDU-01- 30AT-36 | 7-DaHall 1-PDU-02- 30AT-36 | 220V | 30AT | PDU-01 | 36 | 220V | 30AT | PDU-02 | 36 | A: U3-7A(U7-5A) 4P 300A; B: U3-7B(U7-6B) 4P 300A; A: LV-7A #05 / 3P 320A (U7-5A); B: LV-7B #06 / 3P 320A (U7-6B); A: TR-7A 1000kVA; B: TR-7B 1000kVA; A전원: 0; B전원: 0; 합계: 0; A전원: 0; B전원: 0 | 0 | 0 |  |  | 0 | 2.2 | 무부하 랙
| B502 | 231 BAY | 231B_ZTE385 |  |  | ○ | 7-1-A-3-35-22 | 7-1-B-3-35-22 | 7-DaHall 1-A-3-35-22 | 7-DaHall 1-B-3-35-22 | 48 | 35 | A-3 | 22 | 48 | 35 | B-3 | 22 | IPD A-3-22 / 35A | IPD B-3-22 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B503 | 230 BAY | 230B_ZTE385 |  |  | ○ | 7-1-A-3-35-51 | 7-1-B-3-35-51 | 7-DaHall 1-A-3-35-51 | 7-DaHall 1-B-3-35-51 | 48 | 35 | A-3 | 51 | 48 | 35 | B-3 | 51 | IPD A-3-51 / 35A | IPD B-3-51 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B504 | 229 BAY | 229B_ZTE385 |  |  | ○ | 7-1-A-3-35-50 | 7-1-B-3-35-50 | 7-DaHall 1-A-3-35-50 | 7-DaHall 1-B-3-35-50 | 48 | 35 | A-3 | 50 | 48 | 35 | B-3 | 50 | IPD A-3-50 / 35A | IPD B-3-50 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B505 | 228 BAY | 228B_ZTE385 |  |  | ○ | 7-1-A-3-50-49 | 7-1-B-3-35-49 | 7-DaHall 1-A-3-50-49 | 7-DaHall 1-B-3-35-49 | 48 | 50 | A-3 | 49 | 48 | 35 | B-3 | 49 | IPD A-3-49 / 50A | IPD B-3-49 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B506 | 227 BAY | 227B_ZTE385 |  |  | ○ | 7-1-A-3-50-21 | 7-1-B-3-50-21 | 7-DaHall 1-A-3-50-21 | 7-DaHall 1-B-3-50-21 | 48 | 50 | A-3 | 21 | 48 | 50 | B-3 | 21 | IPD A-3-21 / 50A | IPD B-3-21 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B507 | 226 BAY | 226B_코위버155M |  |  | ○ | 7-1-A-3-35-20 | 7-1-B-3-50-20 | 7-DaHall 1-A-3-35-20 | 7-DaHall 1-B-3-50-20 | 48 | 35 | A-3 | 20 | 48 | 50 | B-3 | 20 | IPD A-3-20 / 35A | IPD B-3-20 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B508 | 225 BAY | 225B_코위버622M |  |  | ○ | 7-1-A-3-35-52 | 7-1-B-3-35-23 | 7-DaHall 1-A-3-35-52 | 7-DaHall 1-B-3-35-23 | 48 | 35 | A-3 | 52 | 48 | 35 | B-3 | 23 | IPD A-3-52 / 35A | IPD B-3-23 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  | PDP 2개 | 0 | 0 | 미사용 랙
[6 empty] | ○ | 7-1-A-3-35-55 | 7-1-B-3-35-54 | 7-DaHall 1-A-3-35-55 | 7-DaHall 1-B-3-35-54 | 48 | 35 | A-3 | 55 | 48 | 35 | B-3 | 54 | IPD A-3-55 / 35A | IPD B-3-54 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B509 | 224 BAY | 224B_우리넷 |  |  | ○ | 7-1-A-3-35-19 | 7-1-B-3-50-19 | 7-DaHall 1-A-3-35-19 | 7-DaHall 1-B-3-50-19 | 48 | 35 | A-3 | 19 | 48 | 50 | B-3 | 19 | IPD A-3-19 / 35A | IPD B-3-19 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B510 | 223 BAY | 223B_코위버155M |  |  | ○ | 7-1-A-3-35-18 | 7-1-B-3-35-18 | 7-DaHall 1-A-3-35-18 | 7-DaHall 1-B-3-35-18 | 48 | 35 | A-3 | 18 | 48 | 35 | B-3 | 18 | IPD A-3-18 / 35A | IPD B-3-18 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B515 | 219 BAY | 219B_코위버PTN |  |  | ○ | 7-1-A-2-50-22 | 7-1-B-2-50-22 | 7-DaHall 1-A-2-50-22 | 7-DaHall 1-B-2-50-22 | 48 | 50 | A-2 | 22 | 48 | 50 | B-2 | 22 | IPD A-2-22 / 50A | IPD B-2-22 / 50A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B516 | 218 BAY | DEKR, Network Rack#2 | 2.2 | ○ |  | 7-1-A2-30-14 | 7-1-B2-30-14 | 7-DaHall 1-PDU-01-30-14 | 7-DaHall 1-PDU-02-30-14 | 220 | 30 | PDU-01 | 14 | 220 | 30 | PDU-02 | 14 | U3-7A-14 / 2P 30A | U3-7B-14 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 4.2837 | 3.0858 | 7.3695 | 671.6 | 365.5 | 1.483 | 1037.1 |  | 2022.01.12 전기투입 | 1.394 | 0.80605 | 적정함
| B517 | 217 BAY | DEKR, Network Rack#1 | 2.2 | ○ |  | 7-1-A2-30-16 | 7-1-B2-30-16 | 7-DaHall 1-PDU-01-30-16 | 7-DaHall 1-PDU-02-30-16 | 220 | 30 | PDU-01 | 16 | 220 | 30 | PDU-02 | 16 | U3-7A-16 / 2P 30A | U3-7B-16 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.3023 | 2.958 | 5.2603 | 335.5 | 410.3 | 1.079 | 745.8 |  | 2022.01.12 전기투입 | 1.0024 | 1.1976 | 적정함
|  | 216 BAY | [16 empty] | A: TR-7A 1000kVA; B: TR-7B 1000kVA |  | 0 |  |  | 0 | 0 | 미사용 랙
|  | 215 BAY | [16 empty] | A: TR-7A 1000kVA; B: TR-7B 1000kVA |  | 0 |  |  | 0 | 0 | 미사용 랙
|  | 214 BAY | [16 empty] | A: TR-7A 1000kVA; B: TR-7B 1000kVA |  | 0 |  |  | 0 | 0 | 미사용 랙
|  | 213 BAY | [16 empty] | A: TR-7A 1000kVA; B: TR-7B 1000kVA |  | 0 |  |  | 0 | 0 | 미사용 랙
| B524 | 212 BAY | 212B_코위버155M |  |  | ○ | 7-1-A-2-50-12 | 7-1-B-2-50-12 | 7-DaHall 1-A-2-50-12 | 7-DaHall 1-B-2-50-12 | 48 | 50 | A-2 | 12 | 48 | 50 | B-2 | 12 | IPD A-2-12 / 50A | IPD B-2-12 / 50A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
1열 | B615 | 121 BAY | 121B_ZTE325 |  |  | ○ | 7-1-A-2-50-66 | 7-1-B-2-50-66 | 7-DaHall 1-A-2-50-66 | 7-DaHall 1-B-2-50-66 | 48 | 50 | A-2 | 66 | 48 | 50 | B-2 | 66 | IPD A-2-66 / 50A | IPD B-2-66 / 50A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B616 | 120 BAY | 120B_ZTE325 |  |  | ○ | 7-1-A-2-50-67 | 7-1-B-2-50-67 | 7-DaHall 1-A-2-50-67 | 7-DaHall 1-B-2-50-67 | 48 | 50 | A-2 | 67 | 48 | 50 | B-2 | 67 | IPD A-2-67 / 50A | IPD B-2-67 / 50A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B617 | 119 BAY | 119B_우리넷 |  |  | ○ | 7-1-A-2-35-65 | 7-1-B-2-35-65 | 7-DaHall 1-A-2-35-65 | 7-DaHall 1-B-2-35-65 | 48 | 35 | A-2 | 65 | 48 | 35 | B-2 | 65 | IPD A-2-65 / 35A | IPD B-2-65 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B618 | 118 BAY | 118B_ZTE385 |  |  | ○ | 7-1-A-2-50-64 | 7-1-B-2-50-64 | 7-DaHall 1-A-2-50-64 | 7-DaHall 1-B-2-50-64 | 48 | 50 | A-2 | 64 | 48 | 50 | B-2 | 64 | IPD A-2-64 / 50A | IPD B-2-64 / 50A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B619 | 117 BAY | 117B_ZTE385 |  |  | ○ | 7-1-A-2-35-60 | 7-1-B-2-35-60 | 7-DaHall 1-A-2-35-60 | 7-DaHall 1-B-2-35-60 | 48 | 35 | A-2 | 60 | 48 | 35 | B-2 | 60 | IPD A-2-60 / 35A | IPD B-2-60 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B620 | 116 BAY | 116B_ZTE385 |  |  | ○ | 7-1-A-2-35-61 | 7-1-B-2-35-61 | 7-DaHall 1-A-2-35-61 | 7-DaHall 1-B-2-35-61 | 48 | 35 | A-2 | 61 | 48 | 35 | B-2 | 61 | IPD A-2-61 / 35A | IPD B-2-61 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B621 | 115 BAY | 115B_ZTE325 |  |  | ○ | 7-1-A-2-35-59 | 7-1-B-2-35-59 | 7-DaHall 1-A-2-35-59 | 7-DaHall 1-B-2-35-59 | 48 | 35 | A-2 | 59 | 48 | 35 | B-2 | 59 | IPD A-2-59 / 35A | IPD B-2-59 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B622 | 114 BAY | 114B_ZTE325 |  |  | ○ | 7-1-A-2-35-56 | 7-1-B-2-35-56 | 7-DaHall 1-A-2-35-56 | 7-DaHall 1-B-2-35-56 | 48 | 35 | A-2 | 56 | 48 | 35 | B-2 | 56 | IPD A-2-56 / 35A | IPD B-2-56 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B623 | 113 BAY | 113B_ZTE325 |  |  | ○ | 7-1-A-2-35-55 | 7-1-B-2-35-55 | 7-DaHall 1-A-2-35-55 | 7-DaHall 1-B-2-35-55 | 48 | 35 | A-2 | 55 | 48 | 35 | B-2 | 55 | IPD A-2-55 / 35A | IPD B-2-55 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B624 | 112 BAY | 112B_ZTE325 |  |  | ○ | 7-1-A-2-35-54 | 7-1-B-2-35-54 | 7-DaHall 1-A-2-35-54 | 7-DaHall 1-B-2-35-54 | 48 | 35 | A-2 | 54 | 48 | 35 | B-2 | 54 | IPD A-2-54 / 35A | IPD B-2-54 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| B625 | 111 BAY | 111B_ZTE325 |  |  | ○ | 7-1-A-2-35-57 | 7-1-B-2-35-57 | 7-DaHall 1-A-2-35-57 | 7-DaHall 1-B-2-35-57 | 48 | 35 | A-2 | 57 | 48 | 35 | B-2 | 57 | IPD A-2-57 / 35A | IPD B-2-57 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
|  | 508 BAY | [36 empty] | 0 |  |  | 0 | 0 | 미사용 랙
| C104 | 507 BAY | Sejong Telecom Inc. |  |  | ○ | 7-1-A-1-50-20 | 7-1-B-1-50-20 | 7-DaHall 1-A-1-50-20 | 7-DaHall 1-B-1-50-20 | 48 | 50 | A-1 | 20 | 48 | 50 | B-1 | 20 | IPD A-1-20 / 50A | IPD B-1-20 / 50A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | SKB장비 |  | 0 | 0 | 미사용 랙
|  |  |  | 2.2 | ○ | [13 empty] | A: 미상(A-E1 ??); B: 미상(UPS분전반(B) / E-20 ??); 합계: 0 | 0 | 0 |  | 랙 상부 위치 / 미사용 전원 | 0 | 2.2 | 무부하 랙
| C105 | 506 BAY | 506B_KT장비 |  |  | ○ | 7-1-A-1-35-11(1) | 7-1-B-1-35-14(1) | 7-DaHall 1-A-1-35-11(1) | 7-DaHall 1-B-1-35-14(1) | 48 | 35 | A-1 | 11(1) | 48 | 35 | B-1 | 14(1) | IPD A-1-11(1) / 35A | IPD B-1-14(1) / 35A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | KT장비 | PDP 2개 | 0 | 0 | 미사용 랙
[6 empty] | ○ | 7-1-A-1-35-15(2) | 7-1-B-1-35-15(2) | 7-DaHall 1-A-1-35-15(2) | 7-DaHall 1-B-1-35-15(2) | 48 | 35 | A-1 | 15(2) | 48 | 35 | B-1 | 15(2) | IPD A-1-15(2) / 35A | IPD B-1-15(2) / 35A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
|  | 505 BAY | [36 empty] | 0 |  |  | 0 | 0 | 미사용 랙
| C107 | 504 BAY | 504B_KT장비 |  |  | ○ | 7-1-B-1-35-16 | 7-1-A-1-35-16 | 7-DaHall 1-B-1-35-16 | 7-DaHall 1-A-1-35-16 | 48 | 35 | B-1 | 16 | 48 | 35 | A-1 | 16 | IPD B-1-16 / 35A | IPD A-1-16 / 35A | IPD B-1 | IPD A-1 | 정류기 B -48V 1400A | 정류기 A -48V 1400A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | [5 empty] | #N/A | 0 | KT장비 |  | 0 | 0 | 미사용 랙
| C108 | 503 BAY | 503B_KT장비 |  |  | ○ | 7-1-A-1-50-17 | 7-1-B-1-50-17 | 7-DaHall 1-A-1-50-17 | 7-DaHall 1-B-1-50-17 | 48 | 50 | A-1 | 17 | 48 | 50 | B-1 | 17 | IPD A-1-17 / 50A | IPD B-1-17 / 50A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | KT장비 |  | 0 | 0 | 미사용 랙
| C109 | 502 BAY | 502B_KT장비 |  |  | ○ | 7-1-A-1-50-56 | 7-1-B-1-50-56 | 7-DaHall 1-A-1-50-56 | 7-DaHall 1-B-1-50-56 | 48 | 50 | A-1 | 56 | 48 | 50 | B-1 | 56 | IPD A-1-56 / 50A | IPD B-1-56 / 50A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | KT장비 |  | 0 | 0 | 미사용 랙
5열 | C110 | 501 BAY | 501B_LGU+장비 |  |  | ○ | 7-1-A-1-100-19 | 7-1-B-1-100-19 | 7-DaHall 1-A-1-100-19 | 7-DaHall 1-B-1-100-19 | 48 | 100 | A-1 | 19 | 48 | 100 | B-1 | 19 | IPD A-1-19 / 100A | IPD B-1-19 / 100A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | LGU+장비 |  | 0 | 0 | 미사용 랙
| C201 | 410 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A1-30-32 | 7-1-B1-30-26 | 7-DaHall 1-RPP-01-30-32 | 7-DaHall 1-RPP-02-30-26 | 220 | 30 | RPP-01 | 32 | 220 | 30 | RPP-02 | 26 | UPS A1-32 / 2P 30A | UPS B1-26 / 2P 30A | UPS 출력분전반 A1 #32 | UPS 출력분전반 B1 #26 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 0 | 0.42936 | 0.42936 | 0 | 25.2 | 0.05 | 25.2 | PBX 교환기 |  | 0.033871 | 1.5661 | 적정함
| C202 | 409 BAY | Sejong Telecom Inc. | 1.6 | ○ | [13 empty] | A: UPS A1-12 / 2P 30A (408Bay 인출); B: UPS B1-17 / 2P 20A (408Bay 인출) | 0 | 0 |  | 408Bay에서 멀티탭 2개 연결 사용 중 | 0 | 1.6 | 무부하 랙
| C203 | 408 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A1-30-12 | 7-1-B1-20-17 | 7-DaHall 1-RPP-01-30-12 | 7-DaHall 1-RPP-02-20-17 | 220 | 30 | RPP-01 | 12 | 220 | 20 | RPP-02 | 17 | UPS A1-12 / 2P 30A | UPS B1-17 / 2P 20A | UPS 출력분전반 A1 #12 | UPS 출력분전반 B1 #17 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 4.1494 | 3.0968 | 7.2462 | 602.3 | 434.2 | 1.981 | 1036.5 |  |  | 1.3931 | 0.20685 | 적정함
| C204 | 407 BAY | Sejong Telecom Inc. |  |  | ○ | 7-1-A-1-35-44 | 7-1-B-1-35-6 | 7-DaHall 1-A-1-35-44 | 7-DaHall 1-B-1-35-6 | 48 | 35 | A-1 | 44 | 48 | 35 | B-1 | 6 | IPD A-1-44 / 35A | IPD B-1-06 / 35A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
|  |  |  | 1.6 | ○ |  | 7-1-A1-30-10 | 7-1-B1-20-15 | 7-DaHall 1-RPP-01-30-10 | 7-DaHall 1-RPP-02-20-15 | 220 | 30 | RPP-01 | 10 | 220 | 20 | RPP-02 | 15 | UPS A1-10 / 2P 30A | UPS B1-15 / 2P 20A | UPS 출력분전반 A1 #10 | UPS 출력분전반 B1 #15 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.6797 | 1.7634 | 3.4431 | 241.1 | 272 | 0.712 | 513.1 |  |  | 0.68965 | 0.91035 | 적정함
| C205 | 406 BAY | Sejong Telecom Inc. |  |  | ○ | 7-1-A-1-35-43 | 7-1-B-1-35-5 | 7-DaHall 1-A-1-35-43 | 7-DaHall 1-B-1-35-5 | 48 | 35 | A-1 | 43 | 48 | 35 | B-1 | 5 | IPD A-1-43 / 35A | IPD B-1-05 / 35A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
|  |  |  | 1.6 | ○ |  | 7-1-A1-30-8 | 7-1-B1-20-13 | 7-DaHall 1-RPP-01-30-8 | 7-DaHall 1-RPP-02-20-13 | 220 | 30 | RPP-01 | 8 | 220 | 20 | RPP-02 | 13 | UPS A1-08 / 2P 30A | UPS B1-13 / 2P 20A | UPS 출력분전반 A1 #08 | UPS 출력분전반 B1 #13 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.39 | 2.8659 | 5.2558 | 342.7 | 394 | 1.022 | 736.7 |  |  | 0.99019 | 0.60981 | 적정함
| C206 | 405 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-B1-20-9 | 7-1-A2-30-8 | 7-DaHall 1-PDU-01-30-8 | 7-DaHall 1-RPP-02-20-9 | 220 | 20 | RPP-02 | 9 | 220 | 30 | PDU-01 | 8 | UPS B1-09 / 2P 20A | U3-7A-08 / 2P 30A | UPS 출력분전반 B1 #09 |  | UPS 출력 분전반B1, 4P 400A |  | UPS 출력 분전반B, #02 3P 150A |  | UPS 출력 배전반B, 4P 400A | U3-7A(U7-5A) 4P 300A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #05 / 3P 320A (U7-5A) | TR-7B 1000kVA | TR-7A 1000kVA | 1.8243 | 1.1694 | 2.9938 | 269.9 | 186.7 | 0.82 | 456.6 |  |  | 0.61371 | 0.98629 | 적정함
| C207 | 404 BAY | Sejong Telecom Inc. | 1.6 | ○ | [13 empty] | B: 라벨 없음(B1 PNL에서 인출 추정); 합계: 0 | 0 | 0 | 인터넷팀 장비 |  | 0 | 1.6 | 무부하 랙
4열 | C208 | 403 BAY | Sejong Telecom Inc. | 1.6 | ○ | [13 empty] | B: 라벨 없음(B1 PNL에서 인출 추정); 합계: 0 | 0 | 0 | 인터넷팀 장비 |  | 0 | 1.6 | 무부하 랙
| C304 | 307 BAY | LGU+PDP |  |  | ○ | 7-1-A-1-100-24 | 7-1-B-1-100-24 | 7-DaHall 1-A-1-100-24 | 7-DaHall 1-B-1-100-24 | 48 | 100 | A-1 | 24 | 48 | 100 | B-1 | 24 | IPD A-1-24 / 100A | IPD B-1-24 / 100A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | LGU+ POP 장비 |  | 0 | 0 | 미사용 랙
| C305 | 306 BAY | 306B_SKB장비 |  |  | ○ | 7-1-A-1-100-7 | 7-1-B-1-100-7 | 7-DaHall 1-A-1-100-7 | 7-DaHall 1-B-1-100-7 | 48 | 100 | A-1 | 7 | 48 | 100 | B-1 | 7 | IPD A-1-07 / 100A | IPD B-1-07 / 100A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | SKB장비 |  | 0 | 0 | 미사용 랙
| C306 | 305 BAY | 305B_LGU+장비 |  |  | ○ | 7-1-A-1-50-57 | 7-1-B-1-50-57 | 7-DaHall 1-A-1-50-57 | 7-DaHall 1-B-1-50-57 | 48 | 50 | A-1 | 57 | 48 | 50 | B-1 | 57 | IPD A-1-57 / 50A | IPD B-1-57 / 50A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | LGU+장비 |  | 0 | 0 | 미사용 랙
| C307 | 304 BAY | 304B_KT장비 |  |  | ○ | 7-1-A-1-50-21 | 7-1-B-1-50-21 | 7-DaHall 1-A-1-50-21 | 7-DaHall 1-B-1-50-21 | 48 | 50 | A-1 | 21 | 48 | 50 | B-1 | 21 | IPD A-1-21 / 50A | IPD B-1-21 / 50A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | KT장비 |  | 0 | 0 | 미사용 랙
| C308 | 303 BAY | 303B_NDCS |  |  | ○ | 7-1-A-1-100-18 | 7-1-B-1-100-18 | 7-DaHall 1-A-1-100-18 | 7-DaHall 1-B-1-100-18 | 48 | 100 | A-1 | 18 | 48 | 100 | B-1 | 18 | IPD A-1-18 / 100A | IPD B-1-18 / 100A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
| C309 | 302 BAY | 302B_SKB |  |  | ○ | 7-1-A-1-100-23 | 7-1-B-1-100-23 | 7-DaHall 1-A-1-100-23 | 7-DaHall 1-B-1-100-23 | 48 | 100 | A-1 | 23 | 48 | 100 | B-1 | 23 | IPD A-1-23 / 100A | IPD B-1-23 / 100A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  |  | 0 | 0 | 미사용 랙
3열 | C310 | 301 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-30 | 7-1-B2-30-30 | 7-DaHall 1-PDU-01-30-30 | 7-DaHall 1-PDU-02-30-30 | 220 | 30 | PDU-01 | 30 | 220 | 30 | PDU-02 | 30 | U3-7A-30 / 2P 30A | U3-7B-30 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 0.34967 | 0.56793 | 0.9176 | 41.8 | 57.1 | 0.157 | 98.9 |  |  | 0.13293 | 1.4671 | 적정함
| C401 | 210 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-13 | 7-1-B2-30-13 | 7-DaHall 1-PDU-01-30-13 | 7-DaHall 1-PDU-02-30-13 | 220 | 30 | PDU-01 | 13 | 220 | 30 | PDU-02 | 13 | U3-7A-13 / 2P 30A | U3-7B-13 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 6.6294 | 5.2444 | 11.8739 | 1044.8 | 814.4 | 2.536 | 1859.2 | 인터넷팀 장비 | AC 콘센트 라벨 : 410Bay-A & 410Bay-B | 2.4989 | -0.89892 | 사용초과 | Sejong Telecom Inc. | C401
| C402 | 209 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-11 | 7-1-B2-30-11 | 7-DaHall 1-PDU-01-30-11 | 7-DaHall 1-PDU-02-30-11 | 220 | 30 | PDU-01 | 11 | 220 | 30 | PDU-02 | 11 | U3-7A-11 / 2P 30A | U3-7B-11 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 6.8332 | 5.6908 | 12.524 | 1005.9 | 808.9 | 2.499 | 1814.8 | 인터넷팀 장비 | AC 콘센트 라벨 : 409Bay-A & 409Bay-B | 2.4392 | -0.83925 | 사용초과 | Sejong Telecom Inc. | C402
| C403 | 208 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-17 | 7-1-B2-30-17 | 7-DaHall 1-PDU-01-30-17 | 7-DaHall 1-PDU-02-30-17 | 220 | 30 | PDU-01 | 17 | 220 | 30 | PDU-02 | 17 | U3-7A-17 / 2P 30A | U3-7B-17 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.9146 | 3.3793 | 13.3734 | 442 | 553.1 | 1.484 | 995.1 | 인터넷팀 장비 |  | 1.3375 | 0.2625 | 적정함
[5 empty] | ○ |  | 7-1-A2-30-27 | 7-1-B2-30-27 | 7-DaHall 1-PDU-01-30-27 | 7-DaHall 1-PDU-02-30-27 | 220 | 30 | PDU-01 | 27 | 220 | 30 | PDU-02 | 27 | U3-7A-27 / 2P 30A | U3-7B-27 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 3.2932 | 3.7863 |  | 535.6 | 599.3 | 1.67 | 1134.9 |  |  | 1.5254 | -1.5254 | 사용초과 | 0 | 0
| C404 | 207 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-19 | 7-1-B2-30-19 | 7-DaHall 1-PDU-01-30-19 | 7-DaHall 1-PDU-02-30-19 | 220 | 30 | PDU-01 | 19 | 220 | 30 | PDU-02 | 19 | U3-7A-19 / 2P 30A | U3-7B-19 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 3.9278 | 8.9772 | 12.9049 | 602.4 | 1380.9 | 2.786 | 1983.3 | 인터넷팀 장비 |  | 2.6657 | -1.0657 | 사용초과 | Sejong Telecom Inc. | C404
| C405 | 206 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-21 | 7-1-B2-30-21 | 7-DaHall 1-PDU-01-30-21 | 7-DaHall 1-PDU-02-30-21 | 220 | 30 | PDU-01 | 21 | 220 | 30 | PDU-02 | 21 | U3-7A-21 / 2P 30A | U3-7B-21 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 3.95 | 4.0522 | 8.0022 | 606.7 | 626.8 | 1.791 | 1233.5 | 인터넷팀 장비 |  | 1.6579 | -0.05793 | 사용초과 | Sejong Telecom Inc. | C405
| C406 | 205 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-23 | 7-1-B2-30-23 | 7-DaHall 1-PDU-01-30-23 | 7-DaHall 1-PDU-02-30-23 | 220 | 30 | PDU-01 | 23 | 220 | 30 | PDU-02 | 23 | U3-7A-23 / 2P 30A | U3-7B-23 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.8176 | 2.6319 | 4.4494 | 273.4 | 397.2 | 1.021 | 670.6 | 인터넷팀 장비 |  | 0.90134 | 0.69866 | 적정함
| C407 | 204 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-25 | 7-1-B2-30-25 | 7-DaHall 1-PDU-01-30-25 | 7-DaHall 1-PDU-02-30-25 | 220 | 30 | PDU-01 | 25 | 220 | 30 | PDU-02 | 25 | U3-7A-25 / 2P 30A | U3-7B-25 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.4568 | 1.7329 | 3.1898 | 225.6 | 268.3 | 0.734 | 493.9 | 인터넷팀 장비 |  | 0.66384 | 0.93616 | 적정함
| C408 | 203 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-32 | 7-1-B2-30-32 | 7-DaHall 1-PDU-01-30-32 | 7-DaHall 1-PDU-02-30-32 | 220 | 30 | PDU-01 | 32 | 220 | 30 | PDU-02 | 32 | U3-7A-32 / 2P 30A | U3-7B-32 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.1083 | 1.8987 | 4.0069 | 291.8 | 246.1 | 0.762 | 537.9 | 세종 긴급청약 | 22.07.14 구성 및 전기투입 | 0.72298 | 0.87702 | 적정함
2열 | C409 | 202 BAY | Sejong Telecom Inc. | 2.2 | ○ |  | 7-1-A2-30-41 | 7-1-B2-30-41 | 7-DaHall 1-PDU-01-30-41 | 7-DaHall 1-PDU-02-30-41 | 220 | 30 | PDU-01 | 41 | 220 | 30 | PDU-02 | 41 | U3-7A-32 / 2P 30A | U3-7B-32 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.0602 | 0 | 1.0602 | 128.2 | 0 | 0.18 | 128.2 |  | '23.07. 31 전기투입/세종요청 1랙 증설 | 0.17231 | 2.0277 | 적정함
G열 | C501 | G10 | Shinhan financial Investment | 1.1 | ○ |  | 7-1-A1-20-19 | 7-1-B1-30-10 | 7-DaHall 1-RPP-01-20-19 | 7-DaHall 1-RPP-02-30-10 | 220 | 20 | RPP-01 | 19 | 220 | 30 | RPP-02 | 10 | UPS A1-19 (A1-L-10) / 2P 20A | UPS B1-10 (B1-R-5) / 2P 30A | UPS 출력분전반 A1 #19 | UPS 출력분전반 B1 #10 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.0023 | 0.66886 | 1.6712 | 111.9 | 76.3 | 0.28 | 188.2 | IDC 고객 (신한금융투자) |  | 0.25296 | 0.84704 | 적정함
| C502 | G09 | Quad Miner | 4 | ○ |  | 7-1-A2-30-44 | 7-1-B2-30-44 | 7-DaHall 1-PDU-01-30-44 | 7-DaHall 1-PDU-02-30-44 | 220 | 30 | PDU-01 | 44 | 220 | 30 | PDU-02 | 44 | U3-7A-44 / 2P 30A | U3-7B-44 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 6.7731 | 2.3385 | 9.1116 | 1065.9 | 317.7 | 2.434 | 1383.6 | 쿼드마이너 |  | 1.8597 | 2.1403 | 적정함
| C503 | G08 | Quad Miner |  | ○ |  | 7-1-A2-30-2 | 7-1-B2-30-2 | 7-DaHall 1-PDU-01-30-2 | 7-DaHall 1-PDU-02-30-2 | 220 | 30 | PDU-01 | 2 | 220 | 30 | PDU-02 | 2 | U3-7A-02 / 2P 30A | U3-7B-02 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 쿼드마이너('24.01 예정) |  | 0 | 0 | 무부하 랙
| C504 | G07 | 7F-G07 랙 |  |  | ○ | 7-1-A-1-35-50 | 7-1-B-1-50-47 | 7-DaHall 1-A-1-35-50 | 7-DaHall 1-B-1-50-47 | 48 | 35 | A-1 | 50 | 48 | 50 | B-1 | 47 | IPD A-1-50 / 35A | IPD B-1-47 / 50A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 |  | DC FUSE 제거/미사용 | 0 | 0 | 미사용 랙
[5 empty] | ○ |  | 7-1-A2-30-46 | 7-1-B2-30-46 | 7-DaHall 1-PDU-01-30-46 | 7-DaHall 1-PDU-02-30-46 | 220 | 30 | PDU-01 | 46 | 220 | 30 | PDU-02 | 46 | U3-7A-46 / 2P 30A | U3-7B-46 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 쿼드마이너(미정) |  | 0 | 0 | 무부하 랙
| C505 | G06 |  |  | ○ |  | 7-1-B1-30-18 | 7-1-A1-30-24 | 7-DaHall 1-RPP-01-30-24 | 7-DaHall 1-RPP-02-30-18 | 220 | 30 | RPP-02 | 18 | 220 | 30 | RPP-01 | 24 | UPS B1-18 / 2P 30A | UPS A1-24 / 2P 30A | UPS 출력분전반 B1 #18 | UPS 출력분전반 A1 #24 | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | IDC 고객 (NTT #5) |  | 0 | 0 | 무부하 랙
| C506 | G05 |  |  | ○ |  | 7-1-B1-20-29 | 7-1-A1-20-33 | 7-DaHall 1-RPP-01-20-33 | 7-DaHall 1-RPP-02-20-29 | 220 | 20 | RPP-02 | 29 | 220 | 20 | RPP-01 | 33 | UPS B1-29 / 2P 20A | UPS A1-33 / 2P 20A | UPS 출력분전반 B1 #29 | UPS 출력분전반 A1 #33 | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | IDC 고객 (NTT #6) |  | 0 | 0 | 무부하 랙
| C507 | G04 |  |  | ○ |  | 7-1-B1-30-16 | 7-1-A1-30-22 | 7-DaHall 1-RPP-01-30-22 | 7-DaHall 1-RPP-02-30-16 | 220 | 30 | RPP-02 | 16 | 220 | 30 | RPP-01 | 22 | UPS B1-16 / 2P 30A | UPS A1-22 / 2P 30A | UPS 출력분전반 B1 #16 | UPS 출력분전반 A1 #22 | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | IDC 고객 (NTT #7) |  | 0 | 0 | 무부하 랙
| C508 | G03 |  |  | ○ |  | 7-1-A2-30-1 | 7-1-B2-30-1 | 7-DaHall 1-PDU-01-30-1 | 7-DaHall 1-PDU-02-30-1 | 220 | 30 | PDU-01 | 1 | 220 | 30 | PDU-02 | 1 | U3-7A-01 / 2P 30A | U3-7B-01 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | IDC 고객 (NTT #8) |  | 0 | 0 | 무부하 랙
[5 empty] | ○ |  | 7-1-A2-30-12 | 7-1-B2-30-12 | 7-DaHall 1-PDU-01-30-12 | 7-DaHall 1-PDU-02-30-12 | 220 | 30 | PDU-01 | 12 | 220 | 30 | PDU-02 | 12 | U3-7A-12 / 2P 30A | U3-7B-12 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| C509 | G02 | 7F-G02 랙 | [15 empty] | 합계: 0 | 0 | 0 | 미사용 랙 (빈 랙) |  | 0 | 0 | 미사용 랙
[19 empty] | B: TR-7B 1000kVA |  | 0 |  | AC 전원 철거 | 0 | 0 | 미사용 랙
| C510 | G01 | 7F-G01 랙 | [15 empty] | 합계: 0 |  | 0 | LG HELLOVISION (빈 랙) |  | 0 | 0 | 미사용 랙
F열 | C601 | [37 empty] | 0 |  |  | 0 | 0 | 미사용 랙
| C602 | F09 |  |  | ○ |  | 7-1-A1-20-39 | 7-1-B1-30-40 | 7-DaHall 1-RPP-01-20-39 | 7-DaHall 1-RPP-02-30-40 | 220 | 20 | RPP-01 | 39 | 220 | 30 | RPP-02 | 40 | UPS A1-39 / 2P 20A | UPS B1-40 / 2P 30A | UPS 출력분전반 A1 #39 | UPS 출력분전반 B1 #40 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 미사용 랙 (빈 랙) | C509, A회로 이설(12/7) | 0 | 0 | 무부하 랙
| C603 | F08 |  |  |  | ○ | 7-1-B-5-35-40 | 7-1-A-5-35-41 | 7-DaHall 1-B-5-35-40 | 7-DaHall 1-A-5-35-41 | 48 | 35 | B-5 | 40 | 48 | 35 | A-5 | 41 | IPD B-5-F40 (구 IPD A) / 35A | IPD A-5-F41 (구 IPD B) / 35A | IPD B-5 (구 IPD A) | IPD A-5 (구 IPD B) | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | 미사용 랙 (빈 랙) | DC FUSE 삽입상태 /DC PDP 미사용 중 | 0 | 0 | 미사용 랙
[5 empty] | ○ |  | 7-1-A1-20-35 | 7-1-B1-30-34 | 7-DaHall 1-RPP-01-20-35 | 7-DaHall 1-RPP-02-30-34 | 220 | 20 | RPP-01 | 35 | 220 | 30 | RPP-02 | 34 | UPS A1-35 / 2P 20A | UPS B1-34 / 2P 30A | UPS 출력분전반 A1 #35 | UPS 출력분전반 B1 #34 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | C510, A회로 이설(12/7) | 0 | 0 | 무부하 랙
| C604 | F07 | CARANG | 2.2 | ○ |  | 7-1-A1-30-18 | 7-1-B2-30-29 | 7-DaHall 1-RPP-01-30-18 | 7-DaHall 1-PDU-02-30-29 | 220 | 30 | RPP-01 | 18 | 220 | 30 | PDU-02 | 29 | UPS A1-18 / 2P 30A | U3-7B-29 / 2P 30A | UPS 출력분전반 A1 #18 |  | UPS 출력 분전반A1, 4P 400A |  | UPS 출력 분전반A, #01 4P 225A |  | UPS 출력 배전반A, 4P 400A | U3-7B(U7-6B) 4P 300A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.5619 | 1.8013 | 3.3631 | 212.4 | 0 | 0.95 | 212.4 | 미사용 랙 (빈 랙) |  | 0.28548 | 1.9145 | 적정함
| C605 | F06 | Delphicom Co., Ltd. | 2.2 | ○ |  |  | 7-1-B1-30-36 |  | 7-DaHall 1-RPP-02-30-36 |  |  |  |  | 220 | 30 | RPP-02 | 36 | B: UPS B1-36 / 2P 30A; B: UPS 출력분전반 B1 #36; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 7.3429; 합계: 7.3429; B전원: 1098.2 | 1.693 | 1098.2 | IDC 고객 (델피콤) |  | 1.4761 | 0.72392 | 적정함
| C606 | F05 | Delphicom Co., Ltd. | 1.1 | ○ |  | 7-1-A2-30-3 | 7-1-A1-30-16 | 7-DaHall 1-PDU-01-30-3 | 7-DaHall 1-RPP-01-30-16 | 220 | 30 | PDU-01 | 3 | 220 | 30 | RPP-01 | 16 | U3-7A-03 / 2P 30A | UPS A1-16 / 2P 30A |  | UPS 출력분전반 A1 #16 |  | UPS 출력 분전반A1, 4P 400A |  | UPS 출력 분전반A, #01 4P 225A | U3-7A(U7-5A) 4P 300A | UPS 출력 배전반A, 4P 400A | LV-7A #05 / 3P 320A (U7-5A) | LV-7A #06 / 3P 320A (U7-6A) | TR-7A 1000kVA |  | 2.4923 | 2.6061 | 5.0984 | 349.5 | 232 | 0.929 | 581.5 | IDC 고객 (델피콤) |  | 0.78159 | 0.31841 | 적정함
| C607 | F04 | Feather-IT | 2.2 | ○ |  | 7-1-A1-30-26 | 7-1-B1-30-20 | 7-DaHall 1-RPP-01-30-26 | 7-DaHall 1-RPP-02-30-20 | 220 | 30 | RPP-01 | 26 | 220 | 30 | RPP-02 | 20 | UPS A1-26 / 2P 30A | UPS B1-26 / 2P 30A | UPS 출력분전반 A1 #26 | UPS 출력분전반 B1 #20 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 3.3147 | 0.6567 | 3.9714 | 541.3 | 87.6 | 1.253 | 628.9 | 2023.11.06 설치 (패더IT) |  | 0.8453 | 1.3547 | 적정함
| C608 | F03 | 7F-F03 랙 | [35 empty] | 0 |  |  | 0 | 0 | 미사용 랙 | bar: A; A to B전원
| C609 | F02 | 7F-F02 랙 |  |  | ○ | [12 empty] | IPD A-1-52 | IPD B-1-52 | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [6 empty] | 0 | IDC 고객 (NTT) | DC FUSE 제거/미사용(2021.01.19) | 0 | 0 | 미사용 랙
| C610 | F01 | 7F-F01 랙 |  |  | ○ | 7-1-A-1-35-51 | 7-1-B-1-35-51 | 7-DaHall 1-A-1-35-51 | 7-DaHall 1-B-1-35-51 | 48 | 35 | A-1 | 51 | 48 | 35 | B-1 | 51 | IPD A-1-51 / 35A | IPD B-1-51 / 35A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | IDC 고객 (NTT) |  | 0 | 0 | 미사용 랙
E열 | C701 | [37 empty] | 0 |  |  | 0 | 0 | 미사용 랙
| C702 | E09 | eBID | 2.2 | ○ |  | 7-1-B1-30-30 | 7-1-A1--36 | 7-DaHall 1-RPP-01--36 | 7-DaHall 1-RPP-02-30-30 | 220 | 30 | RPP-02 | 30 |  |  | RPP-01 | 36 | UPS B1-30 / 2P 30A | UPS A1-36 / 2P 30A | UPS 출력분전반 B1 #30 | UPS 출력분전반 A1 #36 | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | 3.4232 | 1.8465 | 5.2696 | 527.9 | 268.5 | 1.31 | 796.4 | IDC 고객 (르네트) |  | 1.0704 | 1.1296 | 적정함
| C703 | E08 | Exanet | 0.55 | ○ |  | 7-1-B1-20-27 | 7-1-A1-30-14 | 7-DaHall 1-RPP-01-30-14 | 7-DaHall 1-RPP-02-20-27 | 220 | 20 | RPP-02 | 27 | 220 | 30 | RPP-01 | 14 | UPS B1-27 / 2P 20A | UPS A1-14 / 2P 30A | UPS 출력분전반 B1 #27 | UPS 출력분전반 A1 #14 | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | 6.4544 | 5.8135 | 12.2679 | 996.5 | 900.8 | 2.816 | 1897.3 | IDC 고객 (엑사넷) |  | 2.5501 | -2.0001 | 사용초과 | Exanet | C703
| C704 | E07 |  |  | ○ |  |  | 7-1-B1-20-25 |  | 7-DaHall 1-RPP-02-20-25 |  |  |  |  | 220 | 20 | RPP-02 | 25 | B: UPS B1-25 / 2P 20A; B: UPS 출력분전반 B1 #25; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 0; 합계: 0; B전원: 0 | 0 | 0 | 미사용 랙 (빈 랙) |  | 0 | 0 | 무부하 랙
| C705 | E06 |  |  | ○ |  |  | 7-1-B1-20-23 |  | 7-DaHall 1-RPP-02-20-23 |  |  |  |  | 220 | 20 | RPP-02 | 23 | B: UPS B1-23 / 2P 20A; B: UPS 출력분전반 B1 #23; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 0; 합계: 0; B전원: 0 | 0 | 0 | 미사용 랙 (빈 랙) |  | 0 | 0 | 무부하 랙
| C706 | E05 |  |  | ○ |  |  | 7-1-B1-20-21 |  | 7-DaHall 1-RPP-02-20-21 |  |  |  |  | 220 | 20 | RPP-02 | 21 | B: UPS B1-21 / 2P 20A; B: UPS 출력분전반 B1 #21; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 0; 합계: 0; B전원: 0 | 0 | 0 | IDC 고객 (니즈텔레콤) |  | 0 | 0 | 무부하 랙
| C707 | E04 | Net People Co., Ltd. | 2.2 | ○ |  | 7-1-A1-30-4 |  | 7-DaHall 1-RPP-01-30-4 |  | 220 | 30 | RPP-01 | 4 |  |  |  |  | A: UPS A1-04 / 2P 30A; A: UPS 출력분전반 A1 #04; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 0 | 0 | 0 | IDC 고객 (넷피플) |  | 0 | 2.2 | 무부하 랙
| C708 | E03 |  |  | ○ |  | 7-1-A1-30-6 |  | 7-DaHall 1-RPP-01-30-6 |  | 220 | 30 | RPP-01 | 6 |  |  |  |  | A: UPS A1-06 / 2P 30A; A: UPS 출력분전반 A1 #06; A전원: 0; 합계: 0; A전원: 0 | 0 | 0 | IDC 고객 (넷피플) |  | 0 | 0 | 무부하 랙
| C709 | E02 |  |  | ○ |  |  | 7-1-B1-20-19 |  | 7-DaHall 1-RPP-02-20-19 |  |  |  |  | 220 | 20 | RPP-02 | 19 | B: UPS B1-19 / 2P 20A; B: UPS 출력분전반 B1 #19; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 0; 합계: 0; B전원: 0 | 0 | 0 | 미사용 랙 (빈 랙) |  | 0 | 0 | 무부하 랙
| C710 | E01 | 7F-E01 랙 |  | X | X | [32 empty] | 0 | IDC / 압류장비 |  | 0 | 0 | 미사용 랙
D열 | C801 | [37 empty] | 0 |  |  | 0 | 0 | 미사용 랙
| C802 | D07 | Needs Telecom |  | ○ |  |  | 7-1-A1-20-11 | 7-DaHall 1-RPP-01-20-11 | [5 empty] | 220 | 20 | RPP-01 | 11 | B: UPS A1-11 / 2P 20A; B: UPS 출력분전반 A1 #11; B: UPS 출력 분전반A1, 4P 400A; B: UPS 출력 분전반A, #01 4P 225A; B: UPS 출력 배전반A, 4P 400A; B: LV-7A #06 / 3P 320A (U7-6A); B: TR-7A 1000kVA; A전원: 0; 합계: 3.4779; A전원: 0 | 0 | 0 | IDC 고객 (니즈텔레콤) | 미사용 회로로 판단됨. 12월 계측시 0A면 삭제 예정 | 0 | 0 | 무부하 랙
|  |  |  | 2.2 | ○ |  | 7-1-B1-30-32 | 7-1-A1-30-38 | 7-DaHall 1-RPP-01-30-38 | 7-DaHall 1-RPP-02-30-32 | 220 | 30 | RPP-02 | 32 | 220 | 30 | RPP-01 | 38 | UPS B1-32 / 2P 30A | UPS A1-38 / 2P 30A | UPS 출력분전반 B1 #32 | UPS 출력분전반 A1 #38 | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 분전반A, #01 4P 225A | UPS 출력분전반B 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | 2.2006 | 3.4779 |  | 321.6 | 546.4 | 1.231 | 868 |  |  | 1.1667 | 1.0333 | 적정함
| C803 | D06 |  |  | ○ |  | 7-1-B1-30-28 | 7-1-A1-30-34 | 7-DaHall 1-RPP-01-30-34 | 7-DaHall 1-RPP-02-30-28 | 220 | 30 | RPP-02 | 28 | 220 | 30 | RPP-01 | 34 | UPS B1-28 / 2P 30A | UPS A1-34 / 2P 30A | UPS 출력분전반 B1 #28 | UPS 출력분전반 A1 #14 | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 분전반A, #01 4P 225A | UPS 출력분전반B 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | IDC 고객 (??) |  | 0 | 0 | 무부하 랙
| C804 | D05 | NTT KOREA Co., Ltd. | 1.1 | ○ |  | 7-1-A2-30-6 | 7-1-B2-30-6 | 7-DaHall 1-PDU-01-30-6 | 7-DaHall 1-PDU-02-30-6 | 220 | 30 | PDU-01 | 6 | 220 | 30 | PDU-02 | 6 | U3-7A-06 / 2P 30A | U3-7B-06 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 0 | 0 | 0.57012 | 0 | 0 | 0 | 0 | IDC 고객 (NTT) | 미사용 회로. 랙 상부 방치 중(12/6 확인) | 0 | 1.1 | 무부하 랙
[7 empty] | 7-1-A2-30-54 | 7-1-B2-30-53 | 7-DaHall 1-PDU-01-30-54 | 7-DaHall 1-PDU-02-30-53 | 220 | 30 | PDU-01 | 54 | 220 | 30 | PDU-02 | 53 | A: U3-7A-54 / 2P 30A; B: U3-7B-53 / 2P 30A; A: U3-7A(U7-5A) 4P 300A; B: U3-7B(U7-6B) 4P 300A; A: LV-7A #05 / 3P 320A (U7-5A); B: LV-7B #06 / 3P 320A (U7-6B); A: TR-7A 1000kVA; B: TR-7B 1000kVA; A전원: 0.34008; B전원: 0.23004 | 0.115 | 0 |  |  | 0 | 0 | 미사용 랙
| C805 | D04 | NTT KOREA Co., Ltd. | 1.1 | ○ |  | 7-1-A3-50-2 | 7-1-B3-50-2 | 7-DaHall 1-RPP-03-50-2 | 7-DaHall 1-RPP-04-50-2 | 220 | 50 | RPP-03 | 2 | 220 | 50 | RPP-04 | 2 | UPS A2-02 / 2P 50A | UPS B2-02 / 2P 50A | UPS 출력분전반 A2 #02 | UPS 출력분전반 B2 #01 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 0.88832 | 1.744 | 2.6323 | 130.6 | 257.7 | 0.64 | 388.3 | IDC 고객 (NTT_스미세이) |  | 0.52191 | 0.57809 | 적정함
| C806 | D03 | UNSYS Co., Ltd. | 2.2 | ○ |  |  | 7-1-B1-30-14 |  | 7-DaHall 1-RPP-02-30-14 |  |  |  |  | 220 | 30 | RPP-02 | 14 | B: UPS B1-14 / 2P 30A; B: UPS 출력분전반 B1 #14; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 14.0604; 합계: 14.0604; B전원: 2196.2 | 3.312 | 2196.2 | IDC 고객 (유엔시스) |  | 2.9519 | -0.75188 | 사용초과 | UNSYS Co., Ltd. | C806
| C807 | D02 |  |  | ○ | [13 empty] | A: 1회로 구성(미사용), 차단기 파악 실패. A1 또는 B1 PNL 의심; 합계: 0 | 0 | 0 | IDC / 압류장비 | 1회로 구성(미사용) | 0 | 0 | 무부하 랙
| C808 | D01 |  |  | ○ |  | 7-1-A2-30-4 | 7-1-B2-30-4 | 7-DaHall 1-PDU-01-30-4 | 7-DaHall 1-PDU-02-30-4 | 220 | 30 | PDU-01 | 4 | 220 | 30 | PDU-02 | 4 | U3-7A-04 / 2P 30A | U3-7B-04 / 2P 30A | [6 empty] | U3-7A 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 미사용 랙 (빈 랙) |  | 0 | 0 | 무부하 랙
|  | QDF | [36 empty] | 0 |  |  | 0 | 0 | 미사용 랙
|  | QDF | [36 empty] | 0 |  |  | 0 | 0 | 미사용 랙
C열 | C901 | [37 empty] | 0 |  |  | 0 | 0 | 미사용 랙
| C902 | C08 | IT Train | 2.2 | ○ |  | 7-1-A1-20-23 | 7-1-B1-30-12 | 7-DaHall 1-RPP-01-20-23 | 7-DaHall 1-RPP-02-30-12 | 220 | 20 | RPP-01 | 23 | 220 | 30 | RPP-02 | 12 | UPS A1-23 / 2P 20A | UPS B1-12 / 2P 30A | UPS 출력분전반 A1 #23 | UPS 출력분전반 B1 #12 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력배전반A, 4P 400A | UPS 출력분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.5585 | 4.3486 | 5.9071 | 203.2 | 622.5 | 1.288 | 825.7 | IDC 고객(IT Train - 사조2차) |  | 1.1098 | 1.0902 | 적정함
| C903 | C07 | IT Train | 2.2 | ○ |  | 7-1-A1-20-37 | 7-1-B1-30-8 | 7-DaHall 1-RPP-01-20-37 | 7-DaHall 1-RPP-02-30-8 | 220 | 20 | RPP-01 | 37 | 220 | 30 | RPP-02 | 8 | UPS A1-37 / 2P 20A | UPS B1-08 / 2P 30A | UPS 출력분전반 A1 #37 | UPS 출력분전반 B1 #08 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력배전반A, 4P 400A | UPS 출력분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 6.1548 | 6.0969 | 12.2517 | 922.1 | 903.6 | 2.801 | 1825.7 | IDC 고객(IT Train - 사조2차) |  | 2.4539 | -0.2539 | 사용초과 | IT Train | C903
| C904 | C06 | IT Train | 2.2 | ○ |  | 7-1-A2-30-10 | 7-1-B2-30-10 | 7-DaHall 1-PDU-01-30-10 | 7-DaHall 1-PDU-02-30-10 | 220 | 30 | PDU-01 | 10 | 220 | 30 | PDU-02 | 10 | U3-7A-10 / 2P 30A | U3-7B-10 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U3-7A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.39 | 3.4529 | 5.8429 | 341.9 | 516.1 | 1.49 | 858 | IDC 고객(IT Train - 사조2차) |  | 1.1532 | 1.0468 | 적정함
| C905 |  | IT Train | 2.2 | ○ |  | 7-1-A2-30-42 | 7-1-B2-30-42 | 7-DaHall 1-PDU-01-30-42 | 7-DaHall 1-PDU-02-30-42 | 220 | 30 | PDU-01 | 42 | 220 | 30 | PDU-02 | 42 | U3-7A-42 / 2P 30A | U3-7B-42 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U3-7A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 3.3412 | 4.4681 | 7.8093 | 493.8 | 656.8 | 1.699 | 1150.6 | IDC 고객(IT Train - 사조2차) |  | 1.5465 | 0.65349 | 적정함
| C907 | C04 | 7F-C04 랙 | [35 empty] | 0 | 미설치 (랙 없음) |  | 0 | 0 | 미사용 랙
| C908 | C03 | 7F-C03 랙 | [35 empty] | 0 | 미설치 (랙 없음) |  | 0 | 0 | 미사용 랙
| C909 | C02 | Sejong Telecom Inc. | 2.2 | ○ |  | 7-1-A2-30-34 | 7-1-B2-30-34 | 7-DaHall 1-PDU-01-30-34 | 7-DaHall 1-PDU-02-30-34 | 220 | 30 | PDU-01 | 34 | 220 | 30 | PDU-02 | 34 | U3-7A-34 / 2P 30A | U3-7B-34 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | IDC 고객(타타커뮤니케이션즈) |  | 0 | 2.2 | 무부하 랙
| C910 | C01 | Sejong Telecom Inc. |  |  | ○ | 7-1-B-5-100-48 | 7-1-B-1-100-41 | 7-DaHall 1-B-5-100-48 | 7-DaHall 1-B-1-100-41 | 48 | 100 | B-5 | 48 | 48 | 100 | B-1 | 41 | IPD B-5-F48 (구 IPD A) / 100A | IPD B-1-41 / 100A | IPD B-5 (구 IPD A) | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | IDC 고객(타타커뮤니케이션즈) | DC전원 장비직결 | 0 | 0 | 미사용 랙
|  |  |  | 2.2 | ○ |  | 7-1-A2-30-15 | 7-1-B2-30-15 | 7-DaHall 1-PDU-01-30-15 | 7-DaHall 1-PDU-02-30-15 | 220 | 30 | PDU-01 | 15 | 220 | 30 | PDU-02 | 15 | U3-7A-15 / 2P 30A | U3-7B-15 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 0.78998 | 1.08 | 1.87 | 71.1 | 96.5 | 0.252 | 167.6 |  |  | 0.22527 | 1.9747 | 적정함
B열 | C1001 | [37 empty] | 0 |  |  | 0 | 0 | 미사용 랙
| C1002 | B08 | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-35 | 7-1-B2-30-35 | 7-DaHall 1-PDU-01-30-35 | 7-DaHall 1-PDU-02-30-35 | 220 | 30 | PDU-01 | 35 | 220 | 30 | PDU-02 | 35 | U3-7A-35 / 2P 30A | U3-7B-35 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 6.7996 | 6.5469 | 13.3465 | 1091.2 | 1054.4 | 3.003 | 2145.6 | 세종 인터넷(클라우드이음) | 신규 구성중 | 2.8839 | -1.2839 | 사용초과 | Sejong Telecom Inc. | C1002
| C1003 | B07 | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-33 | 7-1-B2-30-33 | 7-DaHall 1-PDU-01-30-33 | 7-DaHall 1-PDU-02-30-33 | 220 | 30 | PDU-01 | 33 | 220 | 30 | PDU-02 | 33 | U3-7A-33 / 2P 30A | U3-7B-33 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 8.6702 | 8.3825 | 17.0527 | 1396.1 | 1354 | 3.809 | 2750.1 | 세종 인터넷(클라우드이음) | 신규 구성중 | 3.6964 | -2.0964 | 사용초과 | Sejong Telecom Inc. | C1003
| C1004 | B06 | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-31 | 7-1-B2-30-31 | 7-DaHall 1-PDU-01-30-31 | 7-DaHall 1-PDU-02-30-31 | 220 | 30 | PDU-01 | 31 | 220 | 30 | PDU-02 | 31 | U3-7A-31 / 2P 30A | U3-7B-31 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 4.519 | 3.712 | 8.231 | 687.6 | 527.2 | 1.671 | 1214.8 | 세종 인터넷(클라우드이음) | 신규 구성중 | 1.6328 | -0.032796 | 사용초과 | Sejong Telecom Inc. | C1004
| C1005 | B05 | Sejong Telecom Inc. | 2.2 | ○ |  | 7-1-A2-30-39 | 7-1-B2-30-39 | 7-DaHall 1-PDU-01-30-39 | 7-DaHall 1-PDU-02-30-39 | 220 | 30 | PDU-01 | 39 | 220 | 30 | PDU-02 | 39 | U3-7A-39 / 2P 30A | U3-7B-39 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.0399 | 1.8556 | 2.8954 | 139.9 | 262.4 | 0.568 | 402.3 | 세종 인터넷(클라우드이음) |  | 0.54073 | 1.6593 | 적정함
| C1006 | B04 | 7F-B04 랙 | [35 empty] | 0 | 미설치 (랙 없음) |  | 0 | 0 | 미사용 랙
| C1007 | B03 | 7F-B03 랙 | [35 empty] | 0 | 미설치 (랙 없음) |  | 0 | 0 | 미사용 랙
| C1008 | B02 | 7F-B02 랙 | [35 empty] | 0 | 미설치 (랙 없음) |  | 0 | 0 | 미사용 랙
| C1009 | B01 | 7F-B01 랙 | [35 empty] | 0 | 미설치 (랙 없음) |  | 0 | 0 | 미사용 랙
A열 | C1101 | [37 empty] | 0 |  |  | 0 | 0 | 미사용 랙
| C1102 | A08 | LG Hello Vision Co., Ltd. | 2.2 | ○ |  | 7-1-A3-50-8 | 7-1-B3-50-8 | 7-DaHall 1-RPP-03-50-8 | 7-DaHall 1-RPP-04-50-8 | 220 | 50 | RPP-03 | 8 | 220 | 50 | RPP-04 | 8 | UPS A2-08 / 2P 50A | UPS B2-08 / 2P 50A | UPS 출력분전반 A2 #08 | UPS 출력분전반 B2 #08 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.9716 | 1.9433 | 3.9148 | 303.2 | 296.7 | 0.87 | 599.9 | IDC 고객(LG HELLOVISION) |  | 0.80632 | 1.3937 | 적정함
| C1103 | A07 | LG Hello Vision Co., Ltd. | 2.2 | ○ |  | 7-1-A3-50-6 | 7-1-B3-50-6 | 7-DaHall 1-RPP-03-50-6 | 7-DaHall 1-RPP-04-50-6 | 220 | 50 | RPP-03 | 6 | 220 | 50 | RPP-04 | 6 | UPS A2-06 / 2P 50A | UPS B2-06 / 2P 50A | UPS 출력분전반 A2 #06 | UPS 출력분전반 B2 #06 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.584 | 1.2212 | 2.8052 | 242.5 | 179 | 0.633 | 421.5 | IDC 고객(LG HELLOVISION) |  | 0.56653 | 1.6335 | 적정함
| C1104 | A06 | LG Hello Vision Co., Ltd. | 2.2 | ○ |  | 7-1-A3-50-10 | 7-1-B3-50-10 | 7-DaHall 1-RPP-03-50-10 | 7-DaHall 1-RPP-04-50-10 | 220 | 50 | RPP-03 | 10 | 220 | 50 | RPP-04 | 10 | UPS A2-10 / 2P 50A | UPS B2-10 / 2P 50A | UPS 출력분전반 A2 #10 | UPS 출력분전반 B2 #10 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.6123 | 2.8519 | 5.4642 | 355 | 383.1 | 1.072 | 738.1 | IDC 고객(LG HELLOVISION) |  | 0.99207 | 1.2079 | 적정함
| C1105 | A05 | LG Hello Vision Co., Ltd. | 2.2 | ○ |  | 7-1-A3-50-9 | 7-1-B3-50-9 | 7-DaHall 1-RPP-03-50-9 | 7-DaHall 1-RPP-04-50-9 | 220 | 50 | RPP-03 | 9 | 220 | 50 | RPP-04 | 9 | UPS A2-09 / 2P 50A | UPS B2-09 / 2P 50A | UPS 출력분전반 A2 #09 | UPS 출력분전반 B2 #09 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.7464 | 1.6301 | 4.3765 | 407.2 | 243.8 | 0.943 | 651 | IDC 고객(LG HELLOVISION) |  | 0.875 | 1.325 | 적정함
| C1106 | A04 | LG Hello Vision Co., Ltd. |  |  | ○ | 7-1-B-5-35-42 | 7-1-A-5-35-42 | 7-DaHall 1-B-5-35-42 | 7-DaHall 1-A-5-35-42 | 48 | 35 | B-5 | 42 | 48 | 35 | A-5 | 42 | IPD B-5-F42(1) (구 IPD A) / 35A | IPD A-5-F42(1) (구 IPD B) / 35A | IPD B-5 (구 IPD A) | IPD A-5 (구 IPD B) | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | IDC 고객(LG HELLOVISION) | DC전원 장비직결 | 0 | 0 | 미사용 랙
[6 empty] | ○ | 7-1-B-5-35-43 | 7-1-A-5-35-43 | 7-DaHall 1-B-5-35-43 | 7-DaHall 1-A-5-35-43 | 48 | 35 | B-5 | 43 | 48 | 35 | A-5 | 43 | IPD B-5-F43(2) (구 IPD A) / 35A | IPD A-5-F43(2) (구 IPD B) / 35A | IPD B-5 (구 IPD A) | IPD A-5 (구 IPD B) | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | #N/A | 0 | IDC 고객(LG HELLOVISION) | DC전원 장비직결 | 0 | 0 | 미사용 랙
|  |  |  | 2.2 | ○ |  | 7-1-A3-50-7 | 7-1-B3-50-7 | 7-DaHall 1-RPP-03-50-7 | 7-DaHall 1-RPP-04-50-7 | 220 | 50 | RPP-03 | 7 | 220 | 50 | RPP-04 | 7 | UPS A2-07 / 2P 50A | UPS B2-07 / 2P 50A | UPS 출력분전반 A2 #07 | UPS 출력분전반 B2 #07 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.5091 | 4.1687 | 6.6778 | 398.7 | 635.8 | 1.447 | 1034.5 | IDC 고객(LG HELLOVISION) | DC전원 장비직결 | 1.3905 | 0.80954 | 적정함
| C1107 | A03 | LG Hello Vision Co., Ltd. | 2.2 | ○ |  | 7-1-A3-50-5 | 7-1-B3-50-5 | 7-DaHall 1-RPP-03-50-5 | 7-DaHall 1-RPP-04-50-5 | 220 | 50 | RPP-03 | 5 | 220 | 50 | RPP-04 | 5 | UPS A2-05 / 2P 50A | UPS B2-05 / 2P 50A | UPS 출력분전반 A2 #05 | UPS 출력분전반 B2 #05 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 3.4057 | 4.4897 | 7.8954 | 505.5 | 697.7 | 1.649 | 1203.2 | IDC 고객(LG HELLOVISION) |  | 1.6172 | 0.5828 | 적정함
| C1108 | A02 | LG Hello Vision Co., Ltd. | 2.2 | ○ |  | 7-1-A3-50-3 | 7-1-B3-50-3 | 7-DaHall 1-RPP-03-50-3 | 7-DaHall 1-RPP-04-50-3 | 220 | 50 | RPP-03 | 3 | 220 | 50 | RPP-04 | 3 | UPS A2-03 / 2P 50A | UPS B2-03 / 2P 50A | UPS 출력분전반 A2 #03 | UPS 출력분전반 B2 #03 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.7946 | 3.3461 | 6.1407 | 393.2 | 504.2 | 1.239 | 897.4 | IDC 고객(LG HELLOVISION) |  | 1.2062 | 0.99382 | 적정함
| C1109 | A01 | LG Hello Vision Co., Ltd. | 2.2 | ○ |  | 7-1-A3-50-1 | 7-1-B3-50-1 | 7-DaHall 1-RPP-03-50-1 | 7-DaHall 1-RPP-04-50-1 | 220 | 50 | RPP-03 | 1 | 220 | 50 | RPP-04 | 1 | UPS A2-01 / 2P 50A | UPS B2-01 / 2P 50A | UPS 출력분전반 A2 #01 | UPS 출력분전반 B2 #01 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.1335 | 1.0665 | 2.1999 | 157 | 138.4 | 1.346 | 295.4 | IDC 고객(LG HELLOVISION) |  | 0.39704 | 1.803 | 적정함
| C1210 |  | DEK, 층간 Patch Cabinet
| C1211 |  | DEK, 층간 Patch Cabinet
|  |  | 신규BMS(20F TPS실) Rack | 2.2 | ○ |  |  | 7-1-B2-30-49 |  | 7-DaHall 1-PDU-02-30-49 |  |  |  |  | 220 | 30 | PDU-02 | 49 | B: U3-7B-49 / 2P 30A; B: U3-7B(U7-6B) 4P 300A; B: LV-7B #06 / 3P 320A (U7-6B); B: TR-7B 1000kVA; B전원: 0.90141; 합계: 0.90141; B전원: 103.6 | 0.158 | 103.6 |  |  | 0.13925 | 2.0608 | 적정함
|  |  | 신규BMS(7F TPS실) Rack | 2.2 | ○ |  |  | 7-1-B2-30-51 |  | 7-DaHall 1-PDU-02-30-51 |  |  |  |  | 220 | 30 | PDU-02 | 51 | B: U3-7B-51 / 2P 30A; B: U3-7B(U7-6B) 4P 300A; B: LV-7B #06 / 3P 320A (U7-6B); B: TR-7B 1000kVA; B전원: 0.55004; 합계: 0.55004; B전원: 74 | 0.108 | 74 |  |  | 0.099462 | 2.1005 | 적정함
|  |  | 8층 Office 분전반(창고) |  |  |  | 7-1-A4-225-2 |  | 7-DaHall 1-PDU-03-225-2 |  | 220 | 225 | PDU-03 | 2 |  |  |  |  | A전원: 14.5183; 합계: 14.5183 | 3.02 | 0 |  |  | 0 | 0 | 미사용 랙
누락 회로 파악 불가 |  |  |  |  | ○ |  | 7-1-A1-20-1 |  | 7-DaHall 1-RPP-01-20-1 |  | 220 | 20 | RPP-01 | 1 |  |  |  |  | A: UPS A1-01 / 2P 20A; A: UPS 출력분전반 A1 #01; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 0 | 0 | 0 | W-DCS 8000 |  | 0 | 0 | 무부하 랙
[5 empty] | ○ |  | 7-1-A1-30-2 |  | 7-DaHall 1-RPP-01-30-2 |  | 220 | 30 | RPP-01 | 2 |  |  |  |  | A: UPS A1-02 / 2P 30A; A: UPS 출력분전반 A1 #02; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 0 | 0 | 0 | TO 8F 보안실 UPS항온항습기 모니터용PC |  | 0 | 0 | 무부하 랙
[5 empty] | ○ |  | 7-1-A1-20-3 |  | 7-DaHall 1-RPP-01-20-3 |  | 220 | 20 | RPP-01 | 3 |  |  |  |  | A: UPS A1-03 / 2P 20A; A: UPS 출력분전반 A1 #03; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 0 | 0 | 0 | ?? (전송) |  | 0 | 0 | 무부하 랙
[5 empty] | ○ |  | 7-1-A1-20-5 |  | 7-DaHall 1-RPP-01-20-5 |  | 220 | 20 | RPP-01 | 5 |  |  |  |  | A: UPS A1-05 / 2P 20A; A: UPS 출력분전반 A1 #05; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 0 | 0 | 0 | ?? (전송) |  | 0 | 0 | 무부하 랙
[5 empty] | ○ |  | 7-1-A1-20-9 |  | 7-DaHall 1-RPP-01-20-9 |  | 220 | 20 | RPP-01 | 9 |  |  |  |  | A: UPS A1-09 / 2P 20A; A: UPS 출력분전반 A1 #09; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 0 | 0 | 0 | IDC (Voice사업팀 MMS용-B) |  | 0 | 0 | 무부하 랙
[5 empty] | ○ |  | 7-1-A1-20-13 |  | 7-DaHall 1-RPP-01-20-13 |  | 220 | 20 | RPP-01 | 13 |  |  |  |  | A: UPS A1-13 / 2P 20A; A: UPS 출력분전반 A1 #13; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 0 | 0 | 0 | ONS1064 SERVER |  | 0 | 0 | 무부하 랙
[5 empty] | ○ |  | 7-1-A1-20-15 |  | 7-DaHall 1-RPP-01-20-15 |  | 220 | 20 | RPP-01 | 15 |  |  |  |  | A: UPS A1-15 / 2P 20A; A: UPS 출력분전반 A1 #15; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 0 | 0 | 0 | NTT 하-1 |  | 0 | 0 | 무부하 랙
[5 empty] | ○ |  | 7-1-A1-20-17 |  | 7-DaHall 1-RPP-01-20-17 |  | 220 | 20 | RPP-01 | 17 |  |  |  |  | A: UPS A1-17 / 2P 20A; A: UPS 출력분전반 A1 #17; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 0 | 0 | 0 | 8층 보안실 CCTV 모니터 |  | 0 | 0 | 무부하 랙
[5 empty] | ○ |  | 7-1-A1-20-27 |  | 7-DaHall 1-RPP-01-20-27 |  | 220 | 20 | RPP-01 | 27 |  |  |  |  | A: UPS A1-27 / 2P 20A; A: UPS 출력분전반 A1 #27; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 3.1544; 합계: 3.1544; A전원: 410.6 | 0.619 | 410.6 | 전송 (NMS B-15) |  | 0.55188 | -0.55188 | 사용초과 | 0 | 0
[5 empty] | ○ |  | 7-1-A1-30-28 |  | 7-DaHall 1-RPP-01-30-28 |  | 220 | 30 | RPP-01 | 28 |  |  |  |  | A: UPS A1-28 / 2P 30A; A: UPS 출력분전반 A1 #28; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 1.6154; 합계: 1.6154; A전원: 131.9 | 0.554 | 131.9 | 운용실콘센트 |  | 0.17728 | -0.17728 | 사용초과 | 0 | 0
[5 empty] | ○ |  | 7-1-A1-20-29 |  | 7-DaHall 1-RPP-01-20-29 |  | 220 | 20 | RPP-01 | 29 |  |  |  |  | A: UPS A1-29 / 2P 20A; A: UPS 출력분전반 A1 #29; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 4.1315; 합계: 4.1315; A전원: 131.9 | 0.713 | 131.9 | 전송 (NMS B-16) |  | 0.17728 | -0.17728 | 사용초과 | 0 | 0
[5 empty] | ○ |  | 7-1-A1-30-30 |  | 7-DaHall 1-RPP-01-30-30 |  | 220 | 30 | RPP-01 | 30 |  |  |  |  | A: UPS A1-30 / 2P 30A; A: UPS 출력분전반 A1 #30; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 4.2718; 합계: 4.2718; A전원: 504.8 | 0.972 | 504.8 | 운용실콘센트 창가1열 |  | 0.67849 | -0.67849 | 사용초과 | 0 | 0
[5 empty] | ○ |  | 7-1-A1-20-31 |  | 7-DaHall 1-RPP-01-20-31 |  | 220 | 20 | RPP-01 | 31 |  |  |  |  | A: UPS A1-31 / 2P 20A; A: UPS 출력분전반 A1 #31; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 5.7882; 합계: 5.7882; A전원: 589.4 | 0.929 | 589.4 | 전송 (??) |  | 0.7922 | -0.7922 | 사용초과 | 0 | 0
[5 empty] | ○ |  |  | 7-1-B2-30-50 |  | 7-DaHall 1-PDU-02-30-50 |  |  |  |  | 220 | 30 | PDU-02 | 50 | B: U3-7B-50 / 2P 30A; B: U3-7B(U7-6B) 4P 300A; B: LV-7B #06 / 3P 320A (U7-6B); B: TR-7B 1000kVA; B전원: 3.5322; 합계: 3.5322; B전원: 344.4 | 0.532 | 344.4 | 7층 출입카드(전층 출입통제) |  | 0.4629 | -0.4629 | 사용초과 | 0 | 0
[5 empty] | ○ |  |  | 7-1-B2-30-52 |  | 7-DaHall 1-PDU-02-30-52 |  |  |  |  | 220 | 30 | PDU-02 | 52 | B: U3-7B-52 / 2P 30A; B: U3-7B(U7-6B) 4P 300A; B: LV-7B #06 / 3P 320A (U7-6B); B: TR-7B 1000kVA; B전원: 0; 합계: 0; B전원: 0 | 0 | 0 | 20F MAIN (FMS) |  | 0 | 0 | 무부하 랙
[5 empty] | ○ |  |  | 7-1-B2-30-54 |  | 7-DaHall 1-PDU-02-30-54 |  |  |  |  | 220 | 30 | PDU-02 | 54 | B: U3-7B-54 / 2P 30A; B: U3-7B(U7-6B) 4P 300A; B: LV-7B #06 / 3P 320A (U7-6B); B: TR-7B 1000kVA; B전원: 0; 합계: 0; B전원: 0 | 0 | 0 | 7F MAIN (FMS) |  | 0 | 0 | 무부하 랙
[5 empty] | ○ |  | 7-1-A2-30-52 |  | 7-DaHall 1-PDU-01-30-52 |  | 220 | 30 | PDU-01 | 52 |  |  |  |  | A: U3-7A-52 / 2P 30A; A: U3-7A(U7-5A) 4P 300A; A: LV-7A #05 / 3P 320A (U7-5A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 0 | 0 | 0 | 7F NTT CCTV 전원 |  | 0 | 0 | 무부하 랙
[5 empty] | ○ |  |  | 7-1-B1-20-1 |  | 7-DaHall 1-RPP-02-20-1 |  |  |  |  | 220 | 20 | RPP-02 | 1 | B: UPS B1-01 / 2P 20A; B: UPS 출력분전반 B1 #01; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 0.9106; 합계: 0.9106; B전원: 129.4 | 0.216 | 129.4 | 강남방향 창가열 콘센트 |  | 0.17392 | -0.17392 | 사용초과 | 0 | 0
[5 empty] | ○ |  |  | 7-1-B1-30-2 |  | 7-DaHall 1-RPP-02-30-2 |  |  |  |  | 220 | 30 | RPP-02 | 2 | B: UPS B1-02 / 2P 30A; B: UPS 출력분전반 B1 #02; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 0.28097; 합계: 0.28097; B전원: 34.1 | 3.573 | 34.1 | 정면창가 콘센트 |  | 0.045833 | -0.045833 | 사용초과 | 0 | 0
[5 empty] | ○ |  |  | 7-1-B1-20-3 |  | 7-DaHall 1-RPP-02-20-3 |  |  |  |  | 220 | 20 | RPP-02 | 3 | B: UPS B1-03 / 2P 20A; B: UPS 출력분전반 B1 #03; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 0.55027; 합계: 0.55027; B전원: 70.9 | 0.129 | 70.9 | ?? |  | 0.095296 | -0.095296 | 사용초과 | 0 | 0
[5 empty] | ○ |  |  | 7-1-B1-30-6 |  | 7-DaHall 1-RPP-02-30-6 |  |  |  |  | 220 | 30 | RPP-02 | 6 | B: UPS B1-06 / 2P 30A; B: UPS 출력분전반 B1 #08; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 0; 합계: 0; B전원: 0 | 0 | 0 | 전송 (GAINS) |  | 0 | 0 | 무부하 랙
[5 empty] | ○ |  |  | 7-1-B1-20-7 |  | 7-DaHall 1-RPP-02-20-7 |  |  |  |  | 220 | 20 | RPP-02 | 7 | B: UPS B1-07 / 2P 20A; B: UPS 출력분전반 B1 #07; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 1.1224; 합계: 1.1224; B전원: 153.7 | 0.223 | 153.7 | C2C DWDM EMS RACK |  | 0.20659 | -0.20659 | 사용초과 | 0 | 0
[5 empty] | ○ |  |  | 7-1-B1-20-11 |  | 7-DaHall 1-RPP-02-20-11 |  |  |  |  | 220 | 20 | RPP-02 | 11 | B: UPS B1-11 / 2P 20A; B: UPS 출력분전반 B1 #11; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 0; 합계: 0; B전원: 0 | 0 | 0 | 전송 (ONS1064 SERVER) |  | 0 | 0 | 무부하 랙
[5 empty] | ○ |  |  | 7-1-B1-30-22 |  | 7-DaHall 1-RPP-02-30-22 |  |  |  |  | 220 | 30 | RPP-02 | 22 | B: UPS B1-22 / 2P 30A; B: UPS 출력분전반 B1 #22; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 0; 합계: 0; B전원: 0 | 0 | 0 | 운용실 바닥콘센트 |  | 0 | 0 | 무부하 랙
[5 empty] | ○ |  |  | 7-1-B1-30-24 |  | 7-DaHall 1-RPP-02-30-24 |  |  |  |  | 220 | 30 | RPP-02 | 24 | B: UPS B1-24 / 2P 30A; B: UPS 출력분전반 B1 #24; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 2.2591; 합계: 2.2591; B전원: 217.9 | 0.626 | 217.9 | 운용실 콘센트 창가1열 |  | 0.29288 | -0.29288 | 사용초과 | 0 | 0
[5 empty] | ○ |  |  | 7-1-B1-20-35 |  | 7-DaHall 1-RPP-02-20-35 |  |  |  |  | 220 | 20 | RPP-02 | 35 | B: UPS B1-35 / 2P 20A; B: UPS 출력분전반 B1 #35; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 2.539; 합계: 2.539; B전원: 298.3 | 0.468 | 298.3 | 7F NMS A-18 |  | 0.40094 | -0.40094 | 사용초과 | 0 | 0
[5 empty] | ○ |  |  | 7-1-B1-20-37 |  | 7-DaHall 1-RPP-02-20-37 |  |  |  |  | 220 | 20 | RPP-02 | 37 | B: UPS B1-37 / 2P 20A; B: UPS 출력분전반 B1 #37; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 5.8492; 합계: 5.8492; B전원: 670.1 | 1.015 | 670.1 | 7F NMS A-19 |  | 0.90067 | -0.90067 | 사용초과 | 0 | 0
[5 empty] | ○ |  |  | 7-1-B1-20-38 |  | 7-DaHall 1-RPP-02-20-38 |  |  |  |  | 220 | 20 | RPP-02 | 38 | B: UPS B1-38 / 2P 30A; B: UPS 출력분전반 B1 #38; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; 합계: 0; B전원: 772.1 | 1.087 | 772.1 | IDC MAN POP |  | 1.0378 | -1.0378 | 사용초과 | 0 | 0
[5 empty] | ○ |  |  | 7-1-B1-20-39 |  | 7-DaHall 1-RPP-02-20-39 |  |  |  |  | 220 | 20 | RPP-02 | 39 | B: UPS B1-39 / 2P 20A; B: UPS 출력분전반 B1 #39; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 3.1025; 합계: 3.1025; B전원: 291.6 | 3.033 | 291.6 | 7F NMS A-20 |  | 0.39194 | -0.39194 | 사용초과 | 0 | 0
[35 empty] | 742.2418 | 20.7896
Note on L38: A-4-27 OSN550 A-4-33 코위버CWDM
Note on M38: A-4-27 OSN550 A-4-33 코위버CWDM
Note on N38: A-4-27 OSN550 A-4-33 코위버CWDM
Note on O38: A-4-27 OSN550 A-4-33 코위버CWDM
Note on P38: B-4-33 코위버CWDM B-4-57 OSN550
Note on Q38: B-4-33 코위버CWDM B-4-57 OSN550
Note on R38: B-4-33 코위버CWDM B-4-57 OSN550
Note on S38: B-4-33 코위버CWDM B-4-57 OSN550
Note on T38: A-4-27 OSN550 A-4-33 코위버CWDM
Note on U38: B-4-33 코위버CWDM B-4-57 OSN550
Note on L39: A-4-27 OSN550 A-4-33 코위버CWDM
Note on M39: A-4-27 OSN550 A-4-33 코위버CWDM
Note on N39: A-4-27 OSN550 A-4-33 코위버CWDM
Note on O39: A-4-27 OSN550 A-4-33 코위버CWDM
Note on P39: B-4-33 코위버CWDM B-4-57 OSN550
Note on Q39: B-4-33 코위버CWDM B-4-57 OSN550
Note on R39: B-4-33 코위버CWDM B-4-57 OSN550
Note on S39: B-4-33 코위버CWDM B-4-57 OSN550
Note on T39: A-4-27 OSN550 A-4-33 코위버CWDM
Note on U39: B-4-33 코위버CWDM B-4-57 OSN550
Note on R68: B-2-62 PDP B-2-63 장비직결
Note on S68: B-2-62 PDP B-2-63 장비직결
Note on T68: A-2-62 PDP A-2-63 장비직결
Note on U68: B-2-62 PDP B-2-63 장비직결
Note on R69: B-2-62 PDP B-2-63 장비직결
Note on S69: B-2-62 PDP B-2-63 장비직결
Note on T69: A-2-62 PDP A-2-63 장비직결
Note on U69: B-2-62 PDP B-2-63 장비직결
Note on C164: 이현상: 인터넷에서 어마무시하게 전기 실사용 중이라함 확인 필요(21.05.27)
Note on T227: 이현상: IPD / B-5_P48 C-1 랙 장비__A 인가? 정원용M 확인 필요...
Note on U227: 이현상: 이거 랙 번호가 정확한건가? 변익준M에 확인 필요..
Note on T243: 이현상: IPD / B-5_P42 A-5 랙 장비_A(1) 인가? 정원용M 확인 필요..
Note on U243: 이현상: IPD / B-5_P42 A-5 랙 장비_B(1) 인가?
Note on T244: 이현상: IPD / B-5_P43 A-5 랙 장비_A(2) 인가? 정원용M 확인 필요..
Note on U244: 이현상: IPD / B-5_P43 A-5 랙 장비_B(2) 인가?

## 6층_랙별_계통 및_부하량
6층 랙별 전기공급계통 | [47 empty] | 미디어꾼 | 계약용량 | 시간당 전력량 | 남은 전력량 | 전력초과여부 | 피크값 | 평균값 | 0
[8 empty] | 층/분전반명/차단기용량/차단기번호 | [40 empty] | 0 | 0 | 0 | 미사용 랙 | 0 | #DIV/0!
DEKR No. | 랙 No. | 고객명 | 계약용량 | 리셉터클 Name |  | 차단기 정보 |  | DEK Naming Convention 적용 명칭(NEW) |  | 차단기 정보(수정) | [7 empty] | 분전반 정보 |  | 배전반 정보 |  | TR 정보 |  | 월 평균 전류 |  |  | 월 유효전력량 |  | kW(전월최대유효전력) | 월간 사용전력량[kWh] | 비 고 |  | 시간당 전력량 | 남은 전력량 | 전력초과여부 | 사용초과 고객 수 |  | 적정함 | 무부하 랙 | 열 구분 (부스바명) | DEKR No. | 고객명 | 계약용량 | DEK Naming Convention 적용 명칭(NEW) |  | 월 평균 전류 |  |  | 월 유효전력량 |  | kW(전월최대유효전력) | 월간 사용전력량[kWh] | 비 고
|  |  | kW | A | B | A | B | A | B | A |  |  |  | B |  |  |  | A | B | A | B | A | B | A | B | 합계 | A | B | [7 empty] | 21 |  | 31 | 194 |  |  |  | kW | 상 | 하 | 상 | 하 | 합계 | 상 | 하
A101 | [29 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙 |  |  |  |  | 찾을 수 없음 |  |  |  | 찾을 수 없음 |  | 찾을 수 없음
A102 | 6F-AE19 | [24 empty] | 0 |  |  |  | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A103 | 6F-AE18 | [24 empty] | 0 |  |  |  | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A104 | 6F-AE17 | [24 empty] | 0 |  |  |  | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A105 | 6F-AE16 |  |  | A6-2-4 | B6-2-4 | U6-A6-36 / 2P 30A | U6-B6-36 / 2P 30A | 6-DaHall 1-PDU-07-30-36 | 6-DaHall 1-PDU-08-30-36 | 220 | 30 | 07 | 36 | 220 | 30 | 08 | 36 | U6-A6 4P 300A | U6-B6 4P 300A | LV-6A #06, 3P 320A | LV-6B #02, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A106 | 6F-AE15 |  |  | A6-2-5 | B6-2-5 | U6-A6-38 / 2P 30A | U6-B6-38 / 2P 30A | 6-DaHall 1-PDU-07-30-38 | 6-DaHall 1-PDU-08-30-38 | 220 | 30 | 07 | 38 | 220 | 30 | 08 | 38 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A107 | 6F-AE14 |  |  | A6-2-6 | B6-2-6 | U6-A6-40 / 2P 30A | U6-B6-40 / 2P 30A | 6-DaHall 1-PDU-07-30-40 | 6-DaHall 1-PDU-08-30-40 | 220 | 30 | 07 | 40 | 220 | 30 | 08 | 40 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A108 | 6F-AE13 |  |  | A6-2-7 | B6-2-7 | U6-A6-42 / 2P 30A | U6-B6-42 / 2P 30A | 6-DaHall 1-PDU-07-30-42 | 6-DaHall 1-PDU-08-30-42 | 220 | 30 | 07 | 42 | 220 | 30 | 08 | 42 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A109 | 6F-AE12 |  |  | A6-2-8 | B6-2-8 | U6-A6-44 / 2P 30A | U6-B6-44 / 2P 30A | 6-DaHall 1-PDU-07-30-44 | 6-DaHall 1-PDU-08-30-44 | 220 | 30 | 07 | 44 | 220 | 30 | 08 | 44 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A110 | 6F-AE11 |  |  | A6-2-9 | B6-2-9 | U6-A6-46 / 2P 30A | U6-B6-46 / 2P 30A | 6-DaHall 1-PDU-07-30-46 | 6-DaHall 1-PDU-08-30-46 | 220 | 30 | 07 | 46 | 220 | 30 | 08 | 46 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A201 | [29 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A202 | 6F-AD19 | [28 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A203 | 6F-AD18 | [28 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A204 | 6F-AD17 | [28 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A205 | 6F-AD16 |  |  | A6-3-4 | B6-3-4 | U6-A6-54 / 2P 30A | U6-B6-54 / 2P 30A | 6-DaHall 1-PDU-07-30-54 | 6-DaHall 1-PDU-08-30-54 | 220 | 30 | 07 | 54 | 220 | 30 | 08 | 54 | U6-A6 4P 300A | U6-B6 4P 300A | LV-6A #06, 3P 320A | LV-6B #02, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A206 | 6F-AD15 |  |  | A6-3-5 | B6-3-5 | U6-A6-53 / 2P 30A | U6-B6-53 / 2P 30A | 6-DaHall 1-PDU-07-30-53 | 6-DaHall 1-PDU-08-30-53 | 220 | 30 | 07 | 53 | 220 | 30 | 08 | 53 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A207 | 6F-AD14 |  |  | A6-3-6 | B6-3-6 | U6-A6-51 / 2P 30A | U6-B6-51 / 2P 30A | 6-DaHall 1-PDU-07-30-51 | 6-DaHall 1-PDU-08-30-51 | 220 | 30 | 07 | 51 | 220 | 30 | 08 | 51 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A208 | 6F-AD13 |  |  | A6-3-7 | B6-3-7 | U6-A6-49 / 2P 30A | U6-B6-49 / 2P 30A | 6-DaHall 1-PDU-07-30-49 | 6-DaHall 1-PDU-08-30-49 | 220 | 30 | 07 | 49 | 220 | 30 | 08 | 49 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A209 | 6F-AD12 |  |  | A2-3-8 | B2-3-8 | U6-A2-16 / 2P 30A | U6-B2-16 / 2P 30A | 6-DaHall 1-PDU-03-30-16 | 6-DaHall 1-PDU-04-30-16 | 220 | 30 | 03 | 16 | 220 | 30 | 04 | 16 | U-A2 4P 200A | U-B2 4P 200A | UPS 출력배전반(A) #02, 4P 200A | UPS 출력배전반(B) #04, 4P 200A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A210 | 6F-AD11 |  |  | A2-3-9 | B2-3-9 | U6-A2-18 / 2P 30A | U6-B2-18 / 2P 30A | 6-DaHall 1-PDU-03-30-18 | 6-DaHall 1-PDU-04-30-18 | 220 | 30 | 03 | 18 | 220 | 30 | 04 | 18 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A303 | 6F-AC18 | [28 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A304 | 6F-AC17 | [28 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A305 | 6F-AC16 |  |  | A6-4-4 | B6-4-4 | U6-A6-08 / 2P 30A | U6-B6-08 / 2P 30A | 6-DaHall 1-PDU-07-30-8 | 6-DaHall 1-PDU-08-30-8 | 220 | 30 | 07 | 8 | 220 | 30 | 08 | 8 | U6-A6 4P 300A | U6-B6 4P 300A | LV-6A #06, 3P 320A | LV-6B #02, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A306 | 6F-AC15 |  |  | A6-4-5 | B6-4-5 | U6-A6-10 / 2P 30A | U6-B6-10 / 2P 30A | 6-DaHall 1-PDU-07-30-10 | 6-DaHall 1-PDU-08-30-10 | 220 | 30 | 07 | 10 | 220 | 30 | 08 | 10 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A307 | 6F-AC14 |  |  | A6-4-6 | B6-4-6 | U6-A6-12 / 2P 30A | U6-B6-12 / 2P 30A | 6-DaHall 1-PDU-07-30-12 | 6-DaHall 1-PDU-08-30-12 | 220 | 30 | 07 | 12 | 220 | 30 | 08 | 12 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A308 | 6F-AC13 |  |  | A6-4-7 | B6-4-7 | U6-A6-14 / 2P 30A | U6-B6-14 / 2P 30A | 6-DaHall 1-PDU-07-30-14 | 6-DaHall 1-PDU-08-30-14 | 220 | 30 | 07 | 14 | 220 | 30 | 08 | 14 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A309 | 6F-AC12 |  |  | A1-4-8 | B1-4-8 | U-A1-48 / 2P 30A | U-B1-48 / 2P 30A | 6-DaHall 1-PDU-01-30-48 | 6-DaHall 1-PDU-02-30-48 | 220 | 30 | 01 | 48 | 220 | 30 | 02 | 48 | U-A1 4P 200A | U-B1 4P 200A | UPS 출력배전반(A) #04, 4P 200A | UPS 출력배전반(B) #02, 4P 200A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A310 | 6F-AC11 |  |  | A5-4-9 | B5-4-9 | U6-A5-50 / 2P 30A | U6-B5-50 / 2P 30A | 6-DaHall 1-PDU-05-30-50 | 6-DaHall 1-PDU-06-30-50 | 220 | 30 | 05 | 50 | 220 | 30 | 06 | 50 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A403 | 6F-AB18 | [28 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A404 | 6F-AB17 | [28 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A405 | 6F-AB16 |  |  | A6-5-4 | B6-5-4 | U6-A6-22 / 2P 30A | U6-B6-22 / 2P 30A | 6-DaHall 1-PDU-07-30-22 | 6-DaHall 1-PDU-08-30-22 | 220 | 30 | 07 | 22 | 220 | 30 | 08 | 22 | U6-A6 4P 300A | U6-B6 4P 300A | LV-6A #06, 3P 320A | LV-6B #02, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A406 | 6F-AB15 |  |  | A6-5-5 | B6-5-5 | U6-A6-24 / 2P 30A | U6-B6-24 / 2P 30A | 6-DaHall 1-PDU-07-30-24 | 6-DaHall 1-PDU-08-30-24 | 220 | 30 | 07 | 24 | 220 | 30 | 08 | 24 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A407 | 6F-AB14 |  |  | A6-5-6 | B6-5-6 | U6-A6-26 / 2P 30A | U6-B6-26 / 2P 30A | 6-DaHall 1-PDU-07-30-26 | 6-DaHall 1-PDU-08-30-26 | 220 | 30 | 07 | 26 | 220 | 30 | 08 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A408 | 6F-AB13 |  |  | A6-5-7 | B6-5-7 | U6-A6-28 / 2P 30A | U6-B6-28 / 2P 30A | 6-DaHall 1-PDU-07-30-28 | 6-DaHall 1-PDU-08-30-28 | 220 | 30 | 07 | 28 | 220 | 30 | 08 | 28 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A409 | 6F-AB12 |  |  | A2-5-8 | B2-5-8 | U-A2-33 / 2P 30A | U-B2-33 / 2P 30A | 6-DaHall 1-PDU-03-30-33 | 6-DaHall 1-PDU-04-30-33 | 220 | 30 | 03 | 33 | 220 | 30 | 04 | 33 | U-A2 4P 200A | U-B2 4P 200A | UPS 출력배전반(A) #02, 4P 200A | UPS 출력배전반(B) #04, 4P 200A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A410 | 6F-AB11 |  |  | A2-5-9 | B2-5-9 | U-A2-35 / 2P 30A | U-B2-35 / 2P 30A | 6-DaHall 1-PDU-03-30-35 | 6-DaHall 1-PDU-04-30-35 | 220 | 30 | 03 | 35 | 220 | 30 | 04 | 35 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A503 | 6F-V18 | [24 empty] | 0 |  |  |  | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A504 | 6F-V17 |  |  | A2-7-2 | B2-7-2 | U-A2-24 / 2P 30A | U-B2-24 / 2P 30A | 6-DaHall 1-PDU-03-30-24 | 6-DaHall 1-PDU-04-30-24 | 220 | 30 | 03 | 24 | 220 | 30 | 04 | 24 | U-A2 4P 200A | U-B2 4P 200A | UPS 출력배전반(A) #02, 4P 200A | UPS 출력배전반(B) #04, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
|  |  |  | A2-7-1 | B2-7-1 | U-A2-22 / 2P 30A | U-B2-22 / 2P 30A | 6-DaHall 1-PDU-03-30-22 | 6-DaHall 1-PDU-04-30-22 | 220 | 30 | 03 | 22 | 220 | 30 | 04 | 22 | [6 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A505 | 6F-V16 |  |  | A2-7-3 | B2-7-3 | U-A2-26 / 2P 30A | U-B2-26 / 2P 30A | 6-DaHall 1-PDU-03-30-26 | 6-DaHall 1-PDU-04-30-26 | 220 | 30 | 03 | 26 | 220 | 30 | 04 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
|  |  |  | A2-8-1 | B2-8-1 | U-A2-38 / 2P 30A | U-B2-38 / 2P 30A | 6-DaHall 1-PDU-03-30-38 | 6-DaHall 1-PDU-04-30-38 | 220 | 30 | 03 | 38 | 220 | 30 | 04 | 38 | [6 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A506 | 6F-V15 |  |  | A2-7-4 | B2-7-4 | U-A2-28 / 2P 30A | U-B2-28 / 2P 30A | 6-DaHall 1-PDU-03-30-28 | 6-DaHall 1-PDU-04-30-28 | 220 | 30 | 03 | 28 | 220 | 30 | 04 | 28 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A507 | 6F-V14 |  |  | A2-7-5 | B2-7-5 | U-A2-30 / 2P 30A | U-B2-30 / 2P 30A | 6-DaHall 1-PDU-03-30-30 | 6-DaHall 1-PDU-04-30-30 | 220 | 30 | 03 | 30 | 220 | 30 | 04 | 30 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A508 | 6F-V13 |  |  | A2-7-6 | B2-7-6 | U-A2-32 / 2P 30A | U-B2-32 / 2P 30A | 6-DaHall 1-PDU-03-30-32 | 6-DaHall 1-PDU-04-30-32 | 220 | 30 | 03 | 32 | 220 | 30 | 04 | 32 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A509 | 6F-V12 |  |  | A2-7-7 | B2-7-7 | U-A2-34 / 2P 30A | U-B2-34 / 2P 30A | 6-DaHall 1-PDU-03-30-34 | 6-DaHall 1-PDU-04-30-34 | 220 | 30 | 03 | 34 | 220 | 30 | 04 | 34 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A510 | 6F-V11 |  |  | A2-7-8 | B2-7-8 | U-A2-36 / 2P 30A | U-B2-36 / 2P 30A | 6-DaHall 1-PDU-03-30-36 | 6-DaHall 1-PDU-04-30-36 | 220 | 30 | 03 | 36 | 220 | 30 | 04 | 36 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 6F-W19 | [24 empty] | 0 |  |  |  | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A603 | 6F-W18 | [24 empty] | 0 |  |  |  | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A604 | 6F-W17 |  |  | A2-8-2 | B2-8-2 | U-A2-40 / 2P 30A | U-B2-40 / 2P 30A | 6-DaHall 1-PDU-03-30-40 | 6-DaHall 1-PDU-04-30-40 | 220 | 30 | 03 | 40 | 220 | 30 | 04 | 40 | U-A2 4P 200A | U-B2 4P 200A | UPS 출력배전반(A) #02, 4P 200A | UPS 출력배전반(B) #04, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A605 | 6F-W16 |  |  | A2-8-3 | B2-8-3 | U-A2-42 / 2P 30A | U-B2-42 / 2P 30A | 6-DaHall 1-PDU-03-30-42 | 6-DaHall 1-PDU-04-30-42 | 220 | 30 | 03 | 42 | 220 | 30 | 04 | 42 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A606 | 6F-W15 |  |  | A2-8-4 | B2-8-4 | U-A2-44 / 2P 30A | U-B2-44 / 2P 30A | 6-DaHall 1-PDU-03-30-44 | 6-DaHall 1-PDU-04-30-44 | 220 | 30 | 03 | 44 | 220 | 30 | 04 | 44 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A607 | 6F-W14 |  |  | A2-8-5 | B2-8-5 | U-A2-46 / 2P 30A | U-B2-46 / 2P 30A | 6-DaHall 1-PDU-03-30-46 | 6-DaHall 1-PDU-04-30-46 | 220 | 30 | 03 | 46 | 220 | 30 | 04 | 46 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A608 | 6F-W13 |  |  | A2-8-6 | B2-8-6 | U-A2-48 / 2P 30A | U-B2-48 / 2P 30A | 6-DaHall 1-PDU-03-30-48 | 6-DaHall 1-PDU-04-30-48 | 220 | 30 | 03 | 48 | 220 | 30 | 04 | 48 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
|  |  |  | A6-8-6(1) | B6-8-6(1) | U6-A6-45 / 2P 30A | U6-B6-47 / 2P 30A | 6-DaHall 1-PDU-07-30-45 | 6-DaHall 1-PDU-08-30-47 | 220 | 30 | 07 | 45 | 220 | 30 | 08 | 47 | U6-A6 4P 300A | U6-B6 4P 300A | LV-6A #06, 3P 320A | LV-6B #02, 3P 320A |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A609 | 6F-W12 |  |  | A5-8-7 | B5-8-7 | U6-A5-01 / 2P 30A | U6-B5-01 / 2P 30A | 6-DaHall 1-PDU-05-30-1 | 6-DaHall 1-PDU-06-30-1 | 220 | 30 | 05 | 1 | 220 | 30 | 06 | 1 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
|  |  |  | A6-8-7(1) | B6-8-7(1) | U6-A6-43 / 2P 30A | U6-B6-45 / 2P 30A | 6-DaHall 1-PDU-07-30-43 | 6-DaHall 1-PDU-08-30-45 | 220 | 30 | 07 | 43 | 220 | 30 | 08 | 45 | U6-A6 4P 300A | U6-B6 4P 300A | LV-6A #06, 3P 320A | LV-6B #02, 3P 320A |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A610 | 6F-W11 |  |  | A5-8-8 | B5-8-8 | U6-A5-03 / 2P 30A | U6-B5-03 / 2P 30A | 6-DaHall 1-PDU-05-30-3 | 6-DaHall 1-PDU-06-30-3 | 220 | 30 | 05 | 3 | 220 | 30 | 06 | 3 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
|  |  |  | A6-8-8(1) | B6-8-8(1) | U6-A6-41 / 2P 30A | U6-B6-43 / 2P 30A | 6-DaHall 1-PDU-07-30-41 | 6-DaHall 1-PDU-08-30-43 | 220 | 30 | 07 | 41 | 220 | 30 | 08 | 43 | U6-A6 4P 300A | U6-B6 4P 300A | LV-6A #06, 3P 320A | LV-6B #02, 3P 320A |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 6F-X19 | [24 empty] | 0 |  |  |  | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
| 6F-X18 | [24 empty] | 0 |  |  |  | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
| 6F-X17 |  |  | A5-9-2 | B5-9-2 | U6-A5-07 / 2P 30A | U6-B5-07 / 2P 30A | 6-DaHall 1-PDU-05-30-7 | 6-DaHall 1-PDU-06-30-7 | 220 | 30 | 05 | 7 | 220 | 30 | 06 | 7 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
| 6F-X16 |  |  | A5-9-3 | B5-9-3 | U6-A5-09 / 2P 30A | U6-B5-09 / 2P 30A | 6-DaHall 1-PDU-05-30-9 | 6-DaHall 1-PDU-06-30-9 | 220 | 30 | 05 | 9 | 220 | 30 | 06 | 9 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A706 | 6F-X15 | 주식회사 씨엘엠앤에스 | 1.1 | A5-9-4 | B5-9-4 | U6-A5-11 / 2P 30A | U6-B5-11 / 2P 30A | 6-DaHall 1-PDU-05-30-11 | 6-DaHall 1-PDU-06-30-11 | 220 | 30 | 05 | 11 | 220 | 30 | 06 | 11 | [6 empty] | 1.81 | 1.9057 | 3.7157 | 176.8 | 194.8 | 0.669 | 371.6 |  |  | 0.49946 | 0.60054 | 적정함
A707 | 6F-X14 | 주식회사 씨엘엠앤에스 | 2.2 | A5-9-5 | B5-9-5 | U6-A5-13 / 2P 30A | U6-B5-13 / 2P 30A | 6-DaHall 1-PDU-05-30-13 | 6-DaHall 1-PDU-06-30-13 | 220 | 30 | 05 | 13 | 220 | 30 | 06 | 13 | [6 empty] | 2.0275 | 3.5289 | 5.5563 | 215.8 | 438.7 | 0.979 | 654.5 |  |  | 0.8797 | 1.3203 | 적정함
A708 | 6F-X13 | 주식회사 씨엘엠앤에스 | 2.2 | A5-9-6 | B5-9-6 | U6-A5-15 / 2P 30A | U6-B5-15 / 2P 30A | 6-DaHall 1-PDU-05-30-15 | 6-DaHall 1-PDU-06-30-15 | 220 | 30 | 05 | 15 | 220 | 30 | 06 | 15 | [6 empty] | 3.7039 | 3.177 | 6.8809 | 503.2 | 446.9 | 1.382 | 950.1 |  |  | 1.277 | 0.92298 | 적정함
A709 | 6F-X12 | 주식회사 씨엘엠앤에스 | 1.1 | A5-9-7 | B5-9-7 | U6-A5-17 / 2P 30A | U6-B5-17 / 2P 30A | 6-DaHall 1-PDU-05-30-17 | 6-DaHall 1-PDU-06-30-17 | 220 | 30 | 05 | 17 | 220 | 30 | 06 | 17 | [6 empty] | 0.95682 | 0.91132 | 1.8681 | 127.6 | 121 | 0.402 | 248.6 |  |  | 0.33414 | 0.76586 | 적정함
A710 |  | DEK, 층간 Patch Cabinet |  | A5-9-8 | B5-9-8 | U6-A5-19 / 2P 30A | U6-B5-19 / 2P 30A | 6-DaHall 1-PDU-05-30-19 | 6-DaHall 1-PDU-06-30-19 | 220 | 30 | 05 | 19 | 220 | 30 | 06 | 19 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 6F-Y19 | [24 empty] | 0 |  |  |  | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
| 6F-Y18 | [24 empty] | 0 |  |  |  | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
| 6F-Y17 |  |  | A5-10-2 | B5-10-2 | U6-A5-23 / 2P 30A | U6-B5-23 / 2P 30A | [10 empty] | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA |  |  | 0 |  |  |  | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A806 | 6F-Y16 | Pyler | 12 | A5-10-3 | B5-10-3 | U6-A5-25 / 2P 30A | U6-B5-25 / 2P 30A | 6-DaHall 1-PDU-05-30-25 | 6-DaHall 1-PDU-06-30-25 | 220 | 30 | 05 | 25 | 220 | 30 | 06 | 25 | [6 empty] | 3.7772 | 4.4484 | 8.2256 | 587.4 | 696.3 | 4.364 | 2402.6 |  |  | 3.2293 | 8.7707 | 적정함
| 6F-Y15 |  |  | A5-10-4 | B5-10-4 | U6-A5-27 / 2P 30A | U6-B5-27 / 2P 30A | 6-DaHall 1-PDU-05-30-27 | 6-DaHall 1-PDU-06-30-27 | 220 | 30 | 05 | 27 | 220 | 30 | 06 | 27 | [6 empty] | 3.8393 | 3.1651 | 7.0044 | 612.2 | 506.7 | 2.671 | 2402.6 |  |  | 3.2293 | -3.2293 | 사용초과 | 0 | 0
A807 | 6F-Y14 | Pyler | 12 | A5-10-5 | B5-10-5 | U6-A5-29 / 2P 30A | U6-B5-29 / 2P 30A | 6-DaHall 1-PDU-05-30-29 | 6-DaHall 1-PDU-06-30-29 | 220 | 30 | 05 | 29 | 220 | 30 | 06 | 29 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 12 | 무부하 랙
|  |  |  | A5-10-2 | B5-10-2 | U6-A5-23 / 2P 30A | U6-B5-23 / 2P 30A | 6-DaHall 1-PDU-05-30-23 | 6-DaHall 1-PDU-06-30-23 | 220 | 30 | 05 | 23 | 220 | 30 | 06 | 23 | [6 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A808 | 6F-Y13 | Servis | 1.6 | A5-10-6 | B5-10-6 | U6-A5-31 / 2P 30A | U6-B5-31 / 2P 30A | 6-DaHall 1-PDU-05-30-31 | 6-DaHall 1-PDU-06-30-31 | 220 | 30 | 05 | 31 | 220 | 30 | 06 | 31 | [6 empty] | 1.5458 | 0.38038 | 1.9261 | 251 | 45.4 | 0.432 | 296.4 |  |  | 0.39839 | 1.2016 | 적정함
A809 | 6F-Y12 | Terrapin Tech Co., Ltd. | 1.6 | A5-10-7 | B5-10-7 | U6-A5-33 / 2P 30A | U6-B5-33 / 2P 30A | 6-DaHall 1-PDU-05-30-33 | 6-DaHall 1-PDU-06-30-33 | 220 | 30 | 05 | 33 | 220 | 30 | 06 | 33 | [6 empty] | 1.1197 | 1.18 | 2.2997 | 146.7 | 145.5 | 0.416 | 292.2 |  |  | 0.39274 | 1.2073 | 적정함
A810 | 6F-Y11 | Sejong Telecom Inc. | 1.6 | A5-10-8 | B5-10-8 | U6-A5-35 / 2P 30A | U6-B5-35 / 2P 30A | 6-DaHall 1-PDU-05-30-35 | 6-DaHall 1-PDU-06-30-35 | 220 | 30 | 05 | 35 | 220 | 30 | 06 | 35 | [6 empty] | 0.68 | 0.39 | 1.07 | 88.2 | 44.7 | 0.193 | 132.9 |  |  | 0.17863 | 1.4214 | 적정함
B115 | [29 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B116 | 6F-S11 |  |  | A4-36-3 | B4-36-3 | U-A4-23 / 2P 30A | U-B4-23 / 2P 30A | 6-DaHall 1-PDU-11-30-23 | 6-DaHall 1-PDU-12-30-23 | 220 | 30 | 11 | 23 | 220 | 30 | 12 | 23 | U-A4 4P 200A | U-B4 4P 200A | UPS 출력배전반(A) #01, 4P 200A | UPS 출력배전반(B) #01, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B117 | 6F-S12 |  |  | A4-36-4 | B4-36-4 | U-A4-25 / 2P 30A | U-B4-25 / 2P 30A | 6-DaHall 1-PDU-11-30-25 | 6-DaHall 1-PDU-12-30-25 | 220 | 30 | 11 | 25 | 220 | 30 | 12 | 25 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B118 | 6F-S13 |  |  | A4-36-5 | B4-36-5 | U-A4-27 / 2P 30A | U-B4-27 / 2P 30A | 6-DaHall 1-PDU-11-30-27 | 6-DaHall 1-PDU-12-30-27 | 220 | 30 | 11 | 27 | 220 | 30 | 12 | 27 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
|  |  |  | U-A4-49 | U-B4-49 | U-A4-49 / 2P 30A | U-B4-49 / 2P 30A | 6-DaHall 1-PDU-11-30-49 | 6-DaHall 1-PDU-12-30-49 | 220 | 30 | 11 | 49 | 220 | 30 | 12 | 49 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B119 | 6F-S14 |  |  | A4-36-6 | B4-36-6 | U-A4-29 / 2P 30A | U-B4-29 / 2P 30A | 6-DaHall 1-PDU-11-30-29 | 6-DaHall 1-PDU-12-30-29 | 220 | 30 | 11 | 29 | 220 | 30 | 12 | 29 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B120 | 6F-S15 |  |  | A4-36-7 | B4-36-7 | U-A4-31 / 2P 30A | U-B4-31 / 2P 30A | 6-DaHall 1-PDU-11-30-31 | 6-DaHall 1-PDU-12-30-31 | 220 | 30 | 11 | 31 | 220 | 30 | 12 | 31 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
|  |  |  | U-A4-47 | U-B4-47 | U-A4-47 / 2P 30A | U-B4-47 / 2P 30A | 6-DaHall 1-PDU-11-30-47 | 6-DaHall 1-PDU-12-30-47 | 220 | 30 | 11 | 47 | 220 | 30 | 12 | 47 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B121 | 6F-S16 |  |  | A4-36-8 | B4-36-8 | U-A4-33 / 2P 30A | U-B4-33 / 2P 30A | 6-DaHall 1-PDU-11-30-33 | 6-DaHall 1-PDU-12-30-33 | 220 | 30 | 11 | 33 | 220 | 30 | 12 | 33 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B122 | 6F-S17 | [28 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B123 | 6F-S18 | [28 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B124 | 6F-S19 | [28 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B125 | [29 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B201 |  | Net Target | 2.2 | A1-13-5 | B1-13-5 |  |  | 6-DaHall 1-PDU-01-30-25 | 6-DaHall 1-PDU-02-30-25 | 220 | 30 | 01 | 25 | 220 | 30 | 02 | 25 | U-A1 4P 200A | U-B1 4P 200A | UPS 출력배전반(A) #04, 4P 200A | UPS 출력배전반(B) #02, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 2.2 | 무부하 랙
B202 | 6F-AA11 | Digital Edge Korea | 2.2 | A1-13-1 | B1-13-1 | U-A1-27 / 2P 30A | U-B1-27 / 2P 30A | 6-DaHall 1-PDU-01-30-27 | 6-DaHall 1-PDU-02-30-27 | 220 | 30 | 01 | 27 | 220 | 30 | 02 | 27 | [6 empty] | 2.2737 | 1.3432 | 3.6169 | 305.1 | 180.4 | 0.684 | 485.5 |  |  | 0.65255 | 1.5474 | 적정함
B203 | 6F-AA12 | Digital Edge Korea | 2.2 | A1-13-2 | B1-13-2 | U-A1-29 / 2P 30A | U-B1-29 / 2P 30A | 6-DaHall 1-PDU-01-30-29 | 6-DaHall 1-PDU-02-30-29 | 220 | 30 | 01 | 29 | 220 | 30 | 02 | 29 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 2.2 | 무부하 랙
B204 | 6F-AA13 | Net Target | 2.2 | A1-13-3 | B1-13-3 | U-A1-31 / 2P 30A | U-B1-31 / 2P 30A | 6-DaHall 1-PDU-01-30-31 | 6-DaHall 1-PDU-02-30-31 | 220 | 30 | 01 | 31 | 220 | 30 | 02 | 31 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 2.2 | 무부하 랙
B205 | 6F-AA14 | Net Target | 2.2 | A1-13-4 | B1-13-4 | U-A1-33 / 2P 30A | U-B1-33 / 2P 30A | 6-DaHall 1-PDU-01-30-33 | 6-DaHall 1-PDU-02-30-33 | 220 | 30 | 01 | 33 | 220 | 30 | 02 | 33 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 2.2 | 무부하 랙
B206 | 6F-AA15 | Net Target | 6 | A1-13-5 | B1-13-5 | U-A1-35 / 2P 30A | U-B1-35 / 2P 30A | 6-DaHall 1-PDU-01-30-35 | 6-DaHall 1-PDU-02-30-35 | 220 | 30 | 01 | 35 | 220 | 30 | 02 | 35 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 6 | 무부하 랙
B207 | 6F-AA16 |  |  | A1-13-6 | B1-13-6 | U-A1-37 / 2P 30A | U-B1-37 / 2P 30A | 6-DaHall 1-PDU-01-30-37 | 6-DaHall 1-PDU-02-30-37 | 220 | 30 | 01 | 37 | 220 | 30 | 02 | 37 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B208 | 6F-AA17 | Net Target | 2.2 | A1-13-7 | B1-13-7 | U-A1-39 / 2P 30A | U-B1-39 / 2P 30A | 6-DaHall 1-PDU-01-30-39 | 6-DaHall 1-PDU-02-30-39 | 220 | 30 | 01 | 39 | 220 | 30 | 02 | 39 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 2.2 | 무부하 랙
B209 | 6F-AA18 | Piolink | 2.2 | A1-13-8 | B1-13-8 | U-A1-41 / 2P 30A | U-B1-41 / 2P 30A | 6-DaHall 1-PDU-01-30-41 | 6-DaHall 1-PDU-02-30-41 | 220 | 30 | 01 | 41 | 220 | 30 | 02 | 41 | [6 empty] | 0.82312 | 0.62934 | 1.4525 | 120.7 | 87.3 | 0.366 | 208 |  |  | 0.27957 | 1.9204 | 적정함
B210 | 6F-AA19 | RXN Co., Ltd. | 4.4 | A1-13-8(2) | B1-13-8(2) | U-A1-49 / 2P 30A | U-B1-30 / 2P 30A | 6-DaHall 1-PDU-01-30-49 | 6-DaHall 1-PDU-02-30-30 | 220 | 30 | 01 | 49 | 220 | 30 | 02 | 30 | [6 empty] | 8.1177 | 8.0599 | 16.1776 | 1274.5 | 1256.3 | 4.392 | 2530.8 |  |  | 3.4016 | 0.99839 | 적정함
B211 |  | DEK, 층간 Patch Cabinet | [26 empty] | 0 |  |  |  | 0 | 0 | 무부하 랙
B215 | [29 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B216 | 6F-R11 |  |  | A1-16-1 | B1-16-1 | U-A1-45 / 2P 30A | U-B1-45 / 2P 30A | 6-DaHall 1-PDU-01-30-45 | 6-DaHall 1-PDU-02-30-45 | 220 | 30 | 01 | 45 | 220 | 30 | 02 | 45 | U-A1 4P 200A | U-B1 4P 200A | UPS 출력배전반(A) #04, 4P 200A | UPS 출력배전반(B) #02, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B217 | 6F-R12 |  |  | A1-16-2 | B1-16-2 | U-A1-47 / 2P 30A | U-B1-47 / 2P 30A | 6-DaHall 1-PDU-01-30-47 | 6-DaHall 1-PDU-02-30-47 | 220 | 30 | 01 | 47 | 220 | 30 | 02 | 47 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B218 | 6F-R13 |  |  | A5-16-3 | B5-16-3 | U6-A5-48 / 2P 30A | U6-B5-48 / 2P 30A | 6-DaHall 1-PDU-05-30-48 | 6-DaHall 1-PDU-06-30-48 | 220 | 30 | 05 | 48 | 220 | 30 | 06 | 48 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B219 | 6F-R14 |  |  | A1-16-4 | B1-16-4 | U-A1-18 / 2P 30A | U-B1-34 / 2P 30A | 6-DaHall 1-PDU-01-30-18 | 6-DaHall 1-PDU-02-30-34 | 220 | 30 | 01 | 18 | 220 | 30 | 02 | 34 | U-A1 4P 200A | U-B1 4P 200A | UPS 출력배전반(A) #04, 4P 200A | UPS 출력배전반(B) #02, 4P 200A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B220 | 6F-R15 | 에네이 |  | A1-16-5 | B1-16-5 | U-A1-20 / 2P 30A | U-B1-20 / 2P 30A | 6-DaHall 1-PDU-01-30-20 | 6-DaHall 1-PDU-02-30-20 | 220 | 30 | 01 | 20 | 220 | 30 | 02 | 20 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023/04/13 장비 이동 확인 후 Off 할 것 | 0 | 0 | 무부하 랙
B221 | 6F-R16 |  |  | A1-16-6 | B1-16-6 | U-A1-22 / 2P 30A | U-B1-22 / 2P 30A | 6-DaHall 1-PDU-01-30-22 | 6-DaHall 1-PDU-02-30-22 | 220 | 30 | 01 | 22 | 220 | 30 | 02 | 22 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B222 | 6F-R17 | 에네이 |  | A1-16-7 | B1-16-7 | U-A1-24 / 2P 30A | U-B1-24 / 2P 30A | 6-DaHall 1-PDU-01-30-24 | 6-DaHall 1-PDU-02-30-24 | 220 | 30 | 01 | 24 | 220 | 30 | 02 | 24 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023/04/13 장비 이동 확인 후 Off 할 것 | 0 | 0 | 무부하 랙
B223 | 6F-R18 |  |  | A1-16-8 | B1-16-8 | U-A1-26 / 2P 30A | U-B1-26 / 2P 30A | 6-DaHall 1-PDU-01-30-26 | 6-DaHall 1-PDU-02-30-26 | 220 | 30 | 01 | 26 | 220 | 30 | 02 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B224 | 6F-R19 |  |  | A1-16-9 | B1-16-9 | U-A1-28 / 2P 30A | U-B1-28 / 2P 30A | 6-DaHall 1-PDU-01-30-28 | 6-DaHall 1-PDU-02-30-28 | 220 | 30 | 01 | 28 | 220 | 30 | 02 | 28 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B225 | [29 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B301 | 6F-U10 | RXN Co., Ltd. | 2.2 | A5-14-1 | B5-14-1 | U6-A5-37 / 2P 30A | U6-B5-37 / 2P 30A | 6-DaHall 1-PDU-05-30-37 | 6-DaHall 1-PDU-06-30-37 | 220 | 30 | 05 | 37 | 220 | 30 | 06 | 37 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 3.4826 | 3.5799 | 7.0625 | 528.8 | 539.7 | 4.003 | 1068.5 |  |  | 1.4362 | 0.76384 | 적정함
B302 | 6F-U11 | DVS Network Korea Co., Ltd. | 2.2 | A5-14-2 | B5-14-2 | U6-A5-39 / 2P 30A | U6-B5-39 / 2P 30A | 6-DaHall 1-PDU-05-30-39 | 6-DaHall 1-PDU-06-30-39 | 220 | 30 | 05 | 39 | 220 | 30 | 06 | 39 | [6 empty] | 2.0972 | 1.9107 | 4.0079 | 327.6 | 294.5 | 0.907 | 622.1 |  |  | 0.83616 | 1.3638 | 적정함
B303 | 6F-U12 | Du System Co., Ltd. | 1.1 | A5-14-3 | B5-14-3 | U6-A5-41 / 2P 30A | U6-B5-41 / 2P 30A | 6-DaHall 1-PDU-05-30-41 | 6-DaHall 1-PDU-06-30-41 | 220 | 30 | 05 | 41 | 220 | 30 | 06 | 41 | [6 empty] | 1.4414 | 0.81301 | 2.2544 | 207.8 | 127.7 | 0.698 | 335.5 |  |  | 0.45094 | 0.64906 | 적정함
B304 | 6F-U13 | RXN Co., Ltd. | 2.2 | A5-14-4 | B5-14-4 | U6-A5-43 / 2P 30A | U6-B5-43 / 2P 30A | 6-DaHall 1-PDU-05-30-43 | 6-DaHall 1-PDU-06-30-43 | 220 | 30 | 05 | 43 | 220 | 30 | 06 | 43 | [6 empty] | 5.7522 | 4.891 | 10.6432 | 867.9 | 755.7 | 2.457 | 1623.6 |  |  | 2.1823 | 0.017742 | 적정함
B305 | 6F-U14 | RXN Co., Ltd. | 2.2 | A5-14-5 | B5-14-5 | U6-A5-45 / 2P 30A | U6-B5-45 / 2P 30A | 6-DaHall 1-PDU-05-30-45 | 6-DaHall 1-PDU-06-30-45 | 220 | 30 | 05 | 45 | 220 | 30 | 06 | 45 | [6 empty] | 5.0127 | 5.1112 | 10.1239 | 722.7 | 753.7 | 2.145 | 1476.4 |  |  | 1.9844 | 0.21559 | 적정함
B306 | 6F-U15 | RXN Co., Ltd. | 2.2 | A5-14-6 | B5-14-6 | U6-A5-47 / 2P 30A | U6-B5-47 / 2P 30A | 6-DaHall 1-PDU-05-30-47 | 6-DaHall 1-PDU-06-30-47 | 220 | 30 | 05 | 47 | 220 | 30 | 06 | 47 | [6 empty] | 3.5945 | 3.2764 | 19.565 | 584.9 | 534.2 | 2.245 | 3132.1 |  |  | 4.2098 | -2.0098 | 사용초과 | RXN Co., Ltd. | B306
[8 empty] | 6-DaHall 1-PDU-05-30-51 | 6-DaHall 1-PDU-06-30-51 |  | 30 | 05 | 51 | 220 | 30 | 06 | 51 | [6 empty] | 3.594 | 4.159 |  | 554.3 | 652.5 | 2.333 | 3132.1 |  |  | 4.2098 | -4.2098 | 사용초과 | 0 | 0
[8 empty] | 6-DaHall 1-PDU-05-30-53 | 6-DaHall 1-PDU-06-30-53 |  | 30 | 05 | 53 | 220 | 30 | 06 | 53 | [6 empty] | 4.3507 | 0.59047 |  | 711.2 | 95 | 1.662 | 3132.1 |  |  | 4.2098 | -4.2098 | 사용초과 | 0 | 0
B307 | 6F-U16 | Piolink Co., Ltd. | 2.2 | A5-14-7 | B5-14-7 | U6-A5-49 / 2P 30A | U6-B5-49 / 2P 30A | 6-DaHall 1-PDU-05-30-49 | 6-DaHall 1-PDU-06-30-49 | 220 | 30 | 05 | 49 | 220 | 30 | 06 | 49 | [6 empty] | 8.1769 | 1.341 | 9.5179 | 1242.3 | 194.9 | 2.167 | 1437.2 |  |  | 1.9317 | 0.26828 | 적정함
B308 | 6F-U17 | RXN Co., Ltd. | 2.2 | A5-14-8 | B5-14-8 | U6-A5-51 / 2P 30A | U6-B5-51 / 2P 30A | 6-DaHall 1-PDU-03-30-1 | 6-DaHall 1-PDU-04-30-1 | 220 | 30 | 03 | 1 | 220 | 30 | 04 | 1 | U-A2 4P 200A | U-B2 4P 200A | UPS 출력배전반(A) #02, 4P 200A | UPS 출력배전반(B) #04, 4P 200A |  |  | 5.0595 | 4.0983 | 20.3979 | 834.6 | 667.8 | 3.147 | 3340.2 |  |  | 4.4895 | -2.2895 | 사용초과 | RXN Co., Ltd. | B308
[8 empty] | 6-DaHall 1-PDU-03-30-3 | 6-DaHall 1-PDU-04-30-3 |  | 30 | 03 | 3 | 220 | 30 | 04 | 3 | [6 empty] | 4.2526 | 4.8921 |  | 702.9 | 807.3 | 3.154 | 3340.2 |  |  | 4.4895 | -4.4895 | 사용초과 | 0 | 0
[8 empty] | 6-DaHall 1-PDU-03-30-5 | 6-DaHall 1-PDU-04-30-5 |  | 30 | 03 | 5 | 220 | 30 | 04 | 5 | [6 empty] | 0.90176 | 1.1937 |  | 133.1 | 194.5 | 0.518 | 3340.2 |  |  | 4.4895 | -4.4895 | 사용초과 | 0 | 0
B309 | 6F-U18 | RXN Co., Ltd. | 2.2 | A5-14-9 | B5-14-9 | U6-A5-53 / 2P 30A | U6-B5-53 / 2P 30A | 6-DaHall 1-PDU-03-30-7 | 6-DaHall 1-PDU-04-30-7 | 220 | 30 | 03 | 7 | 220 | 30 | 04 | 7 | [6 empty] | 3.8382 | 4.0589 | 14.3143 | 601.1 | 645.1 | 1.828 | 2267.4 |  |  | 3.0476 | -0.84758 | 사용초과 | RXN Co., Ltd. | B309
[8 empty] | 6-DaHall 1-PDU-03-30-9 | 6-DaHall 1-PDU-04-30-9 |  | 30 | 03 | 9 | 220 | 30 | 04 | 9 | [6 empty] | 2.9847 | 3.4325 |  | 470.6 | 550.6 | 1.649 | 2267.4 |  |  | 3.0476 | -3.0476 | 사용초과 | 0 | 0
B310 |  | RXN Co., Ltd. | 2.2 |  |  |  |  | 6-DaHall 1-PDU-03-30-11 | 6-DaHall 1-PDU-04-30-11 | 220 | 30 | 03 | 11 | 220 | 30 | 04 | 11 | [6 empty] | 3.1839 | 3.8195 | 14.317 | 524.4 | 625.6 | 2.038 | 2309.8 |  |  | 3.1046 | -0.90457 | 사용초과 | RXN Co., Ltd. | B310
[8 empty] | 6-DaHall 1-PDU-03-30-13 | 6-DaHall 1-PDU-04-30-13 |  | 30 | 03 | 13 | 220 | 30 | 04 | 13 | [6 empty] | 4.4701 | 2.8435 |  | 695.8 | 464 | 2.686 | 2309.8 |  |  | 3.1046 | -3.1046 | 사용초과 | 0 | 0
B311 |  | RXN Co., Ltd. | 2.2 |  |  |  |  | 6-DaHall 1-PDU-03-30-15 | 6-DaHall 1-PDU-04-30-15 |  | 30 | 03 | 15 | 220 | 30 | 04 | 15 | [6 empty] | 4.0322 | 3.7444 | 11.6766 | 609.6 | 558.8 | 1.684 | 1732.2 |  |  | 2.3282 | -0.12823 | 사용초과 | RXN Co., Ltd. | B311
[8 empty] | 6-DaHall 1-PDU-03-30-17 | 6-DaHall 1-PDU-04-30-17 | 220 | 30 | 03 | 17 | 220 | 30 | 04 | 17 | [6 empty] | 2.0482 | 1.8518 |  | 298.4 | 265.4 | 0.806 | 1732.2 |  |  | 2.3282 | -2.3282 | 사용초과 | 0 | 0
B315 | [29 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B316 | 6F-Q11 |  |  | A5-17-1 | B5-17-1 | U6-A5-20 / 2P 30A | U6-B5-20 / 2P 30A | 6-DaHall 1-PDU-05-30-20 | 6-DaHall 1-PDU-06-30-20 | 220 | 30 | 05 | 20 | 220 | 30 | 06 | 20 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B317 | 6F-Q12 |  |  | A5-17-2 | B5-17-2 | U6-A5-22 / 2P 30A | U6-B5-22 / 2P 30A | 6-DaHall 1-PDU-05-30-22 | 6-DaHall 1-PDU-06-30-22 | 220 | 30 | 05 | 22 | 220 | 30 | 06 | 22 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B318 | 6F-Q13 |  |  | A5-17-3 | B5-17-3 | U6-A5-24 / 2P 30A | U6-B5-24 / 2P 30A | 6-DaHall 1-PDU-05-30-24 | 6-DaHall 1-PDU-06-30-24 | 220 | 30 | 05 | 24 | 220 | 30 | 06 | 24 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B319 | 6F-Q14 |  |  | A5-17-4 | B5-17-4 | U6-A5-26 / 2P 30A | U6-B5-26 / 2P 30A | 6-DaHall 1-PDU-05-30-26 | 6-DaHall 1-PDU-06-30-26 | 220 | 30 | 05 | 26 | 220 | 30 | 06 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B320 | 6F-Q15 |  |  | A5-17-5 | B5-17-5 | U6-A5-28 / 2P 30A | U6-B5-28 / 2P 30A | 6-DaHall 1-PDU-05-30-28 | 6-DaHall 1-PDU-06-30-28 | 220 | 30 | 05 | 28 | 220 | 30 | 06 | 28 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B321 | 6F-Q16 |  |  | A5-17-6 | B5-17-6 | U6-A5-30 / 2P 30A | U6-B5-30 / 2P 30A | 6-DaHall 1-PDU-05-30-30 | 6-DaHall 1-PDU-06-30-30 | 220 | 30 | 05 | 30 | 220 | 30 | 06 | 30 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B322 | 6F-Q17 |  |  | A5-17-7 | B5-17-7 | U6-A5-32 / 2P 30A | U6-B5-32 / 2P 30A | 6-DaHall 1-PDU-05-30-32 | 6-DaHall 1-PDU-06-30-32 | 220 | 30 | 05 | 32 | 220 | 30 | 06 | 32 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B323 | 6F-Q18 |  |  | A5-17-8 | B5-17-8 | U6-A5-34 / 2P 30A | U6-B5-34 / 2P 30A | 6-DaHall 1-PDU-05-30-34 | 6-DaHall 1-PDU-06-30-34 | 220 | 30 | 05 | 34 | 220 | 30 | 06 | 34 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B324 | 6F-Q19 |  |  | A5-17-9 | B5-17-9 | U6-A5-36 / 2P 30A | U6-B5-36 / 2P 30A | 6-DaHall 1-PDU-05-30-36 | 6-DaHall 1-PDU-06-30-36 | 220 | 30 | 05 | 36 | 220 | 30 | 06 | 36 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B325 | [29 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B401 |  | 주식회사 메타넷티플랫폼 | 2.2 | A5-15-5(2) | B5-15-5(2) | U6-A5-54 / 2P 30A | U6-B5-54 / 2P 30A | 6-DaHall 1-PDU-05-30-54 | 6-DaHall 1-PDU-06-30-54 | 220 | 30 | 05 | 54 | 220 | 30 | 06 | 54 | [6 empty] | 4.2693 | 2.4015 | 6.6707 | 619.3 | 362.7 | 1.426 | 982 | 랙 미설치 | 제로투세븐(메타넷) 이동설치 예정(4/15) | 1.3199 | 0.88011 | 적정함
B402 | 6F-T11 | 주식회사 메타넷티플랫폼 | 2.2 | A5-15-1 | B5-15-1 | U6-A5-02 / 2P 30A | U6-B5-02 / 2P 30A | 6-DaHall 1-PDU-05-30-2 | 6-DaHall 1-PDU-06-30-2 | 220 | 30 | 05 | 2 | 220 | 30 | 06 | 2 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 11.5171 | 10.4239 | 21.941 | 1875.7 | 1692.2 | 5.421 | 3567.9 | 랙 미설치 | 제로투세븐(메타넷) 이동설치 예정(4/15) | 4.7956 | -2.5956 | 사용초과 | 주식회사 메타넷티플랫폼 | B402
B403 | 6F-T12 | U.I.WINS | 2.2 | A5-15-2 | B5-15-2 | U6-A5-04 / 2P 30A | U6-B5-04 / 2P 30A | 6-DaHall 1-PDU-05-30-4 | 6-DaHall 1-PDU-06-30-4 | 220 | 30 | 05 | 4 | 220 | 30 | 06 | 4 | [6 empty] | 5.2189 | 4.0793 | 9.2981 | 780.1 | 629.9 | 2.094 | 1410 |  |  | 1.8952 | 0.30484 | 적정함
B404 | 6F-T13 | ETSIN Co., Ltd. | 2.2 | A5-15-3 | B5-15-3 | U6-A5-06 / 2P 30A | U6-B5-06 / 2P 30A | 6-DaHall 1-PDU-05-30-6 | 6-DaHall 1-PDU-06-30-6 | 220 | 30 | 05 | 6 | 220 | 30 | 06 | 6 | [6 empty] | 0.71 | 0.69123 | 1.4012 | 96.8 | 92.6 | 0.28 | 189.4 |  |  | 0.25457 | 1.9454 | 적정함
B405 | 6F-T14 | Dongyang & I&C Co., Ltd. | 1.1 | A5-15-4 | B5-15-4 | U6-A5-08 / 2P 30A | U6-B5-08 / 2P 30A | 6-DaHall 1-PDU-05-30-8 | 6-DaHall 1-PDU-06-30-8 | 220 | 30 | 05 | 8 | 220 | 30 | 06 | 8 | [6 empty] | 2.7817 | 3.4827 | 6.2644 | 395.4 | 530.7 | 1.699 | 926.1 |  |  | 1.2448 | -0.14476 | 사용초과 | Dongyang & I&C Co., Ltd. | B405
B406 | 6F-T15 |  | 2.2 | A5-15-5 | B5-15-5 | U6-A5-10 / 2P 30A | U6-B5-10 / 2P 30A | 6-DaHall 1-PDU-05-30-10 | 6-DaHall 1-PDU-06-30-10 | 220 | 30 | 05 | 10 | 220 | 30 | 06 | 10 | [6 empty] | 1.007 | 0.54039 | 1.5474 | 131.5 | 72.3 | 0.302 | 203.8 |  | 제로투세븐(메타넷) 이동설치 예정(4/15) | 0.27392 | 1.9261 | 적정함
B407 | 6F-T16 | ELIMNET Co., Ltd. | 0.55 | A5-15-6 | B5-15-6 | U6-A5-12 / 2P 30A | U6-B5-12 / 2P 30A | 6-DaHall 1-PDU-05-30-12 | 6-DaHall 1-PDU-06-30-12 | 220 | 30 | 05 | 12 | 220 | 30 | 06 | 12 | [6 empty] | 1.4167 | 0 | 1.4167 | 212 | 0 | 0.302 | 212 |  |  | 0.28495 | 0.26505 | 적정함
B408 | 6F-T17 | MarkPro | 2.2 | A5-15-7 | B5-15-7 | U6-A5-14 / 2P 30A | U6-B5-14 / 2P 30A | 6-DaHall 1-PDU-05-30-14 | 6-DaHall 1-PDU-06-30-14 | 220 | 30 | 05 | 14 | 220 | 30 | 06 | 14 | [6 empty] | 4.9341 | 3.2451 | 8.1792 | 779.2 | 450.8 | 1.857 | 1230 |  |  | 1.6532 | 0.54677 | 적정함
B409 | 6F-T18 | MarkPro | 2.2 | A5-15-8 | B5-15-8 | U6-A5-16 / 2P 30A | U6-B5-16 / 2P 30A | 6-DaHall 1-PDU-05-30-16 | 6-DaHall 1-PDU-06-30-16 | 220 | 30 | 05 | 16 | 220 | 30 | 06 | 16 | [6 empty] | 3.3747 | 4.0675 | 7.4422 | 487.3 | 605.1 | 1.671 | 1092.4 |  |  | 1.4683 | 0.73172 | 적정함
B410 | 6F-T19 | Enei | 1.1 | A1-13-9 | B1-13-9 | U-A1-43 / 2P 30A | U-B1-43 / 2P 30A | 6-DaHall 1-PDU-01-30-43 | 6-DaHall 1-PDU-02-30-43 | 220 | 30 | 01 | 43 | 220 | 30 | 02 | 43 | U-A1 4P 200A | U-B1 4P 200A | UPS 출력배전반(A) #04, 4P 200A | UPS 출력배전반(B) #02, 4P 200A |  |  | 3.7276 | 3.7623 | 7.4899 | 585.4 | 585.4 | 2.527 | 1170.8 | 2023/04/13 이설 후 전기사용예정 |  | 1.5737 | -0.47366 | 사용초과 | Enei | B410
B411 |  | Enei | 2.2 |  |  | U-A1-42 / 2P 30A | U-B1-42 / 2P 30A | 6-DaHall 1-PDU-01-30-42 | 6-DaHall 1-PDU-02-30-42 | 220 | 30 | 01 | 42 | 220 | 30 | 02 | 42 | [6 empty] | 3.9927 | 4.105 | 8.0977 | 634 | 643.1 | 1.922 | 1277.1 | 2023/04/13 이설 후 전기사용예정 |  | 1.7165 | 0.48347 | 적정함
B415 | [29 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B416 | 6F-P11 |  |  | A5-18-1 | B5-18-1 | U6-A5-38 / 2P 30A | U6-B5-38 / 2P 30A | 6-DaHall 1-PDU-05-30-38 | 6-DaHall 1-PDU-06-30-38 | 220 | 30 | 05 | 38 | 220 | 30 | 06 | 38 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B417 | 6F-P12 |  |  | A5-18-2 | B5-18-2 | U6-A5-40 / 2P 30A | U6-B5-40 / 2P 30A | 6-DaHall 1-PDU-05-30-40 | 6-DaHall 1-PDU-06-30-40 | 220 | 30 | 05 | 40 | 220 | 30 | 06 | 40 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B418 | 6F-P13 |  |  | A5-18-3 | B5-18-3 | U6-A5-42 / 2P 30A | U6-B5-42 / 2P 30A | 6-DaHall 1-PDU-05-30-42 | 6-DaHall 1-PDU-06-30-42 | 220 | 30 | 05 | 42 | 220 | 30 | 06 | 42 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B419 | 6F-P14 |  |  | A5-18-4 | B5-18-4 | U6-A5-44 / 2P 30A | U6-B5-44 / 2P 30A | 6-DaHall 1-PDU-05-30-44 | 6-DaHall 1-PDU-06-30-44 | 220 | 30 | 05 | 44 | 220 | 30 | 06 | 44 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B420 | 6F-P15 |  |  | A5-18-5 | B5-18-5 | U6-A5-46 / 2P 30A | U6-B5-46 / 2P 30A | 6-DaHall 1-PDU-05-30-46 | 6-DaHall 1-PDU-06-30-46 | 220 | 30 | 05 | 46 | 220 | 30 | 06 | 46 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B421 | 6F-P16 |  |  | A7-18-6 | B7-18-6 | U6-A7-01 / 2P 30A | U6-B7-01 / 2P 30A | 6-DaHall 1-PDU-13-30-1 | 6-DaHall 1-PDU-14-30-1 | 220 | 30 | 13 | 1 | 220 | 30 | 14 | 1 | U6-A7 4P 300A | U6-B7 4P 300A | LV-6A #07, 3P 320A | LV-6B #03, 3P 320A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B422 | 6F-P17 |  |  | A7-18-7 | B7-18-7 | U6-A7-03 / 2P 30A | U6-B7-03 / 2P 30A | 6-DaHall 1-PDU-13-30-3 | 6-DaHall 1-PDU-14-30-3 | 220 | 30 | 13 | 3 | 220 | 30 | 14 | 3 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B423 | 6F-P18 |  |  | A7-18-8 | B7-18-8 | U6-A7-05 / 2P 30A | U6-B7-05 / 2P 30A | 6-DaHall 1-PDU-13-30-5 | 6-DaHall 1-PDU-14-30-5 | 220 | 30 | 13 | 5 | 220 | 30 | 14 | 5 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B424 | 6F-P19 |  |  | A7-18-9 | B7-18-9 | U6-A7-07 / 2P 30A | U6-B7-07 / 2P 30A | 6-DaHall 1-PDU-13-30-7 | 6-DaHall 1-PDU-14-30-7 | 220 | 30 | 13 | 7 | 220 | 30 | 14 | 7 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
B425 | [28 empty] | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
C101 | [29 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
C102 | 6F-O11 |  |  | A4-19-1 | B4-19-1 | U6-A7-52 / 2P 30A | U6-B7-52 / 2P 30A | 6-DaHall 1-PDU-13-30-52 | 6-DaHall 1-PDU-14-30-52 | 220 | 30 | 13 | 52 | 220 | 30 | 14 | 52 | U6-A7 4P 300A | U6-B7 4P 300A | LV-6A #07, 3P 320A | LV-6B #03, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C103 | 6F-O12 |  |  | A4-19-2 | B4-19-2 | U-A4-03 / 2P 30A | U-B4-03 / 2P 30A | 6-DaHall 1-PDU-11-30-3 | 6-DaHall 1-PDU-12-30-3 | 220 | 30 | 11 | 3 | 220 | 30 | 12 | 3 | U-A4 4P 200A | U-B4 4P 200A | UPS 출력배전반(A) #01, 4P 200A | UPS 출력배전반(B) #01, 4P 200A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 철거완료(9/1) |  | 0 | 0 | 무부하 랙
C104 | 6F-O13 |  |  | A4-19-3 | B4-19-3 | U-A4-05 / 2P 30A | U-B4-05 / 2P 30A | 6-DaHall 1-PDU-11-30-5 | 6-DaHall 1-PDU-12-30-5 | 220 | 30 | 11 | 5 | 220 | 30 | 12 | 5 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C105 | 6F-O14 |  |  | A4-19-4 | B4-19-4 | U-A4-07 / 2P 30A | U-B4-07 / 2P 30A | 6-DaHall 1-PDU-11-30-7 | 6-DaHall 1-PDU-12-30-7 | 220 | 30 | 11 | 7 | 220 | 30 | 12 | 7 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C106 | 6F-O15 |  |  | A4-19-5 | B4-19-5 | U-A4-09 / 2P 30A | U-B4-09 / 2P 30A | 6-DaHall 1-PDU-11-30-9 | 6-DaHall 1-PDU-12-30-9 | 220 | 30 | 11 | 9 | 220 | 30 | 12 | 9 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 철거완료(9/1) |  | 0 | 0 | 무부하 랙
C107 | 6F-O16 |  |  | A4-19-6 | B4-19-6 | U-A4-11 / 2P 30A | U-B4-11 / 2P 30A | 6-DaHall 1-PDU-11-30-11 | 6-DaHall 1-PDU-12-30-11 | 220 | 30 | 11 | 11 | 220 | 30 | 12 | 11 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 철거완료(9/1) |  | 0 | 0 | 무부하 랙
C108 | 6F-O17 |  |  | A4-19-7 | B4-19-7 | U-A4-13 / 2P 30A | U-A3-31 / 2P 30A | 6-DaHall 1-PDU-11-30-13 | 6-DaHall 1-PDU-09-30-31 | 220 | 30 | 11 | 13 | 220 | 30 | 09 | 31 |  | U-A3 4P 200A |  | UPS 출력배전반(A) #03, 4P 200A |  | TR-6A 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 철거완료(9/1) |  | 0 | 0 | 무부하 랙
C109 | 6F-O18 |  |  | A4-19-8 | B4-19-8 | U-A4-15 / 2P 30A | U-B4-15 / 2P 30A | 6-DaHall 1-PDU-11-30-15 | 6-DaHall 1-PDU-12-30-15 | 220 | 30 | 11 | 15 | 220 | 30 | 12 | 15 |  | U-B4 4P 200A |  | UPS 출력배전반(B) #01, 4P 200A |  | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 철거완료(9/1) |  | 0 | 0 | 무부하 랙
C110 | 6F-O19 |  |  | A4-19-9 | B4-19-9 | U-A4-17 / 2P 30A | U-B4-17 / 2P 30A | 6-DaHall 1-PDU-11-30-17 | 6-DaHall 1-PDU-12-30-17 | 220 | 30 | 11 | 17 | 220 | 30 | 12 | 17 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C201 | [29 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
C202 | 6F-N11 |  |  | A4-20-1 | B4-20-1 | U-A4-02 / 2P 30A | U-B4-02 / 2P 30A | 6-DaHall 1-PDU-11-30-2 | 6-DaHall 1-PDU-12-30-2 | 220 | 30 | 11 | 2 | 220 | 30 | 12 | 2 | U-A4 4P 200A | U-B4 4P 200A | UPS 출력배전반(A) #01, 4P 200A | UPS 출력배전반(B) #01, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CB Off (22년 5월) |  | 0 | 0 | 무부하 랙
C203 | 6F-N12 |  |  | A4-20-2 | B4-20-2 | U-A4-04 / 2P 30A | U-B4-04 / 2P 30A | 6-DaHall 1-PDU-11-30-4 | 6-DaHall 1-PDU-12-30-4 | 220 | 30 | 11 | 4 | 220 | 30 | 12 | 4 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CB Off (22년 5월) |  | 0 | 0 | 무부하 랙
C204 | 6F-N13 |  |  | A4-20-3 | B4-20-3 | U-A4-06 / 2P 30A | U-B4-06 / 2P 30A | 6-DaHall 1-PDU-11-30-6 | 6-DaHall 1-PDU-12-30-6 | 220 | 30 | 11 | 6 | 220 | 30 | 12 | 6 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CB Off (22년 5월) |  | 0 | 0 | 무부하 랙
C205 | 6F-N14 |  |  | A4-20-4 | B4-20-4 | U-A4-08 / 2P 30A | U-B4-08 / 2P 30A | 6-DaHall 1-PDU-11-30-8 | 6-DaHall 1-PDU-12-30-8 | 220 | 30 | 11 | 8 | 220 | 30 | 12 | 8 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CB Off (22년 5월) |  | 0 | 0 | 무부하 랙
C206 | 6F-N15 |  |  | A4-20-5 | B4-20-5 | U-A4-10 / 2P 30A | U-B4-10 / 2P 30A | 6-DaHall 1-PDU-11-30-10 | 6-DaHall 1-PDU-12-30-10 | 220 | 30 | 11 | 10 | 220 | 30 | 12 | 10 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | '22/02/22 전기투입 |  | 0 | 0 | 무부하 랙
C207 | 6F-N16 |  |  | A4-20-6 | B4-20-6 | U-A4-12 / 2P 30A | U-B4-12 / 2P 30A | 6-DaHall 1-PDU-11-30-12 | 6-DaHall 1-PDU-12-30-12 | 220 | 30 | 11 | 12 | 220 | 30 | 12 | 12 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C208 | 6F-N17 |  |  | A4-20-7 | #B3-20-7 | U-A4-14 / 2P 30A | U-B3-21 / 2P 30A | 6-DaHall 1-PDU-11-30-14 | 6-DaHall 1-PDU-10-30-21 | 220 | 30 | 11 | 14 | 220 | 30 | 10 | 21 |  | U-B3 4P 200A |  | UPS 출력배전반(B) #03, 4P 200A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C209 | 6F-N18 |  |  | A4-20-8 | B4-20-8 | U-A4-16 / 2P 30A | U-B4-16 / 2P 30A | 6-DaHall 1-PDU-11-30-16 | 6-DaHall 1-PDU-12-30-16 | 220 | 30 | 11 | 16 | 220 | 30 | 12 | 16 |  | U-B4 4P 200A |  | UPS 출력배전반(B) #01, 4P 200A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C210 | 6F-N19 |  |  | A4-20-9 | B4-20-9 | U-A4-18 / 2P 30A | U-B4-18 / 2P 30A | 6-DaHall 1-PDU-11-30-18 | 6-DaHall 1-PDU-12-30-18 | 220 | 30 | 11 | 18 | 220 | 30 | 12 | 18 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C301 | [29 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
C302 | 6F-M11 |  |  | A3-21-1 | B3-21-1 | U-A3-01 / 2P 30A | U-B3-01 / 2P 30A | 6-DaHall 1-PDU-09-30-1 | 6-DaHall 1-PDU-10-30-1 | 220 | 30 | 09 | 1 | 220 | 30 | 10 | 1 | U-A3 4P 200A | U-B3 4P 200A | UPS 출력배전반(A) #03, 4P 200A | UPS 출력배전반(B) #03, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C303 | 6F-M12 |  |  | A3-21-2 | B3-21-2 | U-A3-03 / 2P 30A | U-B3-03 / 2P 30A | 6-DaHall 1-PDU-09-30-3 | 6-DaHall 1-PDU-10-30-3 | 220 | 30 | 09 | 3 | 220 | 30 | 10 | 3 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C304 | 6F-M13 |  |  | A3-21-3 | B3-21-3 | U-A3-05 / 2P 30A | U-B3-05 / 2P 30A | 6-DaHall 1-PDU-09-30-5 | 6-DaHall 1-PDU-10-30-5 | 220 | 30 | 09 | 5 | 220 | 30 | 10 | 5 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
|  |  |  | A7-21-3(2) | B7-21-3(2) | U6-A7-32 / 2P 30A | U6-B7-34 / 2P 30A | 6-DaHall 1-PDU-13-30-32 | 6-DaHall 1-PDU-14-30-34 | 220 | 30 | 13 | 32 | 220 | 30 | 14 | 34 | U6-A7 4P 300A | U6-B7 4P 300A | LV-6A #07, 3P 320A | LV-6B #03, 3P 320A |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
|  |  |  | A7-21-3(3) | B7-21-3(3) | U6-A7-30 / 2P 30A | U6-B7-30 / 2P 30A | 6-DaHall 1-PDU-13-30-30 | 6-DaHall 1-PDU-14-30-30 | 220 | 30 | 13 | 30 | 220 | 30 | 14 | 30 | [6 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C305 | 6F-M14 |  |  | A3-21-4 | B3-21-4 | U-A3-07 / 2P 30A | U-B3-07 / 2P 30A | 6-DaHall 1-PDU-09-30-7 | 6-DaHall 1-PDU-10-30-7 | 220 | 30 | 09 | 7 | 220 | 30 | 10 | 7 | U-A3 4P 200A | U-B3 4P 200A | UPS 출력배전반(A) #03, 4P 200A | UPS 출력배전반(B) #03, 4P 200A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
|  |  |  | A7-21-4(2) | B7-21-4(2) | U6-A7-34 / 2P 30A | U6-B7-32 / 2P 30A | 6-DaHall 1-PDU-13-30-34 | 6-DaHall 1-PDU-14-30-32 | 220 | 30 | 13 | 34 | 220 | 30 | 14 | 32 | U6-A7 4P 300A | U6-B7 4P 300A | LV-6A #07, 3P 320A | LV-6B #03, 3P 320A |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
|  |  |  | A7-21-4(3) | B7-21-4(3) | U6-A7-28 / 2P 30A | U6-B7-28 / 2P 30A | 6-DaHall 1-PDU-13-30-28 | 6-DaHall 1-PDU-14-30-28 | 220 | 30 | 13 | 28 | 220 | 30 | 14 | 28 | [6 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C306 | 6F-M15 |  |  | A3-21-5 | B3-21-5 | U-A3-09 / 2P 30A | U-B3-09 / 2P 30A | 6-DaHall 1-PDU-09-30-9 | 6-DaHall 1-PDU-10-30-9 | 220 | 30 | 09 | 9 | 220 | 30 | 10 | 9 | U-A3 4P 200A | U-B3 4P 200A | UPS 출력배전반(A) #03, 4P 200A | UPS 출력배전반(B) #03, 4P 200A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022/07/01, 알렉스엔 증설예정 |  | 0 | 0 | 무부하 랙
C307 | 6F-M16 |  |  | A3-21-6 | B3-21-6 | U-A3-11 / 2P 30A | U-B3-11 / 2P 30A | 6-DaHall 1-PDU-09-30-11 | 6-DaHall 1-PDU-10-30-11 | 220 | 30 | 09 | 11 | 220 | 30 | 10 | 11 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C308 | 6F-M17 |  |  | A3-21-7 | B3-21-7 | U-A3-13 / 2P 30A | U-B3-13 / 2P 30A | 6-DaHall 1-PDU-09-30-13 | 6-DaHall 1-PDU-10-30-13 | 220 | 30 | 09 | 13 | 220 | 30 | 10 | 13 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C309 | 6F-M18 |  |  | A3-21-8 | B3-21-8 | U-A3-15 / 2P 30A | U-B3-15 / 2P 30A | 6-DaHall 1-PDU-09-30-15 | 6-DaHall 1-PDU-10-30-15 | 220 | 30 | 09 | 15 | 220 | 30 | 10 | 15 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C310 | 6F-M19 |  |  | A3-21-9 | B3-21-9 | U-A3-17 / 2P 30A | U-B3-17 / 2P 30A | 6-DaHall 1-PDU-09-30-17 | 6-DaHall 1-PDU-10-30-17 | 220 | 30 | 09 | 17 | 220 | 30 | 10 | 17 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C401 | [29 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
C402 | 6F-L11 |  |  | A3-22-1 | B3-22-1 | U-A3-02 / 2P 30A | U-B3-02 / 2P 30A | 6-DaHall 1-PDU-09-30-2 | 6-DaHall 1-PDU-10-30-2 | 220 | 30 | 09 | 2 | 220 | 30 | 10 | 2 | U-A3 4P 200A | U-B3 4P 200A | UPS 출력배전반(A) #03, 4P 200A | UPS 출력배전반(B) #03, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C403 | 6F-L12 |  |  | A3-22-2 | B3-22-2 | U-A3-04 / 2P 30A | U-B3-04 / 2P 30A | 6-DaHall 1-PDU-09-30-4 | 6-DaHall 1-PDU-10-30-4 | 220 | 30 | 09 | 4 | 220 | 30 | 10 | 4 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C404 | 6F-L13 |  |  | A3-22-3 | B3-22-3 | U-A3-06 / 2P 30A | U-B3-06 / 2P 30A | 6-DaHall 1-PDU-09-30-6 | 6-DaHall 1-PDU-10-30-6 | 220 | 30 | 09 | 6 | 220 | 30 | 10 | 6 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C405 | 6F-L14 |  |  | A3-22-4 | B3-22-4 | U-A3-08 / 2P 30A | U-B3-08 / 2P 30A | 6-DaHall 1-PDU-09-30-8 | 6-DaHall 1-PDU-10-30-8 | 220 | 30 | 09 | 8 | 220 | 30 | 10 | 8 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 제로투세븐(메타넷) 이동 및 현위치 철거 예정(4/15) | 0 | 0 | 무부하 랙
C406 | 6F-L15 |  |  | A3-22-5 | B3-22-5 | U-A3-10 / 2P 30A | U-B3-10 / 2P 30A | 6-DaHall 1-PDU-09-30-10 | 6-DaHall 1-PDU-10-30-10 | 220 | 30 | 09 | 10 | 220 | 30 | 10 | 10 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 제로투세븐(메타넷) 이동 및 현위치 철거 예정(4/15) | 0 | 0 | 무부하 랙
C407 | 6F-L16 |  |  | A3-22-6 | B3-22-6 | U-A3-12 / 2P 30A | U-B3-12 / 2P 30A | 6-DaHall 1-PDU-09-30-12 | 6-DaHall 1-PDU-10-30-12 | 220 | 30 | 09 | 12 | 220 | 30 | 10 | 12 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 제로투세븐(메타넷) 이동 및 현위치 철거 예정(4/15) | 0 | 0 | 무부하 랙
C408 | 6F-L17 |  |  | A3-22-7 | B3-22-7 | U-A3-14 / 2P 30A | U-B3-14 / 2P 30A | 6-DaHall 1-PDU-09-30-14 | 6-DaHall 1-PDU-10-30-14 | 220 | 30 | 09 | 14 | 220 | 30 | 10 | 14 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C409 | 6F-L18 |  |  | A3-22-8 | B3-22-8 | U-A3-16 / 2P 30A | U-B3-16 / 2P 30A | 6-DaHall 1-PDU-09-30-16 | 6-DaHall 1-PDU-10-30-16 | 220 | 30 | 09 | 16 | 220 | 30 | 10 | 16 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 철거완료(9/1) |  | 0 | 0 | 무부하 랙
C410 | 6F-L19 |  |  | A3-22-9 | B3-22-9 | U-A3-18 / 2P 30A | U-B3-18 / 2P 30A | 6-DaHall 1-PDU-09-30-18 | 6-DaHall 1-PDU-10-30-18 | 220 | 30 | 09 | 18 | 220 | 30 | 10 | 18 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 철거완료(9/1) |  | 0 | 0 | 무부하 랙
C501 | [29 empty] | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
C502 | 6F-K11 |  |  | A3-23-1 | B3-23-1 | U-A3-20 / 2P 30A | U-B3-20 / 2P 30A | 6-DaHall 1-PDU-09-30-20 | 6-DaHall 1-PDU-10-30-20 | 220 | 30 | 09 | 20 | 220 | 30 | 10 | 20 | U-A3 4P 200A | U-B3 4P 200A | UPS 출력배전반(A) #03, 4P 200A | UPS 출력배전반(B) #03, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C503 | 6F-K12 |  |  | A3-23-2 | B3-23-2 | U-A3-22 / 2P 30A | U-B3-22 / 2P 30A | 6-DaHall 1-PDU-09-30-22 | 6-DaHall 1-PDU-10-30-22 | 220 | 30 | 09 | 22 | 220 | 30 | 10 | 22 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C504 | 6F-K13 |  |  | A3-23-3 | B3-23-3 | U-A3-24 / 2P 30A | U-B3-48 / 2P 30A | 6-DaHall 1-PDU-09-30-24 | 6-DaHall 1-PDU-10-30-48 | 220 | 30 | 09 | 24 | 220 | 30 | 10 | 48 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C505 | 6F-K14 |  |  | A3-23-4 | B3-23-4 | U-A3-26 / 2P 30A | U-B3-26 / 2P 30A | 6-DaHall 1-PDU-09-30-26 | 6-DaHall 1-PDU-10-30-26 | 220 | 30 | 09 | 26 | 220 | 30 | 10 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C506 | 6F-K15 |  |  | A3-23-5 | B3-23-5 | U-A3-28 / 2P 30A | U-B3-28 / 2P 30A | 6-DaHall 1-PDU-09-30-28 | 6-DaHall 1-PDU-10-30-28 | 220 | 30 | 09 | 28 | 220 | 30 | 10 | 28 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C507 | 6F-K16 |  |  | A3-23-6 | B3-23-6 | U-A3-30 / 2P 30A | U-B3-30 / 2P 30A | 6-DaHall 1-PDU-09-30-30 | 6-DaHall 1-PDU-10-30-30 | 220 | 30 | 09 | 30 | 220 | 30 | 10 | 30 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C508 | 6F-K17 |  |  | A3-23-7 | B3-23-7 | U-A3-32 / 2P 30A | U-B3-32 / 2P 30A | 6-DaHall 1-PDU-09-30-32 | 6-DaHall 1-PDU-10-30-32 | 220 | 30 | 09 | 32 | 220 | 30 | 10 | 32 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C509 | 6F-K18 |  |  | A3-23-8 | B3-23-8 | U-A3-34 / 2P 30A | U-B3-34 / 2P 30A | 6-DaHall 1-PDU-09-30-34 | 6-DaHall 1-PDU-10-30-34 | 220 | 30 | 09 | 34 | 220 | 30 | 10 | 34 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
C510 | 6F-K19 |  |  | A3-23-9 | B3-23-9 | U-A3-36 / 2P 30A | U-B3-36 / 2P 30A | 6-DaHall 1-PDU-09-30-36 | 6-DaHall 1-PDU-10-30-36 | 220 | 30 | 09 | 36 | 220 | 30 | 10 | 36 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 6F-AF11 |  |  | A1-1-9 | B1-1-9 | U-A1-17 / 2P 30A | U-B1-17 / 2P 30A | 6-DaHall 1-PDU-01-30-17 | 6-DaHall 1-PDU-02-30-17 | 220 | 30 | 01 | 17 | 220 | 30 | 02 | 17 | U-A1 4P 200A | U-B1 4P 200A | UPS 출력배전반(A) #04, 4P 200A | UPS 출력배전반(B) #02, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | [5 empty] | 0 | 0 |  | 랙 배제결정('22.01.11) 차단기는 off 후 미사용 표기로 변경할 것 | 0 | 0 | 무부하 랙
| 6F-AF12 |  |  | A1-1-8 | B1-1-8 | U-A1-15 / 2P 30A | U-B1-15 / 2P 30A | 6-DaHall 1-PDU-01-30-15 | 6-DaHall 1-PDU-02-30-15 | 220 | 30 | 01 | 15 | 220 | 30 | 02 | 15 | [11 empty] | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 6F-AF13 |  |  | A1-1-7 | B1-1-7 | U-A1-13 / 2P 30A | U-B1-13 / 2P 30A | 6-DaHall 1-PDU-01-30-13 | 6-DaHall 1-PDU-02-30-13 | 220 | 30 | 01 | 13 | 220 | 30 | 02 | 13 | [11 empty] | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 6F-AF14 |  |  | A1-1-6 | B1-1-6 | U-A1-11 / 2P 30A | U-B1-11 / 2P 30A | 6-DaHall 1-PDU-01-30-11 | 6-DaHall 1-PDU-02-30-11 | 220 | 30 | 01 | 11 | 220 | 30 | 02 | 11 | [11 empty] | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 6F-AF15 |  |  | A1-1-5 | B1-1-5 | U-A1-09 / 2P 30A | U-B1-09 / 2P 30A | 6-DaHall 1-PDU-01-30-9 | 6-DaHall 1-PDU-02-30-9 | 220 | 30 | 01 | 9 | 220 | 30 | 02 | 9 | [11 empty] | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 6F-AF16 |  |  | A1-1-4 | B1-1-4 | U-A1-07 / 2P 30A | U-B1-07 / 2P 30A | 6-DaHall 1-PDU-01-30-7 | 6-DaHall 1-PDU-02-30-7 | 220 | 30 | 01 | 7 | 220 | 30 | 02 | 7 | [11 empty] | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 6F-AF17 | [6 empty] | 6-DaHall 1-PDU--30- | 6-DaHall 1-PDU--30- | 220 | 30 |  |  | 220 | 30 | [10 empty] | 0 |  |  | #N/A | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
| 6F-AF18 | [6 empty] | 6-DaHall 1-PDU--30- | 6-DaHall 1-PDU--30- | 220 | 30 |  |  | 220 | 30 | [10 empty] | 0 |  |  | #N/A | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
| 6F-AF19 | [6 empty] | 6-DaHall 1-PDU--30- | 6-DaHall 1-PDU--30- | 220 | 30 |  |  | 220 | 30 | [10 empty] | 0 |  |  | #N/A | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
G1101 | 6F-AG10 | 피플펀드 | 2.2 | A1-35-1 | B1-35-1 | U-A1-02 / 2P 30A | U-B1-02 / 2P 30A | 6-DaHall 1-PDU-01-30-2 | 6-DaHall 1-PDU-02-30-2 | 220 | 30 | 01 | 2 | 220 | 30 | 02 | 2 | U-A1 4P 200A | U-B1 4P 200A | UPS 출력배전반(A) #04, 4P 200A | UPS 출력배전반(B) #02, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 1.9684 | 1.4818 | 3.4502 | 245.9 | 174.5 | 0.582 | 420.4 | 22/09/19 투입(임대장비 설정으로 선투입요청) |  | 0.56505 | 1.6349 | 적정함
G1102 | 6F-AG11 | 피플펀드 | 4 | A1-35-1(2) | B1-35-1(2) | U-A1-36 / 2P 30A | U-B1-36 / 2P 30A | 6-DaHall 1-PDU-01-30-36 | 6-DaHall 1-PDU-02-30-36 | 220 | 30 | 01 | 36 | 220 | 30 | 02 | 36 | [6 empty] | 0.95324 | 1.393 | 2.3462 | 134.8 | 174.6 | 1.404 | 309.4 | 22/09/23 투입 |  | 0.41586 | 3.5841 | 적정함
|  |  |  | A1-35-2(2) | B1-35-2(2) | U-A1-38 / 2P 30A | U-B1-38 / 2P 30A | 6-DaHall 1-PDU-01-30-38 | 6-DaHall 1-PDU-02-30-38 | 220 | 30 | 01 | 38 | 220 | 30 | 02 | 38 | [6 empty] | 0 | 0 |  | 0 | 0 | 0 |  | B전원 : 도어락&CCTV 전원 포함 |  | 0 | 0 | 무부하 랙
G1103 | 6F-AG12 | 피플펀드 | 4 | A1-35-2 | B1-35-2 | U-A1-04 / 2P 30A | U-B1-04 / 2P 30A | 6-DaHall 1-PDU-01-30-4 | 6-DaHall 1-PDU-02-30-4 | 220 | 30 | 01 | 4 | 220 | 30 | 02 | 4 | [6 empty] | 3.5632 | 2.5643 | 6.1275 | 561.1 | 418.2 | 3.406 | 979.3 | 22/09/23 투입 |  | 1.3163 | 2.6837 | 적정함
G2101 | 6F-AG13 | 삼성물산(주)패션부문 | 2.2 | A1-35-3 | B1-35-3 | U-A1-06 / 2P 30A | U-B1-06 / 2P 30A | 6-DaHall 1-PDU-01-30-6 | 6-DaHall 1-PDU-02-30-6 | 220 | 30 | 01 | 6 | 220 | 30 | 02 | 6 | U-A1 4P 200A | U-B1 4P 200A | UPS 출력배전반(A) #04, 4P 200A | UPS 출력배전반(B) #02, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 3.0188 | 5.0794 | 8.0982 | 421.3 | 748.6 | 1.664 | 1169.9 |  |  | 1.5724 | 0.62755 | 적정함
G2102 | 6F-AG14 | 삼성물산(주)패션부문 | 2.2 | A1-35-4 | B1-35-4 | U-A1-08 / 2P 30A | U-B1-08 / 2P 30A | 6-DaHall 1-PDU-01-30-8 | 6-DaHall 1-PDU-02-30-8 | 220 | 30 | 01 | 8 | 220 | 30 | 02 | 8 | [6 empty] | 4.8658 | 3.3518 | 8.2176 | 743.1 | 456.2 | 1.662 | 1199.3 |  |  | 1.612 | 0.58804 | 적정함
G2103 | 6F-AG15 | 삼성물산(주)패션부문 | 2.2 | A1-35-5 | B1-35-5 | U-A1-10 / 2P 30A | U-B1-10 / 2P 30A | 6-DaHall 1-PDU-01-30-10 | 6-DaHall 1-PDU-02-30-10 | 220 | 30 | 01 | 10 | 220 | 30 | 02 | 10 | [6 empty] | 7.4314 | 7.1668 | 14.5982 | 1202.2 | 1157.6 | 3.858 | 2359.8 |  |  | 3.1718 | -0.97177 | 사용초과 | 삼성물산(주)패션부문 | G2103
G2104 | 6F-AG16 | 삼성물산(주)패션부문 | 2.2 | A1-35-6 | B1-35-6 | U-A1-12 / 2P 30A | U-B1-12 / 2P 30A | 6-DaHall 1-PDU-01-30-12 | 6-DaHall 1-PDU-02-30-12 | 220 | 30 | 01 | 12 | 220 | 30 | 02 | 12 | [6 empty] | 7.4215 | 9.4983 | 16.9197 | 1209.7 | 1560.8 | 4.132 | 2770.5 |  |  | 3.7238 | -1.5238 | 사용초과 | 삼성물산(주)패션부문 | G2104
G2105 | 6F-AG17 | 삼성물산(주)패션부문 | 2.2 | A1-35-7 | B1-35-7 | U-A1-14 / 2P 30A | U-B1-14 / 2P 30A | 6-DaHall 1-PDU-01-30-14 | 6-DaHall 1-PDU-02-30-14 | 220 | 30 | 01 | 14 | 220 | 30 | 02 | 14 | [6 empty] | 5.4139 | 7.2019 | 12.6157 | 867.3 | 1175.7 | 3.291 | 2043 |  |  | 2.746 | -0.54597 | 사용초과 | 삼성물산(주)패션부문 | G2105
G2106 | 6F-AG18 | 삼성물산(주)패션부문 | 2.2 | A1-35-8 | B1-35-8 | U-A1-16 / 2P 30A | U-B1-16 / 2P 30A | 6-DaHall 1-PDU-01-30-16 | 6-DaHall 1-PDU-02-30-16 | 220 | 30 | 01 | 16 | 220 | 30 | 02 | 16 | [6 empty] | 5.6209 | 5.1897 | 10.8106 | 882.4 | 818 | 2.613 | 1700.4 |  |  | 2.2855 | -0.085484 | 사용초과 | 삼성물산(주)패션부문 | G2106
G2107 | 6F-AG19 | 삼성물산(주)패션부문 | 2.2 | A4-36-1 | B4-36-1 | U-A4-19 / 2P 30A | U-B4-19 / 2P 30A | 6-DaHall 1-PDU-11-30-19 | 6-DaHall 1-PDU-12-30-19 | 220 | 30 | 11 | 19 | 220 | 30 | 12 | 19 | U-A4 4P 200A | U-B4 4P 200A | UPS 출력배전반(A) #01, 4P 200A | UPS 출력배전반(B) #01, 4P 200A |  |  | 5.355 | 5.2948 | 10.6498 | 922.8 | 828.4 | 2.585 | 1751.2 |  |  | 2.3538 | -0.15376 | 사용초과 | 삼성물산(주)패션부문 | G2107
G2108 | 6F-AG20 |  | 2.2 | A4-36-9 | B4-36-9 | U-A4-44 / 2P 30A | U-B4-44 / 2P 30A | 6-DaHall 1-PDU-11-30-44 | 6-DaHall 1-PDU-12-30-44 | 220 | 30 | 11 | 44 | 220 | 30 | 12 | 44 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022/06/09 전기투입 (임시사용 랙) |  | 0 | 2.2 | 무부하 랙
| DE운용실 사무#1 | DEK 사무실 |  | A7-30-8 |  | U6-A7-02 / 2P 30 |  | 6-DaHall 1-PDU-13-30-2 |  | 220 | 30 | 13 | 2 |  |  |  |  | U6-A7 4P 300A |  | LV-6A #07, 3P 320A |  | TR-6A 1000kVA |  | 0 |  | 0 | 0 |  | 0 | 0 | 2022.05.26 차단기 ON |  | 0 | 0 | 무부하 랙
| DE 출입통제Desk |  |  | A7-31-1 |  | U6-A7-04 / 2P 30A |  | 6-DaHall 1-PDU-13-30-4 |  | 220 | 30 | 13 | 4 | [10 empty] | 0 |  | 0 | 0 |  | 0 | 0 | 2022.05.26 차단기 ON |  | 0 | 0 | 무부하 랙
| DE운용실 감시모니터 |  |  |  | B7-30-8 |  | U6-B7-02 / 2P 30 |  | 6-DaHall 1-PDU-14-30-2 |  |  |  |  | 220 | 30 | 14 | 2 |  | U6-B7 4P 300A |  | LV-6B #03, 3P 320A |  | TR-6B 1000kVA |  | 0 | 0 |  | 0 | 0 | 0 | 2022.05.26 차단기 ON |  | 0 | 0 | 무부하 랙
| DE운용실 사무#2 |  |  |  | B7-31-1 |  | U6-B7-04 / 2P 30 |  | 6-DaHall 1-PDU-14-30-4 |  |  |  |  | 220 | 30 | 14 | 4 | [7 empty] | 0 | 0 |  | 0 | 0 | 0 | 2022.05.26 차단기 ON |  | 0 | 0 | 무부하 랙
| 6층 사무실 |  |  |  | B7-32-1 |  | U6-B7-20 / 2P 30A |  | 6-DaHall 1-PDU-14-30-20 |  |  |  |  | 220 | 30 | 14 | 20 |  | U6-B7 4P 300A |  | LV-6B #03, 3P 320A |  | TR-6B 1000kVA |  | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 6층 인터넷장비 |  |  | A7-28-9 |  | U6-A7-40 / 2P 30A |  | 6-DaHall 1-PDU-13-30-40 |  | 220 | 30 | 13 | 40 |  |  |  |  | U6-A7 4P 300A |  | LV-6A #07, 3P 320A |  | TR-6A 1000kVA |  | 0 |  | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| FMS 6층 전원 |  |  |  |  | U-A1-50 / 2P 30A |  | 6-DaHall 1-PDU-01-30-50 |  | 220 | 30 | 01 | 50 |  |  |  |  | U-A1 4P 200A |  | UPS 출력배전반(A) #04, 4P 200A |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 신규 BMS(6F TPS실) Rack |  | 2.2 |  |  |  |  | 6-DaHall 1-PDU-01-30-46 |  | 220 | 30 | 01 | 46 |  |  |  |  | U-A1 4P 200A |  | UPS 출력배전반(A) #04, 4P 200A |  |  |  | 0.55708 |  | 0.55708 | 77.5 |  | 0.129 | 77.5 |  |  | 0.10417 | 2.0958 | 적정함
[26 empty] | 357.8141 | 28.8145
오차

## 5층_랙별_계통 및_부하량
| 5층 랙별 전기공급계통 | [47 empty] | 미디어꾼 | 계약용량 | 시간당 전력량 | 남은 전력량 | 전력초과여부 | 피크값 | 평균값 | 0
[50 empty] | 0 | 0 | 0 | 미사용 랙 | 0 | #DIV/0!
DEKR No. | 랙 No. | 고객명 | 계약용량 | 리셉터클 Name |  | 차단기 정보 |  | DEK Naming Convention 적용 명칭(NEW) |  | 차단기 정보(수정) | [7 empty] | 분전반 정보 |  | 배전반 정보 |  | TR 정보 |  | 월 평균 전류 |  |  | 월 유효전력량 |  | kW(전월최대유효전력) | 월간 사용전력량[kWh] | 비 고 |  | 시간당 전력량 | 남은 전력량 | 전력초과여부 | 사용초과 고객 수 |  | 적정함 | 무부하 랙 |  | 열 구분 (부스바명) | DEKR No. | 고객명 | 계약용량 | DEK Naming Convention 적용 명칭(NEW) |  | 월 평균 전류 |  |  | 월 유효전력량 |  | kW(전월최대유효전력) | 월간 사용전력량[kWh] | 비 고
|  |  | kW | A | B | A | B | A | B | A |  |  |  | B |  |  |  | A | B | A | B | A | B | A | B | 합계 | A | B | [7 empty] | 64 |  | 80 | 167 |  |  |  |  | kW | 상 | 하 | 상 | 하 | 합계 | 상 | 하
A501 | 5F-A10 | Digital Edge Korea | 2.2 | 1A-1-1 | 1B-1-1 | PDU(A)-1-03 / 3P 30A | PDU(B)-1-03 / 3P 30A | 5-DaHall 1-PDU-11-30-3 | 5-DaHall 1-PDU-12-30-3 | 220 | 30 | 11 | 3 | 220 | 30 | 12 | 3 | PDU(A)-1 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #03 3P 150A | UPS출력 배전반(B), #03 3P 150A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 2.2 | 무부하 랙 | [5 empty] | 찾을 수 없음 |  |  |  | 찾을 수 없음 |  | 찾을 수 없음
A502 | 5F-A11 |  |  | 1A-1-2 | 1B-1-2 | PDU(A)-1-05 / 3P 30A | PDU(B)-1-05 / 3P 30A | 5-DaHall 1-PDU-11-30-5 | 5-DaHall 1-PDU-12-30-5 | 220 | 30 | 11 | 5 | 220 | 30 | 12 | 5 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A503 | 5F-A12 | PCCW Global Korea Limited | 2.2 | 1A-1-3 | 1B-1-3 | PDU(A)-1-09 / 3P 30A | PDU(B)-1-26 / 3P 20A | 5-DaHall 1-PDU-11-30-9 | 5-DaHall 1-PDU-12-20-26 | 220 | 30 | 11 | 9 | 220 | 20 | 12 | 26 | [6 empty] | 5.2395 | 5.0065 | 22.2215 | 829.4 | 796.9 | 2.225 | 3540.1 |  |  | 4.7582 | -2.5582 | 사용초과 | PCCW Global Korea Limited | A503
|  |  |  | A1-1-3(2) | B1-1-3(2) | PDU(A)-1-26 / 3P 20A | PDU(B)-1-30 / 3P 20A | 5-DaHall 1-PDU-11-20-26 | 5-DaHall 1-PDU-12-20-30 | 220 | 20 | 11 | 26 | 220 | 20 | 12 | 30 | [6 empty] | 5.4676 | 6.5079 |  | 872.1 | 1041.7 | 2.608 |  |  |  | 0 | 0 | 무부하 랙
A504 | 5F-A13 | PCCW Global Korea Limited | 2.2 | 1A-1-4 | 1B-1-4 | PDU(A)-1-11 / 3P 30A | PDU(B)-1-09 / 3P 30A | 5-DaHall 1-PDU-11-30-11 | 5-DaHall 1-PDU-12-30-9 | 220 | 30 | 11 | 11 | 220 | 30 | 12 | 9 | [6 empty] | 0 | 2.9366 | 4.8931 | 0 | 457.4 | 0.626 | 761.9 |  |  | 1.0241 | 1.1759 | 적정함
|  |  |  | 1A-1-4(2) | 1B-1-4(2) | PDU(A)-1-13 / 3P 30A | PDU(B)-1-11 / 3P 30A | 5-DaHall 1-PDU-11-30-13 | 5-DaHall 1-PDU-12-30-11 | 220 | 30 | 11 | 13 | 220 | 30 | 12 | 11 | [6 empty] | 1.9565 | 0 |  | 304.5 | 0 | 0.431 |  |  |  | 0 | 0 | 무부하 랙
A505 | 5F-A14 | PCCW Global Korea Limited | 2.2 | 9A-1-5 | 9B-1-5 | PDU(A)-9-01 / 3P 30A | PDU(B)-9-07 / 3P 30A | 5-DaHall 1-PDU-07-30-1 | 5-DaHall 1-PDU-08-30-7 | 220 | 30 | 07 | 1 | 220 | 30 | 08 | 7 | PDU(A)-9 4P 200A | PDU(B)-9 4P 200A | UPS출력 배전반(A), #09 3P 200A | UPS출력 배전반(B), #09 3P 200A |  |  | 7.8089 | 5.3639 | 13.1728 | 1244.9 | 792.5 | 2.794 | 2037.4 |  |  | 2.7384 | -0.53844 | 사용초과 | PCCW Global Korea Limited | A505
A506 | 5F-A15 | PCCW Global Korea Limited | 2.2 | 9A-1-6 | 9B-1-6 | PDU(A)-9-03 / 3P 30A | PDU(B)-9-03 / 3P 30A | 5-DaHall 1-PDU-07-30-3 | 5-DaHall 1-PDU-08-30-3 | 220 | 30 | 07 | 3 | 220 | 30 | 08 | 3 | [6 empty] | 1.2814 | 1.4019 | 2.6833 | 107.5 | 121.7 | 0.341 | 229.2 |  |  | 0.30806 | 1.8919 | 적정함
A507 | 5F-A16 | PCCW Global Korea Limited | 2.2 | 9A-1-7 | 9B-1-7 | PDU(A)-9-05 / 3P 30A | PDU(B)-9-05 / 3P 30A | 5-DaHall 1-PDU-07-30-5 | 5-DaHall 1-PDU-08-30-5 | 220 | 30 | 07 | 5 | 220 | 30 | 08 | 5 | [6 empty] | 0.4 | 0 | 0.4 | 56.7 | 0 | 0.082 | 56.7 |  |  | 0.07621 | 2.1238 | 적정함
A508 | 5F-A17 | Lumen Technologies Korea | 2.2 | 9A-1-8 | 9B-1-8 | PDU(A)-9-02 / 3P 30A | PDU(B)-9-02 / 3P 30A | 5-DaHall 1-PDU-07-30-2 | 5-DaHall 1-PDU-08-30-2 | 220 | 30 | 07 | 2 | 220 | 30 | 08 | 2 | [6 empty] | 1.0019 | 1.1675 | 13.4083 | 109.8 | 151.2 | 0.392 | 2057.4 |  |  | 2.7653 | -0.56532 | 사용초과 | Lumen Technologies Korea | A508
|  |  |  | A1-1-8(2) | B1-1-8(2) | PDU(A)-1-28 / 3P 20A | PDU(B)-1-28 / 3P 20A | 5-DaHall 1-PDU-11-20-28 | 5-DaHall 1-PDU-12-20-28 | 220 | 20 | 11 | 28 | 220 | 20 | 12 | 28 | PDU(A)-1 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #03 3P 150A | UPS출력 배전반(B), #03 3P 150A |  |  | 5.4329 | 5.806 |  | 869.8 | 926.6 | 2.506 | 2057.4 |  |  | 2.7653 | -2.7653 | 사용초과 | 0 | 0
A509 | 5F-A18 |  |  | 9A-1-9 | 9B-1-9 | PDU(A)-9-04 / 3P 30A | PDU(B)-9-04 / 3P 30A | 5-DaHall 1-PDU-07-30-4 | 5-DaHall 1-PDU-08-30-4 | 220 | 30 | 07 | 4 | 220 | 30 | 08 | 4 | PDU(A)-9 4P 200A | PDU(B)-9 4P 200A | UPS출력 배전반(A), #09 3P 200A | UPS출력 배전반(B), #09 3P 200A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A510 | 5F-A19 | Digital Edge Korea | 2.2 | 9A-1-10 | 9B-1-10 | PDU(A)-9-06 / 3P 30A | PDU(B)-9-06 / 3P 30A | 5-DaHall 1-PDU-07-30-6 | 5-DaHall 1-PDU-08-30-6 | 220 | 30 | 07 | 6 | 220 | 30 | 08 | 6 | [6 empty] | 0.37117 | 1.35 | 1.7212 | 57.3 | 183.7 | 0.337 | 241 |  |  | 0.32392 | 1.8761 | 적정함
A601 | 5F-B10 | Digital Edge Korea | 2.2 | A1-2-1 | B1-2-1 | PDU(A)-1-15 / 3P 20A | PDU(B)-1-13 / 3P 20A | 5-DaHall 1-PDU-11-20-15 | 5-DaHall 1-PDU-12-20-13 | 220 | 20 | 11 | 15 | 220 | 20 | 12 | 13 | PDU(A)-1 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #03 3P 150A | UPS출력 배전반(B), #03 3P 150A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 국제연동망 테스트 |  | 0 | 2.2 | 무부하 랙
A602 | 5F-B11 |  |  | A1-2-2 | B1-2-2 | PDU(A)-1-17 / 3P 20A | PDU(B)-1-15 / 3P 20A | 5-DaHall 1-PDU-11-20-17 | 5-DaHall 1-PDU-12-20-15 | 220 | 20 | 11 | 17 | 220 | 20 | 12 | 15 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A603 |  | Sejong Telecom Inc. | 3 |  |  |  |  | 5-DaHall 1-PDU-15-30-11 | 5-DaHall 1-PDU-16-30-11 | 220 | 30 | 15 | 11 | 220 | 30 | 16 | 11 | PDU(A)-3 4P 300A | PDU(B)-3 4P 300A | UPS출력 배전반(A), #01 3P 300A | UPS출력 배전반(B), #01 3P 300A |  |  | 0 | 0 | 3.3056 | 0 | 0 | 0 | 382.9 | 23/08/23 차단기 투입 |  | 0.51465 | 2.4853 | 적정함
[8 empty] | 5-DaHall 1-PDU-15-30-14 | 5-DaHall 1-PDU-16-30-14 | 220 | 30 | 15 | 14 | 220 | 30 | 16 | 14 | [6 empty] | 1.5793 | 1.7262 |  | 177 | 205.9 | 0.539 |  |  |  | 0 | 0 | 무부하 랙
| 5F-B12 |  |  | A1-2-3 | B1-2-3 | PDU(A)-1-19 / 3P 20A | PDU(B)-1-17 / 3P 20A | 5-DaHall 1-PDU-11-20-19 | 5-DaHall 1-PDU-12-20-17 | 220 | 20 | 11 | 19 | 220 | 20 | 12 | 17 | PDU(A)-1 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #03 3P 150A | UPS출력 배전반(B), #03 3P 150A |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 무부하 랙
A604 | 5F-B13 | Dakos Co., Ltd. | 2.2 | A1-2-4 | B1-2-4 | PDU(A)-1-21 / 3P 20A | PDU(B)-1-19 / 3P 20A | 5-DaHall 1-PDU-11-20-21 | 5-DaHall 1-PDU-12-20-19 | 220 | 20 | 11 | 21 | 220 | 20 | 12 | 19 | [6 empty] | 2.554 | 2.9717 | 5.5257 | 362.1 | 392.6 | 1.108 | 754.7 |  |  | 1.0144 | 1.1856 | 적정함
A605 | 5F-B14 | Ebiz Networks | 2.2 | A1-2-5 | B1-2-5 | PDU(A)-1-23 / 3P 20A | PDU(B)-1-21 / 3P 20A | 5-DaHall 1-PDU-11-20-23 | 5-DaHall 1-PDU-12-20-21 | 220 | 20 | 11 | 23 | 220 | 20 | 12 | 21 | [6 empty] | 4.9109 | 4.5562 | 9.4671 | 765.3 | 690.3 | 2.318 | 1455.6 | 22/09/23, 06시 전기투입 |  | 1.9565 | 0.24355 | 적정함
A606 | 5F-B15 | NTT KOREA Co., Ltd. | 1.1 | A1-2-6 | B1-2-6 | PDU(A)-1-25 / 3P 20A | PDU(B)-1-23 / 3P 20A | 5-DaHall 1-PDU-11-20-25 | 5-DaHall 1-PDU-12-20-23 | 220 | 20 | 11 | 25 | 220 | 20 | 12 | 23 | [6 empty] | 0 | 0 | 1.0049 | 0 | 0 | 0 | 99.7 |  |  | 0.13401 | 0.96599 | 적정함
|  |  |  | A3-2-6(2) | B3-2-6(2) | PDU(A)-3-28 / 3P 20A | PDU(B)-3-28 / 3P 20A | 5-DaHall 1-PDU-15-20-28 | 5-DaHall 1-PDU-16-20-28 | 220 | 20 | 15 | 28 | 220 | 20 | 16 | 28 | PDU(A)-3 4P 300A | PDU(B)-3 4P 300A | UPS출력 배전반(A), #01 3P 300A | UPS출력 배전반(B), #01 3P 300A |  |  | 0.71001 | 0.29488 |  | 78.2 | 21.5 | 0.151 | 99.7 |  |  | 0.13401 | -0.13401 | 사용초과 | 0 | 0
A607 | 5F-B16 | Zeus Networks Co., Ltd. | 1.1 | A1-2-7 | B1-2-7 | PDU(A)-1-27 / 3P 20A | PDU(B)-1-25 / 3P 20A | 5-DaHall 1-PDU-11-20-27 | 5-DaHall 1-PDU-12-20-25 | 220 | 20 | 11 | 27 | 220 | 20 | 12 | 25 | PDU(A)-1 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #03 3P 150A | UPS출력 배전반(B), #03 3P 150A |  |  | 2.6574 | 3.4098 | 6.0672 | 417.3 | 532 | 1.374 | 949.3 |  |  | 1.2759 | -0.17594 | 사용초과 | Zeus Networks Co., Ltd. | A607
A608 | 5F-B17 | Sejong Telecom Inc. | 2.2 | A1-2-8 | B1-2-8 | PDU(A)-1-29 / 3P 20A | PDU(B)-1-27 / 3P 20A | 5-DaHall 1-PDU-11-20-29 | 5-DaHall 1-PDU-12-20-27 | 220 | 20 | 11 | 29 | 220 | 20 | 12 | 27 | [6 empty] | 0 | 0 | 11.3655 | 0 | 0 | 0 | 1631.2 | 미사용 |  | 2.1925 | 0.0075269 | 적정함
|  |  |  | PDU(A)-3-07 | PDU(B)-3-07 | PDU(A)-3-07 / 3P 30A | PDU(B)-3-07 / 3P 30A | 5-DaHall 1-PDU-15-30-7 | 5-DaHall 1-PDU-16-30-7 | 220 | 30 | 15 | 7 | 220 | 30 | 16 | 7 | DU(A)-3 4P 300A | PDU(B)-3 4P 300A | UPS출력 배전반(A), #01 3P 300A | UPS출력 배전반(B), #01 3P 300A |  |  | 3.7956 | 4.01 |  | 579.5 | 619.8 | 1.649 | 1631.2 | '21/10/29 신규구성 |  | 2.1925 | -2.1925 | 사용초과 | 0 | 0
|  |  |  | PDU(A)-3-09 | PDU(B)-3-09 | PDU(A)-3-09 / 3P 30A | PDU(B)-3-09 / 3P 30A | 5-DaHall 1-PDU-15-30-9 | 5-DaHall 1-PDU-16-30-9 | 220 | 30 | 15 | 9 | 220 | 30 | 16 | 9 | [6 empty] | 1.7567 | 1.8033 |  | 210.9 | 221 | 0.604 | 1631.2 |  |  | 2.1925 | -2.1925 | 사용초과 | 0 | 0
A609 | 5F-B18 | 한비로 | 2.2 | A2-2-9 | B1-2-9 | PDU(A)-2-03 / 3P 30A | PDU(B)-1-32 / 3P 20A | 5-DaHall 1-PDU-13-30-3 | 5-DaHall 1-PDU-12-20-32 | 220 | 30 | 13 | 3 | 220 | 20 | 12 | 32 | PDU(A)-2 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #04 3P 150A | UPS출력 배전반(B), #03 3P 150A |  |  | 5.6571 | 3.0076 | 8.6647 | 894.9 | 451.6 | 2.051 | 1346.5 |  |  | 1.8098 | 0.39019 | 적정함
A610 | 5F-B19 | PCCW Global Korea Limited | 2.2 | A2-2-10 | B2-2-10 | PDU(A)-2-05 / 3P 30A | PDU(B)-2-03 / 3P 30A | 5-DaHall 1-PDU-13-30-5 | 5-DaHall 1-PDU-14-30-3 | 220 | 30 | 13 | 5 | 220 | 30 | 14 | 3 |  | PDU(B)-2 4P 150A |  | UPS출력 배전반(B), #04 3P 150A |  |  | 3.9416 | 3.2547 | 7.1963 | 587.6 | 472.4 | 1.937 | 1060 |  |  | 1.4247 | 0.77527 | 적정함
A702 | [28 empty] | 0 |  | 랙 미설치 |  | 0 | 0 | 무부하 랙
A703 | 5F-C12 | Sejong Telecom Inc. | 2.2 | A1-3-3 | B1-3-3 | PDU(A)-1-06 / 3P 30A | PDU(B)-1-04 / 3P 30A | 5-DaHall 1-PDU-11-30-6 | 5-DaHall 1-PDU-12-30-4 | 220 | 30 | 11 | 6 | 220 | 30 | 12 | 4 | PDU(A)-1 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #03 3P 150A | UPS출력 배전반(B), #03 3P 150A | TR-5A 1000KVA | TR-5B 1000KVA | 2.0275 | 1.9205 | 3.9479 | 283 | 251.5 | 0.755 | 534.5 | 21/11/30 전기투입 |  | 0.71841 | 1.4816 | 적정함
A704 | 5F-C13 | Sejong Telecom Inc. | 2.2 | A1-3-4 | B1-3-4 | PDU(A)-1-08 / 3P 20A | PDU(B)-1-06 / 3P 30A | 5-DaHall 1-PDU-11-20-8 | 5-DaHall 1-PDU-12-30-6 | 220 | 20 | 11 | 8 | 220 | 30 | 12 | 6 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | QDF 전기 미사용 |  | 0 | 2.2 | 무부하 랙
A705 | 5F-C14 |  |  | A1-3-5 | B1-3-5 | PDU(A)-1-10 / 3P 20A | PDU(B)-1-08 / 3P 30A | 5-DaHall 1-PDU-11-20-10 | 5-DaHall 1-PDU-12-30-8 | 220 | 20 | 11 | 10 | 220 | 30 | 12 | 8 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A706 | 5F-C15 | DEK, 층간 Patch Cabinet |  | A1-3-6 | B1-3-6 | PDU(A)-1-12 / 3P 20A | PDU(B)-1-10 / 3P 20A | 5-DaHall 1-PDU-11-20-12 | 5-DaHall 1-PDU-12-20-10 | 220 | 20 | 11 | 12 | 220 | 20 | 12 | 10 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A707 | 5F-C16 |  |  | A1-3-7 | B1-3-7 | PDU(A)-1-14 / 3P 20A | PDU(B)-1-12 / 3P 20A | 5-DaHall 1-PDU-11-20-14 | 5-DaHall 1-PDU-12-20-12 | 220 | 20 | 11 | 14 | 220 | 20 | 12 | 12 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A708 | 5F-C17 | CHANEL KOREA | 2.2 | A1-3-8 | B1-3-8 | PDU(A)-1-16 / 3P 20A | PDU(B)-1-14 / 3P 20A | 5-DaHall 1-PDU-11-20-16 | 5-DaHall 1-PDU-12-20-14 | 220 | 20 | 11 | 16 | 220 | 20 | 12 | 14 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 2.2 | 무부하 랙
A709 | 5F-C18 | CHANEL KOREA | 2.2 | A1-3-9 | B1-3-9 | PDU(A)-1-18 / 3P 20A | PDU(B)-1-16 / 3P 20A | 5-DaHall 1-PDU-11-20-18 | 5-DaHall 1-PDU-12-20-16 | 220 | 20 | 11 | 18 | 220 | 20 | 12 | 16 | [6 empty] | 3.0799 | 6.1695 | 9.2494 | 436.8 | 965.9 | 2.145 | 1402.7 |  |  | 1.8853 | 0.31465 | 적정함
A710 | 5F-C19 | CHANEL KOREA | 2.2 | A1-3-10 | B1-3-10 | PDU(A)-1-20 / 3P 20A | PDU(B)-1-18 / 3P 20A | 5-DaHall 1-PDU-11-20-20 | 5-DaHall 1-PDU-12-20-18 | 220 | 20 | 11 | 20 | 220 | 20 | 12 | 18 | [6 empty] | 2.9135 | 3.6126 | 6.5261 | 302.3 | 504.3 | 1.145 | 806.6 |  |  | 1.0841 | 1.1159 | 적정함
| 5F-D12 |  |  | A2-4-3 | B2-4-3 | PDU(A)-2-11 / 3P 20A | PDU(B)-2-09 / 3P 30A | 5-DaHall 1-PDU-13-20-11 | 5-DaHall 1-PDU-14-30-9 | 220 | 20 | 13 | 11 | 220 | 30 | 14 | 9 | PDU(A)-2 4P 150A | PDU(B)-2 4P 150A | UPS출력 배전반(A), #04 3P 150A | UPS출력 배전반(B), #04 3P 150A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A804 | 5F-D13 | Digital Edge Korea | 2.2 | A2-4-4 | B2-4-4 | PDU(A)-2-13 / 3P 20A | PDU(B)-2-11 / 3P 20A | 5-DaHall 1-PDU-13-20-13 | 5-DaHall 1-PDU-14-20-11 | 220 | 20 | 13 | 13 | 220 | 20 | 14 | 11 | [6 empty] | 0.70734 | 0 | 0.70734 | 70.6 | 0 | 0.108 | 70.6 |  |  | 0.094892 | 2.1051 | 적정함
A805 | 5F-D14 | PCCW Global Korea Limited | 3.3 | A2-4-5 | B2-4-5 | PDU(A)-2-15 / 3P 20A | PDU(B)-2-13 / 3P 20A | 5-DaHall 1-PDU-13-20-15 | 5-DaHall 1-PDU-14-20-13 | 220 | 20 | 13 | 15 | 220 | 20 | 14 | 13 | [6 empty] | 0 | 1.7295 | 1.7295 | 0 | 242.6 | 0.353 | 242.6 |  |  | 0.32608 | 2.9739 | 적정함
A806 | 5F-D15 | Sejong Telecom Inc. | 3 | A2-4-6 | B2-4-6 | PDU(A)-2-17 / 3P 20A | PDU(B)-2-15 / 3P 20A | 5-DaHall 1-PDU-13-20-17 | 5-DaHall 1-PDU-14-20-15 | 220 | 20 | 13 | 17 | 220 | 20 | 14 | 15 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 620.4 | 랙 미설치 |  | 0.83387 | 2.1661 | 적정함
|  |  |  | PDU(A)-3-A-12 | PDU(B)-3-B-12 | PDU(A)-3-A-12 / 3P 30A | PDU(B)-3-B-12 / 3P 30A | 5-DaHall 1-PDU-15-30-12 | 5-DaHall 1-PDU-16-30-12 | 220 | 30 | 15 | 12 | 220 | 30 | 16 | 12 | PDU(A)-3 4P 300A | PDU(B)-3 4P 300A | UPS출력 배전반(A), #01 3P 300A | UPS출력 배전반(B), #01 3P 300A |  |  | 2.312 | 2.5684 | 4.8804 | 303.4 | 317 | 0.856 | 620.4 | '21.09.29 전기투입 |  | 0.83387 | -0.83387 | 사용초과 | 0 | 0
A807 | 5F-D16 | Sejong Telecom Inc. | 2.2 | A2-4-7 | B2-4-7 | PDU(A)-2-19 / 3P 20A | PDU(B)-2-17 / 3P 20A | 5-DaHall 1-PDU-13-20-19 | 5-DaHall 1-PDU-14-20-17 | 220 | 20 | 13 | 19 | 220 | 20 | 14 | 17 | PDU(A)-2 4P 150A | PDU(B)-2 4P 150A | UPS출력 배전반(A), #04 3P 150A | UPS출력 배전반(B), #04 3P 150A |  |  | 5.2271 | 0.96051 | 6.1876 | 847.8 | 120.7 | 1.382 | 968.5 | 랙 미설치 |  | 1.3017 | 0.89825 | 적정함
|  |  |  | A1-4-7(2) | B1-4-7(2) | PDU(A)-1-22 / 3P 20A | PDU(B)-1-22 / 3P 20A | 5-DaHall 1-PDU-11-20-22 | 5-DaHall 1-PDU-12-20-22 | 220 | 20 | 11 | 22 | 220 | 20 | 12 | 22 | PDU(A)-1 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #03 3P 150A | UPS출력 배전반(B), #03 3P 150A |  |  | 0 | 0 |  | 0 | 0 | 0 | 968.5 |  |  | 1.3017 | -1.3017 | 사용초과 | 0 | 0
A808 | 5F-D17 | Sejong Telecom Inc. | 2.2 | A2-4-8 | B2-4-8 | PDU(A)-2-21 / 3P 20A | PDU(B)-2-19 / 3P 20A | 5-DaHall 1-PDU-13-20-21 | 5-DaHall 1-PDU-14-20-19 | 220 | 20 | 13 | 21 | 220 | 20 | 14 | 19 | PDU(A)-2 4P 150A | PDU(B)-2 4P 150A | UPS출력 배전반(A), #04 3P 150A | UPS출력 배전반(B), #04 3P 150A |  |  | 3.2932 | 2.5462 | 5.8395 | 454.7 | 388.2 | 1.267 | 842.9 |  |  | 1.1329 | 1.0671 | 적정함
A809 | 5F-D18 | 한국보안기술 | 3.3 | A2-4-9 | B2-4-9 | PDU(A)-2-23 / 3P 20A | PDU(B)-2-21 / 3P 20A | 5-DaHall 1-PDU-13-20-23 | 5-DaHall 1-PDU-14-20-21 | 220 | 20 | 13 | 23 | 220 | 20 | 14 | 21 | [6 empty] | 9.0422 | 3.403 | 12.4453 | 1473.3 | 558 | 2.987 | 2031.3 |  |  | 2.7302 | 0.56976 | 적정함
|  |  |  | - |  | PDU(A)-1-30 / 3P 20A |  | 5-DaHall 1-PDU-11-20-30 |  | 220 | 20 | 11 | 30 |  |  |  |  | PDU(A)-1 4P 150A |  | UPS출력 배전반(A), #03 3P 150A |  |  |  | 0 |  |  | 0 |  | 0 | 2031.3 | 임시 |  | 2.7302 | -2.7302 | 사용초과 | 0 | 0
A810 | 5F-D19 | 한국보안기술 | 3.3 | A2-4-10 | B2-4-10 | PDU(A)-2-25 / 3P 20A | PDU(B)-2-23 / 3P 20A | 5-DaHall 1-PDU-13-20-25 | 5-DaHall 1-PDU-14-20-23 | 220 | 20 | 13 | 25 | 220 | 20 | 14 | 23 | PDU(A)-2 4P 150A | PDU(B)-2 4P 150A | UPS출력 배전반(A), #04 3P 150A | UPS출력 배전반(B), #04 3P 150A |  | TR-5B 1000KVA | 2.4993 | 2.5495 | 5.0487 | 383.5 | 404.1 | 1.093 | 787.6 |  |  | 1.0586 | 2.2414 | 적정함
| 5F-E12 |  |  | A2-5-3 | B2-5-3 | PDU(A)-2-31 / 3P 20A | PDU(B)-2-29 / 3P 20A | 5-DaHall 1-PDU-13-20-31 | 5-DaHall 1-PDU-14-20-29 | 220 | 20 | 13 | 31 | 220 | 20 | 14 | 29 | PDU(A)-2 4P 150A | PDU(B)-2 4P 150A | UPS출력 배전반(A), #04 3P 150A | UPS출력 배전반(B), #04 3P 150A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
| 5F-E13 |  |  | A2-5-4 | B2-5-4 | PDU(A)-2-04 / 3P 30A | PDU(B)-2-31 / 3P 20A | 5-DaHall 1-PDU-13-30-4 | 5-DaHall 1-PDU-14-20-31 | 220 | 30 | 13 | 4 | 220 | 20 | 14 | 31 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A905 | 5F-E14 | Onse Telink | 2.2 | A2-5-5 | B2-5-5 | PDU(A)-2-06 / 3P 30A | PDU(B)-2-04 / 3P 30A | 5-DaHall 1-PDU-13-30-6 | 5-DaHall 1-PDU-14-30-4 | 220 | 30 | 13 | 6 | 220 | 30 | 14 | 4 | [6 empty] | 5.8641 | 7.0524 | 12.9165 | 916.7 | 1086.6 | 2.953 | 2003.3 |  |  | 2.6926 | -0.49261 | 사용초과 | Onse Telink | A905
A906 | 5F-E15 | Onse Telink | 2.2 | A2-5-6 | B2-5-6 | PDU(A)-2-08 / 3P 30A | PDU(B)-2-06 / 3P 30A | 5-DaHall 1-PDU-13-30-8 | 5-DaHall 1-PDU-14-30-6 | 220 | 30 | 13 | 8 | 220 | 30 | 14 | 6 | [6 empty] | 4.2161 | 2.8166 | 7.0327 | 613.3 | 422.2 | 1.54 | 1035.5 |  |  | 1.3918 | 0.8082 | 적정함
A907 | 5F-E16 |  |  | A2-5-7 | B2-5-7 | PDU(A)-2-10 / 3P 30A | PDU(B)-2-08 / 3P 30A | 5-DaHall 1-PDU-13-30-10 | 5-DaHall 1-PDU-14-30-8 | 220 | 30 | 13 | 10 | 220 | 30 | 14 | 8 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A908 | 5F-E17 |  |  | A2-5-8 | B2-5-8 | PDU(A)-2-12 / 3P 20A | PDU(B)-2-10 / 3P 30A | 5-DaHall 1-PDU-13-20-12 | 5-DaHall 1-PDU-14-30-10 | 220 | 20 | 13 | 12 | 220 | 30 | 14 | 10 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A909 | 5F-E18 |  |  | A2-5-9 | B2-5-9 | PDU(A)-2-14 / 3P 20A | PDU(B)-2-12 / 3P 20A | 5-DaHall 1-PDU-13-20-14 | 5-DaHall 1-PDU-14-20-12 | 220 | 20 | 13 | 14 | 220 | 20 | 14 | 12 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
A910 | 5F-E19 | PCCW Global Korea Limited | 2.2 | A2-5-10 | B2-5-10 | PDU(A)-2-16 / 3P 20A | PDU(B)-2-14 / 3P 20A | 5-DaHall 1-PDU-13-20-16 | 5-DaHall 1-PDU-14-20-14 | 220 | 20 | 13 | 16 | 220 | 20 | 14 | 14 | [6 empty] | 3.8811 | 3.2013 | 10.5837 | 632.3 | 519.7 | 1.577 | 1719.8 |  |  | 2.3116 | -0.11156 | 사용초과 | PCCW Global Korea Limited | A910
|  |  |  | A1-5-10(2) | B1-5-10(2) | PDU(A)-1-24 / 3P 20A | PDU(B)-1-24 / 3P 20A | 5-DaHall 1-PDU-11-20-24 | 5-DaHall 1-PDU-12-20-24 | 220 | 20 | 11 | 24 | 220 | 20 | 12 | 24 | PDU(A)-1 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #03 3P 150A | UPS출력 배전반(B), #03 3P 150A |  |  | 0 | 3.5013 |  | 0 | 567.8 | 0.778 | 1719.8 |  |  | 2.3116 | -2.3116 | 사용초과 | 0 | 0
| 5F-F12 |  |  | A2-6-3 | B2-6-3 | PDU(A)-2-22 / 3P 20A | PDU(B)-2-20 / 3P 20A | 5-DaHall 1-PDU-13-20-22 | 5-DaHall 1-PDU-14-20-20 | 220 | 20 | 13 | 22 | 220 | 20 | 14 | 20 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
| 5F-F13 |  |  | A2-6-4 | B2-6-4 | PDU(A)-2-24 / 3P 20A | PDU(B)-2-22 / 3P 20A | 5-DaHall 1-PDU-13-20-24 | 5-DaHall 1-PDU-14-20-22 | 220 | 20 | 13 | 24 | 220 | 20 | 14 | 22 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치 |  | 0 | 0 | 무부하 랙
A1005 | 5F-F14 | Onse Telink | 2.2 | A2-6-5 | B2-6-5 | PDU(A)-2-26 / 3P 20A | PDU(B)-2-24 / 3P 20A | 5-DaHall 1-PDU-13-20-26 | 5-DaHall 1-PDU-14-20-24 | 220 | 20 | 13 | 26 | 220 | 20 | 14 | 24 | [6 empty] | 1.8758 | 5.0704 | 6.9462 | 270.2 | 759.8 | 1.541 | 1030 |  |  | 1.3844 | 0.81559 | 적정함
A1006 | 5F-F15 | ITNEST | 6.6 |  |  |  |  | 5-DaHall 1-PDU-15-30-10 | 5-DaHall 1-PDU-16-30-10 |  | 30 | 15 | 10 |  | 30 | 16 | 10 | [6 empty] | 6.7601 | 0.99968 | 7.7597 | 1102.8 | 26.9 | 1.57 | 1129.7 |  |  | 1.5184 | 5.0816 | 적정함
|  |  |  | A2-6-6 | B2-6-6 | PDU(A)-2-28 / 3P 20A | PDU(B)-2-26 / 3P 20A | 5-DaHall 1-PDU-13-20-28 | 5-DaHall 1-PDU-14-20-26 | 220 | 20 | 13 | 28 | 220 | 20 | 14 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1129.7 | 21/11/30해지 |  | 1.5184 | -1.5184 | 사용초과 | 0 | 0
A1007 | 5F-F16 | Lumen Technology | 6 |  |  |  |  | 5-DaHall 1-PDU-15-30-8 | 5-DaHall 1-PDU-16-30-8 |  | 30 | 15 | 8 |  | 30 | 16 | 8 | [6 empty] | 4.3115 | 4.877 | 9.1885 | 620 | 705.2 | 1.8 | 1325.2 |  |  | 1.7812 | 4.2188 | 적정함
|  |  |  | A2-6-7 | B2-6-7 | PDU(A)-2-30 / 3P 20A | PDU(B)-2-28 / 3P 20A | 5-DaHall 1-PDU-13-20-30 | 5-DaHall 1-PDU-14-20-28 | 220 | 20 | 13 | 30 | 220 | 20 | 14 | 28 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1325.2 |  |  | 1.7812 | -1.7812 | 사용초과 | 0 | 0
A1008 | 5F-F17 | Lumen Technology |  | A2-6-8 | B2-6-8 | PDU(A)-2-32 / 3P 20A | PDU(B)-2-30 / 3P 20A | 5-DaHall 1-PDU-13-20-32 | 5-DaHall 1-PDU-14-20-30 | 220 | 20 | 13 | 32 | 220 | 20 | 14 | 30 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
B116 | R12 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-32 | 5-DaHall 1-PDU-04-30-32 |  | 30 | 03 | 32 |  | 30 | 04 | 32 | [6 empty] | 2.4823 | 0.27073 | 2.753 | 256.8 | 23.1 | #N/A | 279.9 |  |  | 0.37621 | 1.8238 | 적정함
B117 | R11 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-34 | 5-DaHall 1-PDU-04-30-34 |  | 30 | 03 | 34 |  | 30 | 04 | 34 | [6 empty] | 2.2286 | 0.28991 | 2.5186 | 231.2 | 16.1 | #N/A | 247.3 |  |  | 0.33239 | 1.8676 | 적정함
B118 | R10 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-36 | 5-DaHall 1-PDU-04-30-36 |  | 30 | 03 | 36 |  | 30 | 04 | 36 | [6 empty] | 2.1677 | 2.2841 | 4.4518 | 234.1 | 253.9 | #N/A | 488 |  |  | 0.65591 | 1.5441 | 적정함
B119 | R9 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-38 | 5-DaHall 1-PDU-04-30-38 |  | 30 | 03 | 38 |  | 30 | 04 | 38 | [6 empty] | 2.3507 | 2.759 | 5.1097 | 260.8 | 301.3 | #N/A | 562.1 |  |  | 0.75551 | 1.4445 | 적정함
B120 | R8 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-40 | 5-DaHall 1-PDU-04-30-40 |  | 30 | 03 | 40 |  | 30 | 04 | 40 | [6 empty] | 1.366 | 1.4517 | 2.8177 | 171.1 | 186.6 | #N/A | 357.7 |  |  | 0.48078 | 1.7192 | 적정함
B121 | R7 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-42 | 5-DaHall 1-PDU-04-30-42 |  | 30 | 03 | 42 |  | 30 | 04 | 42 | [6 empty] | 1.7853 | 1.582 | 3.3674 | 216.1 | 182.8 | #N/A | 398.9 |  |  | 0.53616 | 1.6638 | 적정함
B122 | R6 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-44 | 5-DaHall 1-PDU-04-30-44 |  | 30 | 03 | 44 |  | 30 | 04 | 44 | [6 empty] | 2.9196 | 2.3193 | 5.2389 | 451.5 | 338.1 | #N/A | 789.6 |  |  | 1.0613 | 1.1387 | 적정함
B216 | R5 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-46 | 5-DaHall 1-PDU-04-30-46 |  | 30 | 03 | 46 |  | 30 | 04 | 46 | [6 empty] | 2.893 | 2.3497 | 5.2427 | 442.2 | 338.2 | #N/A | 780.4 |  |  | 1.0489 | 1.1511 | 적정함
B217 | R4 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-48 | 5-DaHall 1-PDU-04-30-48 |  | 30 | 03 | 48 |  | 30 | 04 | 48 | [6 empty] | 3.6755 | 3.1896 | 6.8651 | 578.6 | 489.7 | #N/A | 1068.3 |  |  | 1.4359 | 0.76411 | 적정함
B218 | R3 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-50 | 5-DaHall 1-PDU-04-30-50 |  | 30 | 03 | 50 |  | 30 | 04 | 50 | [6 empty] | 4.1026 | 3.9358 | 8.0383 | 644.5 | 623.3 | #N/A | 1267.8 |  |  | 1.704 | 0.49597 | 적정함
B219 | R2 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-47 | 5-DaHall 1-PDU-04-30-47 |  | 30 | 03 | 47 |  | 30 | 04 | 47 | [6 empty] | 4.0531 | 4.4097 | 8.4628 | 616.5 | 656.9 | #N/A | 1273.4 |  |  | 1.7116 | 0.48844 | 적정함
B220 | R1 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-49 | 5-DaHall 1-PDU-04-30-49 |  | 30 | 03 | 49 |  | 30 | 04 | 49 | [6 empty] | 5.7896 | 5.5645 | 11.3541 | 917.8 | 878.5 | #N/A | 1796.3 |  |  | 2.4144 | -0.21438 | 사용초과 | KG이니시스 | B220
B221 | R13 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-2 | 5-DaHall 1-PDU-04-30-2 |  | 30 | 03 | 2 |  | 30 | 04 | 2 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 2.2 | 무부하 랙
[8 empty] | 5-DaHall 1-PDU-03-30-4 | 5-DaHall 1-PDU-04-30-4 |  | 30 | 03 | 4 |  | 30 | 04 | 4 | [6 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
[8 empty] | 5-DaHall 1-PDU-03-30-41 | 5-DaHall 1-PDU-04-30-41 |  | 30 | 03 | 41 |  | 30 | 04 | 41 | [6 empty] | 0 | 0 |  | 0 | 0 | #N/A | 0 |  |  | 0 | 0 | 무부하 랙
B222 | R14 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-6 | 5-DaHall 1-PDU-04-30-6 |  | 30 | 03 | 6 |  | 30 | 04 | 6 | [6 empty] | 0.56762 | 0.56844 | 9.2479 | 87.7 | 88.7 | 0 | 1445.1 |  |  | 1.9423 | 0.25766 | 적정함
[8 empty] | 5-DaHall 1-PDU-03-30-8 | 5-DaHall 1-PDU-04-30-8 |  | 30 | 03 | 8 |  | 30 | 04 | 8 | [6 empty] | 1.4476 | 1.7486 |  | 227.4 | 275 | 0 | 1445.1 |  |  | 1.9423 | -1.9423 | 사용초과 | 0 | 0
[8 empty] | 5-DaHall 1-PDU-03-30-43 | 5-DaHall 1-PDU-04-30-43 |  | 30 | 03 | 43 |  | 30 | 04 | 43 | [6 empty] | 2.432 | 2.4836 |  | 377.6 | 388.7 | #N/A | 1445.1 |  |  | 1.9423 | -1.9423 | 사용초과 | 0 | 0
B316 | R15 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-10 | 5-DaHall 1-PDU-04-30-10 |  | 30 | 03 | 10 |  | 30 | 04 | 10 | [6 empty] | 3.56 | 3.5361 | 10.681 | 563.6 | 559.2 | 0 | 1683.8 |  |  | 2.2632 | -0.063172 | 사용초과 | KG이니시스 | B316
[8 empty] | 5-DaHall 1-PDU-03-30-12 | 5-DaHall 1-PDU-04-30-12 |  | 30 | 03 | 12 |  | 30 | 04 | 12 | [6 empty] | 1.7723 | 1.8126 |  | 278 | 283 | 0 | 1683.8 |  |  | 2.2632 | -2.2632 | 사용초과 | 0 | 0
[8 empty] | 5-DaHall 1-PDU-03-30-45 | 5-DaHall 1-PDU-04-30-45 |  | 30 | 03 | 45 |  | 30 | 04 | 45 | [6 empty] | 0 | 0 |  | 0 | 0 | #N/A | 1683.8 |  |  | 2.2632 | -2.2632 | 사용초과 | 0 | 0
B317 | R16 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-14 | 5-DaHall 1-PDU-04-30-14 |  | 30 | 03 | 14 |  | 30 | 04 | 14 | [6 empty] | 0.35264 | 0.65122 | 8.169 | 45.6 | 97.6 | 0 | 1220.6 |  |  | 1.6406 | 0.55941 | 적정함
[8 empty] | 5-DaHall 1-PDU-03-30-37 | 5-DaHall 1-PDU-04-30-37 |  | 30 | 03 | 37 |  | 30 | 04 | 37 | [6 empty] | 3.2319 | 3.9333 |  | 479 | 598.4 | #N/A | 1220.6 |  |  | 1.6406 | -1.6406 | 사용초과 | 0 | 0
B318 | R17 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-16 | 5-DaHall 1-PDU-04-30-16 |  | 30 | 03 | 16 |  | 30 | 04 | 16 | [6 empty] | 3.9112 | 3.8372 | 10.7712 | 632.2 | 621 | 0 | 1675.5 |  |  | 2.252 | -0.052016 | 사용초과 | KG이니시스 | B318
[8 empty] | 5-DaHall 1-PDU-03-30-39 | 5-DaHall 1-PDU-04-30-39 |  | 30 | 03 | 39 |  | 30 | 04 | 39 | [6 empty] | 1.7992 | 1.2236 |  | 265.9 | 156.4 | #N/A | 1675.5 |  |  | 2.252 | -2.252 | 사용초과 | 0 | 0
B319 | R18 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-18 | 5-DaHall 1-PDU-04-30-18 |  | 30 | 03 | 18 |  | 30 | 04 | 18 | [6 empty] | 0.84995 | 0.85023 | 1.7002 | 106.1 | 108 | 0 | 214.1 |  |  | 0.28777 | 1.9122 | 적정함
B320 | R19 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-20 | 5-DaHall 1-PDU-04-30-20 |  | 30 | 03 | 20 |  | 30 | 04 | 20 | [6 empty] | 2.8169 | 1.8217 | 4.6386 | 415.8 | 415.8 | 1.95 | 831.6 |  |  | 1.1177 | 1.0823 | 적정함
B321 | R20 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-22 | 5-DaHall 1-PDU-04-30-22 |  | 30 | 03 | 22 |  | 30 | 04 | 22 | [6 empty] | 2.8763 | 3.0523 | 5.9287 | 392 | 392 | 0 | 784 |  |  | 1.0538 | 1.1462 | 적정함
B322 | R21 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-24 | 5-DaHall 1-PDU-04-30-24 |  | 30 | 03 | 24 |  | 30 | 04 | 24 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 2.2 | 무부하 랙
B416 | R22 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-26 | 5-DaHall 1-PDU-04-30-26 |  | 30 | 03 | 26 |  | 30 | 04 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 2.737 | 0 |  |  | 0 | 2.2 | 무부하 랙
B417 | R23 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall 1-PDU-03-30-28 | 5-DaHall 1-PDU-04-30-28 |  | 30 | 03 | 28 |  | 30 | 04 | 28 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  |  | 0 | 2.2 | 무부하 랙
B418 | R24 | KG이니시스 | [5 empty] | 5-DaHall 1-PDU-03-30-30 | 5-DaHall 1-PDU-04-30-30 |  | 30 | 03 | 30 |  | 30 | 04 | 30 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  |  | 0 | 0 | 무부하 랙
B425 | 5F-M-08 | Digital Edge Korea | 2.2 | 1A-4-3 | 1B-4-3 | U5-1A-46 / 2P 30A | U5-1B-46 / 2P 30A | 5-DaHall 1-PDU-01-30-46 | 5-DaHall 1-PDU-02-30-46 | 220 | 30 | 01 | 46 | 220 | 30 | 02 | 46 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0.62005 | 0.63018 | 1.2502 | 80.8 | 86.8 | #N/A | 167.6 | 변익준M 랙 |  | 0.22527 | 1.9747 | 적정함
B525 |  | DEK, 층간 Patch Cabinet | [26 empty] | 0
| 5F-O18 |  |  | 2A-4-8 | 2B-4-8 | U5-2A-05 / 2P 30A | U5-2B-05 / 2P 30A | 5-DaHall 1-PDU-03-30-5 | 5-DaHall 1-PDU-04-30-5 | 220 | 30 | 03 | 5 | 220 | 30 | 04 | 5 | U5-2A 4P 300A | U5-2B 4P 300A | LV-5A #02 3P 320A | LV-5B #02 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-O19 |  |  | 2A-4-9 | 2B-4-9 | U5-2A-07 / 2P 30A | U5-2B-07 / 2P 30A | 5-DaHall 1-PDU-03-30-7 | 5-DaHall 1-PDU-04-30-7 | 220 | 30 | 03 | 7 | 220 | 30 | 04 | 7 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-O20 |  |  | 2A-4-10 | 2B-4-10 | U5-2A-09 / 2P 30A | U5-2B-09 / 2P 30A | 5-DaHall 1-PDU-03-30-9 | 5-DaHall 1-PDU-04-30-9 | 220 | 30 | 03 | 9 | 220 | 30 | 04 | 9 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-O21 |  |  | 2A-4-11 | 2B-4-11 | U5-2A-11 / 2P 30A | U5-2B-11 / 2P 30A | 5-DaHall 1-PDU-03-30-11 | 5-DaHall 1-PDU-04-30-11 | 220 | 30 | 03 | 11 | 220 | 30 | 04 | 11 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-O22 |  |  | 2A-4-12 | 2B-4-12 | U5-2A-13 / 2P 30A | U5-2B-13 / 2P 30A | 5-DaHall 1-PDU-03-30-13 | 5-DaHall 1-PDU-04-30-13 | 220 | 30 | 03 | 13 | 220 | 30 | 04 | 13 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-O23 |  |  | 2A-4-13 | 2B-4-13 | U5-2A-15 / 2P 30A | U5-2B-15 / 2P 30A | 5-DaHall 1-PDU-03-30-15 | 5-DaHall 1-PDU-04-30-15 | 220 | 30 | 03 | 15 | 220 | 30 | 04 | 15 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-O24 |  |  | 2A-4-14 | 2B-4-14 | U5-2A-17 / 2P 30A | U5-2B-17 / 2P 30A | 5-DaHall 1-PDU-03-30-17 | 5-DaHall 1-PDU-04-30-17 | 220 | 30 | 03 | 17 | 220 | 30 | 04 | 17 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
[33 empty] | 0 | 0 | 무부하 랙
[33 empty] | 0 | 0 | 무부하 랙
[33 empty] | 0 | 0 | 무부하 랙
| 5F-N18 |  |  | 2A-5-8 | 2B-5-8 | U5-2A-35 / 2P 30A | U5-2B-35 / 2P 30A | 5-DaHall 1-PDU-03-30-35 | 5-DaHall 1-PDU-04-30-35 | 220 | 30 | 03 | 35 | 220 | 30 | 04 | 35 | U5-2A 4P 300A | U5-2B 4P 300A | LV-5A #02 3P 320A | LV-5B #02 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-N19 | [31 empty] | 0 | 0 | 무부하 랙
| 5F-N20 | [31 empty] | 0 | 0 | 무부하 랙
| 5F-N21 | [31 empty] | 0 | 0 | 무부하 랙
| 5F-N22 | [31 empty] | 0 | 0 | 무부하 랙
| 5F-N23 | [31 empty] | 0 | 0 | 무부하 랙
| 5F-N24 | [31 empty] | 0 | 0 | 무부하 랙
[33 empty] | 0 | 0 | 무부하 랙
[33 empty] | 0 | 0 | 무부하 랙
[33 empty] | 0 | 0 | 무부하 랙
| 5F-M11 | [31 empty] | 0 | 0 | 무부하 랙
| 5F-M12 | [31 empty] | 0 | 0 | 무부하 랙
| 5F-M13 | [31 empty] | 0 | 0 | 무부하 랙
| 5F-M14 | [31 empty] | 0 | 0 | 무부하 랙
| 5F-M15 | [31 empty] | 0 | 0 | 무부하 랙
| 5F-M16 | [31 empty] | 0 | 0 | 무부하 랙
[33 empty] | 0 | 0 | 무부하 랙
[33 empty] | 0 | 0 | 무부하 랙
[33 empty] | 0 | 0 | 무부하 랙
[33 empty] | 0 | 0 | 무부하 랙
| 5F-K11 |  |  | 3A-8-1 | 3B-8-1 | U5-3A-01 / 2P 30A | U5-3B-01 / 2P 30A | 5-DaHall 1-PDU-05-30-1 | 5-DaHall 1-PDU-06-30-1 | 220 | 30 | 05 | 1 | 220 | 30 | 06 | 1 | U5-3A 4P 300A | U5-3B 4P 300A | LV-5A #03 3P 320A | LV-5B #03 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-K12 |  |  | 3A-8-2 | 3B-8-2 | U5-3A-03 / 2P 30A | U5-3B-03 / 2P 30A | 5-DaHall 1-PDU-05-30-3 | 5-DaHall 1-PDU-06-30-3 | 220 | 30 | 05 | 3 | 220 | 30 | 06 | 3 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-K13 |  |  | 3A-8-3 | 3B-8-3 | U5-3A-05 / 2P 30A | U5-3B-05 / 2P 30A | 5-DaHall 1-PDU-05-30-5 | 5-DaHall 1-PDU-06-30-5 | 220 | 30 | 05 | 5 | 220 | 30 | 06 | 5 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-K14 |  |  | 3A-8-4 | 3B-8-4 | U5-3A-09 / 2P 30A | U5-3B-07 / 2P 30A | 5-DaHall 1-PDU-05-30-9 | 5-DaHall 1-PDU-06-30-7 | 220 | 30 | 05 | 9 | 220 | 30 | 06 | 7 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-K15 |  |  | 3A-8-5 | 3B-8-5 | U5-3A-11 / 2P 30A | U5-3B-09 / 2P 30A | 5-DaHall 1-PDU-05-30-11 | 5-DaHall 1-PDU-06-30-9 | 220 | 30 | 05 | 11 | 220 | 30 | 06 | 9 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-K16 |  |  | 3A-8-6 | 3B-8-6 | U5-3A-13 / 2P 30A | U5-3B-11 / 2P 30A | 5-DaHall 1-PDU-05-30-13 | 5-DaHall 1-PDU-06-30-11 | 220 | 30 | 05 | 13 | 220 | 30 | 06 | 11 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-K17 |  |  | 3A-8-7 | 3B-8-7 | U5-3A-15 / 2P 30A | U5-3B-15 / 2P 30A | 5-DaHall 1-PDU-05-30-15 | 5-DaHall 1-PDU-06-30-15 | 220 | 30 | 05 | 15 | 220 | 30 | 06 | 15 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-K18 |  |  | 3A-8-8 | 3B-8-8 | U5-3A-17 / 2P 30A | U5-3B-17 / 2P 30A | 5-DaHall 1-PDU-05-30-17 | 5-DaHall 1-PDU-06-30-17 | 220 | 30 | 05 | 17 | 220 | 30 | 06 | 17 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
[33 empty] | 0 | 0 | 무부하 랙
[33 empty] | 0 | 0 | 무부하 랙
| 5F-J11 |  |  | 3A-9-1 | 3B-9-1 | U5-3A-19 / 2P 30A | U5-3B-19 / 2P 30A | 5-DaHall 1-PDU-05-30-19 | 5-DaHall 1-PDU-06-30-19 | 220 | 30 | 05 | 19 | 220 | 30 | 06 | 19 | U5-3A 4P 300A | U5-3B 4P 300A | LV-5A #03 3P 320A | LV-5B #03 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-J12 |  |  | 3A-9-2 | 3B-9-2 | U5-3A-21 / 2P 30A | U5-3B-21 / 2P 30A | 5-DaHall 1-PDU-05-30-21 | 5-DaHall 1-PDU-06-30-21 | 220 | 30 | 05 | 21 | 220 | 30 | 06 | 21 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-J13 |  |  | 3A-9-3 | 3B-9-3 | U5-3A-23 / 2P 30A | U5-3B-23 / 2P 30A | 5-DaHall 1-PDU-05-30-23 | 5-DaHall 1-PDU-06-30-23 | 220 | 30 | 05 | 23 | 220 | 30 | 06 | 23 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-J14 |  |  | 3A-9-4 | 3B-9-4 | U5-3A-27 / 2P 30A | U5-3B-25 / 2P 30A | 5-DaHall 1-PDU-05-30-27 | 5-DaHall 1-PDU-06-30-25 | 220 | 30 | 05 | 27 | 220 | 30 | 06 | 25 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-J15 |  |  | 3A-9-5 | 3B-9-5 | U5-3A-29 / 2P 30A | U5-3B-27 / 2P 30A | 5-DaHall 1-PDU-05-30-29 | 5-DaHall 1-PDU-06-30-27 | 220 | 30 | 05 | 29 | 220 | 30 | 06 | 27 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-J16 |  |  | 3A-9-6 | 3B-9-6 | U5-3A-31 / 2P 30A | U5-3B-29 / 2P 30A | 5-DaHall 1-PDU-05-30-31 | 5-DaHall 1-PDU-06-30-29 | 220 | 30 | 05 | 31 | 220 | 30 | 06 | 29 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-J17 |  |  | 3A-9-7 | 3B-9-7 | U5-3A-33 / 2P 30A | U5-3B-33 / 2P 30A | 5-DaHall 1-PDU-05-30-33 | 5-DaHall 1-PDU-06-30-33 | 220 | 30 | 05 | 33 | 220 | 30 | 06 | 33 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-J18 |  |  | 3A-9-8 | 3B-9-8 | U5-3A-35 / 2P 30A | U5-3B-35 / 2P 30A | 5-DaHall 1-PDU-05-30-35 | 5-DaHall 1-PDU-06-30-35 | 220 | 30 | 05 | 35 | 220 | 30 | 06 | 35 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
[33 empty] | 0 | 0 | 무부하 랙
[33 empty] | 0 | 0 | 무부하 랙
| 5F-I11 |  |  | 3A-10-1 | 3B-10-1 | U5-3A-37 / 2P 30A | U5-3B-37 / 2P 30A | 5-DaHall 1-PDU-05-30-37 | 5-DaHall 1-PDU-06-30-37 | 220 | 30 | 05 | 37 | 220 | 30 | 06 | 37 | U5-3A 4P 300A | U5-3B 4P 300A | LV-5A #03 3P 320A | LV-5B #03 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
| 5F-I12 |  |  | 3A-10-2 | 3B-10-2 | U5-3A-39 / 2P 30A | U5-3B-39 / 2P 30A | 5-DaHall 1-PDU-05-30-39 | 5-DaHall 1-PDU-06-30-39 | 220 | 30 | 05 | 39 | 220 | 30 | 06 | 39 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
| 5F-I13 |  |  | 3A-10-3 | 3B-10-3 | U5-3A-41 / 2P 30A | U5-3B-41 / 2P 30A | 5-DaHall 1-PDU-05-30-41 | 5-DaHall 1-PDU-06-30-41 | 220 | 30 | 05 | 41 | 220 | 30 | 06 | 41 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
| 5F-I14 |  |  | 3A-10-4 | 3B-10-4 | U5-3A-45 / 2P 30A | U5-3B-43 / 2P 30A | 5-DaHall 1-PDU-05-30-45 | 5-DaHall 1-PDU-06-30-43 | 220 | 30 | 05 | 45 | 220 | 30 | 06 | 43 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
| 5F-I15 |  |  | 3A-10-5 | 3B-10-5 | U5-3A-47 / 2P 30A | U5-3B-45 / 2P 30A | 5-DaHall 1-PDU-05-30-47 | 5-DaHall 1-PDU-06-30-45 | 220 | 30 | 05 | 47 | 220 | 30 | 06 | 45 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
| 5F-I16 |  |  | 3A-10-6 | 3B-10-6 | U5-3A-49 / 2P 30A | U5-3B-47 / 2P 30A | 5-DaHall 1-PDU-05-30-49 | 5-DaHall 1-PDU-06-30-47 | 220 | 30 | 05 | 49 | 220 | 30 | 06 | 47 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
| 5F-I17 |  |  | 3A-10-7 | 3B-10-7 | U5-3A-51 / 2P 30A | U5-3B-51 / 2P 30A | 5-DaHall 1-PDU-05-30-51 | 5-DaHall 1-PDU-06-30-51 | 220 | 30 | 05 | 51 | 220 | 30 | 06 | 51 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
| 5F-I18 |  |  | 3A-10-8 | 3B-10-8 | U5-3A-53 / 2P 30A | U5-3B-53 / 2P 30A | 5-DaHall 1-PDU-05-30-53 | 5-DaHall 1-PDU-06-30-53 | 220 | 30 | 05 | 53 | 220 | 30 | 06 | 53 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
[33 empty] | 0 | 0 | 무부하 랙
[33 empty] | 0 | 0 | 무부하 랙
C304 | 예비Rack#04/R-6-4 | LG CNS | 13 | 예비Rack#4 / R6-4-1 | 예비Rack#4 / R6-4-2 | LG PDU(A1), #22 / 2P 50A | LG PDU (B1), #22 /2P 50A | 5-DaHall 1-PDU-19-50-22 | 5-DaHall 1-PDU-20-50-22 | 220 | 50 | 19 | 22 | 220 | 50 | 20 | 22 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 1369.8 | 133.3 | #N/A | 2770.1 |  |  | 3.7233 | 9.2767 | 적정함
|  |  |  | 예비Rack#4 / R6-4-3 | 예비Rack#4 / R6-4-4 | LG PDU(A2), #22 / 2P 50A | LG PDU (B2), #22 / 2P 50A | 5-DaHall 1-PDU-21-50-22 | 5-DaHall 1-PDU-22-50-22 | 220 | 50 | 21 | 22 | 220 | 50 | 22 | 22 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 1132.9 | 134.1 | #N/A | 2770.1 |  |  | 3.7233 | -3.7233 | 사용초과 | 0 | 0
C305 | 예비Rack#03/R6-3 | LG CNS | 13 | 예비Rack#3 / R6-3-1 | 예비Rack#3 / R6-3-2 | LG PDU(A1), #20 / 2P 50A | LG PDU (B1), #20 /2P 50A | 5-DaHall 1-PDU-19-50-20 | 5-DaHall 1-PDU-20-50-20 | 220 | 50 | 19 | 20 | 220 | 50 | 20 | 20 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 1510.1 | 289.1 | #N/A | 3413.6 |  |  | 4.5882 | 8.4118 | 적정함
|  |  |  | 예비Rack#3 / R6-3-3 | 예비Rack#3 / R6-3-4 | LG PDU(A2), #20 / 2P 50A | LG PDU (B2), #20 / 2P 50A | 5-DaHall 1-PDU-21-50-20 | 5-DaHall 1-PDU-22-50-20 | 220 | 50 | 21 | 20 | 220 | 50 | 22 | 20 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 1449.6 | 164.8 | #N/A | 3413.6 |  |  | 4.5882 | -4.5882 | 사용초과 | 0 | 0
C306 | 예비Rack#02/R6-2 | LG CNS | 13 | 예비Rack#2 / R6-2-1 | 예비Rack#2 / R6-2-2 | LG PDU(A1), #18 / 2P 50A | LG PDU (B1), #18 /2P 50A | 5-DaHall 1-PDU-19-50-18 | 5-DaHall 1-PDU-20-50-18 | 220 | 50 | 19 | 18 | 220 | 50 | 20 | 18 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 931.9 | 894.8 | #N/A | 3539.3 |  |  | 4.7571 | 8.2429 | 적정함
|  |  |  | 예비Rack#2 / R6-2-3 | 예비Rack#2 / R6-2-4 | LG PDU(A2), #18 / 2P 50A | LG PDU (B2), #18 / 2P 50A | 5-DaHall 1-PDU-21-50-18 | 5-DaHall 1-PDU-22-50-18 | 220 | 50 | 21 | 18 | 220 | 50 | 22 | 18 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 874.2 | 838.4 | #N/A | 3539.3 |  |  | 4.7571 | -4.7571 | 사용초과 | 0 | 0
C307 | 예비Rack#01/R6-1 | LG CNS | 13 | 예비Rack#1 / R6-1-1 | 예비Rack#1 / R6-1-2 | LG PDU(A1), #16 / 2P 50A | LG PDU (B1), #16 /2P 50A | 5-DaHall 1-PDU-19-50-16 | 5-DaHall 1-PDU-20-50-16 | 220 | 50 | 19 | 16 | 220 | 50 | 20 | 16 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 1364.8 | 1384.2 | #N/A | 5096.6 |  |  | 6.8503 | 6.1497 | 적정함
|  |  |  | 예비Rack#1 / R6-1-3 | 예비Rack#1 / R6-1-4 | LG PDU(A2), #16 / 2P 50A | LG PDU (B2), #16 / 2P 50A | 5-DaHall 1-PDU-21-50-16 | 5-DaHall 1-PDU-22-50-16 | 220 | 50 | 21 | 16 | 220 | 50 | 22 | 16 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 1146 | 1201.6 | #N/A | 5096.6 |  |  | 6.8503 | -6.8503 | 사용초과 | 0 | 0
C404 | R5-4 | LG CNS | 13 |  |  |  |  | 5-DaHall 1-PDU-19-30-21 | 5-DaHall 1-PDU-20-30-21 | 220 | 30 | 19 | 21 | 220 | 30 | 20 | 21 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | '23.11.10 준비완료 |  | 0 | 13 | 무부하 랙
[8 empty] | 5-DaHall 1-PDU-21-30-21 | 5-DaHall 1-PDU-22-30-21 | 220 | 30 | 21 | 21 | 220 | 30 | 22 | 21 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 0 | 0 | #N/A | 0 |  |  | 0 | 0 | 무부하 랙
C405 | DGX Rack#3 / R5-3 | LG CNS | 13 | DGX Rack#3 / R5-3-1 | DGX Rack#3 / R5-3-2 | LG PDU(A1), #19 / 2P 30A | LG PDU (B1), #19 /2P 30A | 5-DaHall 1-PDU-19-30-19 | 5-DaHall 1-PDU-20-30-19 | 220 | 30 | 19 | 19 | 220 | 30 | 20 | 19 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 545.2 | 552.9 | #N/A | 2398.8 |  |  | 3.2242 | 9.7758 | 적정함
|  |  |  | DGX Rack#3 / R5-3-3 | DGX Rack#3 / R5-3-4 | LG PDU(A2), #19 / 2P 30A | LG PDU (B2), #19 / 2P 30A | 5-DaHall 1-PDU-21-30-19 | 5-DaHall 1-PDU-22-30-19 | 220 | 30 | 21 | 19 | 220 | 30 | 22 | 19 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 624.1 | 676.6 | #N/A | 2398.8 |  |  | 3.2242 | -3.2242 | 사용초과 | 0 | 0
C406 | DGX Rack#2 / R5-2 | LG CNS | 13 | DGX Rack#2 / R5-2-1 | DGX Rack#2 / R5-2-2 | LG PDU(A1), #17 / 2P 30A | LG PDU (B1), #17 /2P 30A | 5-DaHall 1-PDU-19-30-17 | 5-DaHall 1-PDU-20-30-17 | 220 | 30 | 19 | 17 | 220 | 30 | 20 | 17 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 574.2 | 638.2 | #N/A | 2516.6 |  |  | 3.3825 | 9.6175 | 적정함
|  |  |  | DGX Rack#2 / R5-2-3 | DGX Rack#2 / R5-2-4 | LG PDU(A2), #17 / 2P 30A | LG PDU (B2), #17 / 2P 30A | 5-DaHall 1-PDU-21-30-17 | 5-DaHall 1-PDU-22-30-17 | 220 | 30 | 21 | 17 | 220 | 30 | 22 | 17 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 709.6 | 594.6 | #N/A | 2516.6 |  |  | 3.3825 | -3.3825 | 사용초과 | 0 | 0
C407 | DGX Rack#1 / R5-1 | LG CNS | 13 | DGX Rack#1 / R5-1-1 | DGX Rack#1 / R5-1-2 | LG PDU(A1), #15 / 2P 30A | LG PDU (B1), #15 /2P 30A | 5-DaHall 1-PDU-19-30-15 | 5-DaHall 1-PDU-20-30-15 | 220 | 30 | 19 | 15 | 220 | 30 | 20 | 15 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 990.9 | 1186.2 | #N/A | 3355.4 |  |  | 4.5099 | 8.4901 | 적정함
|  |  |  | DGX Rack#1 / R5-1-3 | DGX Rack#1 / R5-1-4 | LG PDU(A2), #15 / 2P 30A | LG PDU (B2), #15 / 2P 30A | 5-DaHall 1-PDU-21-30-15 | 5-DaHall 1-PDU-22-30-15 | 220 | 30 | 21 | 15 | 220 | 30 | 22 | 15 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 528.6 | 649.7 | #N/A | 3355.4 |  |  | 4.5099 | -4.5099 | 사용초과 | 0 | 0
C504 | NetApp AFF#2 / R4-4 | LG CNS | 13 | NetApp AFF#2 / R4-4-1 | NetApp AFF#2 / R4-4-2 | LG PDU(A1), #14 / 2P 30A | LG PDU (B1), #14 /2P 30A | 5-DaHall 1-PDU-19-30-14 | 5-DaHall 1-PDU-20-30-14 | 220 | 30 | 19 | 14 | 220 | 30 | 20 | 14 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 232.4 | 214.4 | #N/A | 986.1 |  |  | 1.3254 | 11.6746 | 적정함
|  |  |  | NetApp AFF#2 / R4-4-3 | NetApp AFF#2 / R4-4-4 | LG PDU(A2), #14 / 2P 30A | LG PDU (B2), #14 / 2P 30A | 5-DaHall 1-PDU-21-30-14 | 5-DaHall 1-PDU-22-30-14 | 220 | 30 | 21 | 14 | 220 | 30 | 22 | 14 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 268.8 | 270.5 | #N/A | 986.1 |  |  | 1.3254 | -1.3254 | 사용초과 | 0 | 0
C505 | NetApp FAS#1 / R4-3 | LG CNS | 13 | NetApp FAS#1 / R4-3-1 | NetApp FAS#1 / R4-3-2 | LG PDU(A1), #12 / 2P 30A | LG PDU (B1), #12 /2P 30A | 5-DaHall 1-PDU-19-30-12 | 5-DaHall 1-PDU-20-30-12 | 220 | 30 | 19 | 12 | 220 | 30 | 20 | 12 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 562.8 | 540.9 | #N/A | 1509.8 |  |  | 2.0293 | 10.9707 | 적정함
|  |  |  | NetApp FAS#1 / R4-3-2 | NetApp FAS#1 / R4-3-4 | LG PDU(A2), #12 / 2P 30A | LG PDU (B2), #12 / 2P 30A | 5-DaHall 1-PDU-21-30-12 | 5-DaHall 1-PDU-22-30-12 | 220 | 30 | 21 | 12 | 220 | 30 | 22 | 12 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 197.5 | 208.6 | #N/A | 1509.8 |  |  | 2.0293 | -2.0293 | 사용초과 | 0 | 0
C506 | A40 Rack#2 / R4-2 | LG CNS | 13 | A40 Rack#2 / R4-2-1 | A40 Rack#2 / R4-2-2 | LG PDU(A1), #10 / 2P 50A | LG PDU (B1), #10 /2P 50A | 5-DaHall 1-PDU-19-50-10 | 5-DaHall 1-PDU-20-50-10 | 220 | 50 | 19 | 10 | 220 | 50 | 20 | 10 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 951.7 | 940.6 | #N/A | 4079.2 |  |  | 5.4828 | 7.5172 | 적정함
|  |  |  | A40 Rack#2 / R4-2-3 | A40 Rack#2 / R4-2-4 | LG PDU(A2), #10 / 2P 50A | LG PDU (B2), #10 / 2P 50A | 5-DaHall 1-PDU-21-50-10 | 5-DaHall 1-PDU-22-50-10 | 220 | 50 | 21 | 10 | 220 | 50 | 22 | 10 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 1067 | 1119.9 | #N/A | 4079.2 |  |  | 5.4828 | -5.4828 | 사용초과 | 0 | 0
C507 | A40 Rack#1 / R4-1 | LG CNS | 13 | A40 Rack#1 / R4-1-1 | A40 Rack#1 / R4-1-2 | LG PDU(A1), #08 / 2P 50A | LG PDU (B1), #08 /2P 50A | 5-DaHall 1-PDU-19-50-8 | 5-DaHall 1-PDU-20-50-8 | 220 | 50 | 19 | 8 | 220 | 50 | 20 | 8 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 913.2 | 936.3 | #N/A | 3833.7 |  |  | 5.1528 | 7.8472 | 적정함
|  |  |  | A40 Rack#1 / R4-1-3 | A40 Rack#1 / R4-1-4 | LG PDU(A2), #08 / 2P 50A | LG PDU (B2), #08 / 2P 50A | 5-DaHall 1-PDU-21-50-8 | 5-DaHall 1-PDU-22-50-8 | 220 | 50 | 21 | 8 | 220 | 50 | 22 | 8 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 957.8 | 1026.4 | #N/A | 3833.7 |  |  | 5.1528 | -5.1528 | 사용초과 | 0 | 0
C604 | R3-4 | LG CNS | 13 |  |  |  |  | 5-DaHall 1-PDU-19-50-24 | 5-DaHall 1-PDU-20-50-24 | 220 | 50 | 19 | 24 | 220 | 50 | 20 | 24 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | '23.11.10 준비완료 |  | 0 | 13 | 무부하 랙
[8 empty] | 5-DaHall 1-PDU-21-50-24 | 5-DaHall 1-PDU-22-50-24 | 220 | 50 | 21 | 24 | 220 | 50 | 22 | 24 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 0 | 0 | #N/A | 0 |  |  | 0 | 0 | 무부하 랙
C605 | NW/Mgmt Rack / R3-3 | LG CNS | 13 | NW/Mgmt Rack / R3-3-1 | NW/Mgmt Rack / R3-3-2 | LG PDU(A1), #06 / 2P 30A | LG PDU (B1), #06 /2P 30A | 5-DaHall 1-PDU-19-30-6 | 5-DaHall 1-PDU-20-30-6 | 220 | 30 | 19 | 6 | 220 | 30 | 20 | 6 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 449.2 | 264.2 | #N/A | 1737.4 |  |  | 2.3352 | 10.6648 | 적정함
|  |  |  | NW/Mgmt Rack / R3-3-3 | NW/Mgmt Rack / R3-3-4 | LG PDU(A2), #06 / 2P 30A | LG PDU (B2), #06 / 2P 30A | 5-DaHall 1-PDU-21-30-6 | 5-DaHall 1-PDU-22-30-6 | 220 | 30 | 21 | 6 | 220 | 30 | 22 | 6 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 662.5 | 361.5 | #N/A | 1737.4 |  |  | 2.3352 | -2.3352 | 사용초과 | 0 | 0
C606 | RTX Rack#9 / R3-2 | LG CNS | 13 | RTX Rack#9 / R3-2-1 | RTX Rack#9 / R3-2-2 | LG PDU(A1), #04 / 2P 50A | LG PDU (B1), #04 /2P 50A | 5-DaHall 1-PDU-19-50-4 | 5-DaHall 1-PDU-20-50-4 | 220 | 50 | 19 | 4 | 220 | 50 | 20 | 4 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 789.1 | 768.6 | #N/A | 2782.3 |  |  | 3.7397 | 9.2603 | 적정함
|  |  |  | RTX Rack#9 / R3-2-3 | RTX Rack#9 / R3-2-4 | LG PDU(A2), #04 / 2P 50A | LG PDU (B2), #04 / 2P 50A | 5-DaHall 1-PDU-21-50-4 | 5-DaHall 1-PDU-22-50-4 | 220 | 50 | 21 | 4 | 220 | 50 | 22 | 4 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 620.6 | 604 | #N/A | 2782.3 |  |  | 3.7397 | -3.7397 | 사용초과 | 0 | 0
C607 | RTX Rack#8 / R3-1 | LG CNS | 13 | RTX Rack#8 / R3-1-1 | RTX Rack#8 / R3-1-2 | LG PDU(A1), #02 / 2P 50A | LG PDU (B1), #02 /2P 50A | 5-DaHall 1-PDU-19-50-2 | 5-DaHall 1-PDU-20-50-2 | 220 | 50 | 19 | 2 | 220 | 50 | 20 | 2 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 862 | 910.9 | #N/A | 3097.7 |  |  | 4.1636 | 8.8364 | 적정함
|  |  |  | RTX Rack#8 / R3-1-3 | RTX Rack#8 / R3-1-4 | LG PDU(A2), #02 / 2P 50A | LG PDU (B2), #02 / 2P 50A | 5-DaHall 1-PDU-21-50-2 | 5-DaHall 1-PDU-22-50-2 | 220 | 50 | 21 | 2 | 220 | 50 | 22 | 2 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 668 | 656.8 | #N/A | 3097.7 |  |  | 4.1636 | -4.1636 | 사용초과 | 0 | 0
C704 | RTX Rack#7 / R2-4 | LG CNS | 13 | RTX Rack#7 / R2-4-1 | RTX Rack#7 / R2-4-2 | LG PDU(A1), #13 / 2P 50A | LG PDU (B1), #13 /2P 50A | 5-DaHall 1-PDU-19-50-13 | 5-DaHall 1-PDU-20-50-13 | 220 | 50 | 19 | 13 | 220 | 50 | 20 | 13 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 874.8 | 809.1 | #N/A | 3404.9 |  |  | 4.5765 | 8.4235 | 적정함
|  |  |  | RTX Rack#7 / R2-4-3 | RTX Rack#7 / R2-4-4 | LG PDU(A2), #13 / 2P 50A | LG PDU (B2), #13 / 2P 50A | 5-DaHall 1-PDU-21-50-13 | 5-DaHall 1-PDU-22-50-13 | 220 | 50 | 21 | 13 | 220 | 50 | 22 | 13 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 900.8 | 820.2 | #N/A | 3404.9 |  |  | 4.5765 | -4.5765 | 사용초과 | 0 | 0
C705 | RTX Rack#6 / R2-3 | LG CNS | 13 | RTX Rack#6 / R2-3-1 | RTX Rack#6 / R2-3-2 | LG PDU(A1), #11 / 2P 50A | LG PDU (B1), #11 /2P 50A | 5-DaHall 1-PDU-19-50-11 | 5-DaHall 1-PDU-20-50-11 | 220 | 50 | 19 | 11 | 220 | 50 | 20 | 11 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 839.2 | 739 | #N/A | 3263.2 |  |  | 4.386 | 8.614 | 적정함
|  |  |  | RTX Rack#6 / R2-3-3 | RTX Rack#6 / R2-3-4 | LG PDU(A2), #11 / 2P 50A | LG PDU (B2), #11 / 2P 50A | 5-DaHall 1-PDU-21-50-11 | 5-DaHall 1-PDU-22-50-11 | 220 | 50 | 21 | 11 | 220 | 50 | 22 | 11 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 814.8 | 870.2 | #N/A | 3263.2 |  |  | 4.386 | -4.386 | 사용초과 | 0 | 0
C706 | RTX Rack#5 / R2-2 | LG CNS | 13 | RTX Rack#5 / R2-2-1 | RTX Rack#5 / R2-2-2 | LG PDU(A1), #09 / 2P 50A | LG PDU (B1), #09 /2P 50A | 5-DaHall 1-PDU-19-50-9 | 5-DaHall 1-PDU-20-50-9 | 220 | 50 | 19 | 9 | 220 | 50 | 20 | 9 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 907.1 | 886.7 | #N/A | 4126.7 |  |  | 5.5466 | 7.4534 | 적정함
|  |  |  | RTX Rack#5 / R2-2-3 | RTX Rack#5 / R2-2-4 | LG PDU(A2), #09 / 2P 50A | LG PDU (B2), #09 / 2P 50A | 5-DaHall 1-PDU-21-50-9 | 5-DaHall 1-PDU-22-50-9 | 220 | 50 | 21 | 9 | 220 | 50 | 22 | 9 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 1159.6 | 1173.3 | #N/A | 4126.7 |  |  | 5.5466 | -5.5466 | 사용초과 | 0 | 0
C707 | RTX Rack#4 / R2-1 | LG CNS | 13 | RTX Rack#4 / R2-1-1 | RTX Rack#4 / R2-1-2 | LG PDU(A1), #07 / 2P 50A | LG PDU (B1), #07 /2P 50A | 5-DaHall 1-PDU-19-50-7 | 5-DaHall 1-PDU-20-50-7 | 220 | 50 | 19 | 7 | 220 | 50 | 20 | 7 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 1271.9 | 1321.7 | #N/A | 4047.8 |  |  | 5.4406 | 7.5594 | 적정함
|  |  |  | RTX Rack#4 / R2-1-3 | RTX Rack#4 / R2-1-4 | LG PDU(A2), #07 / 2P 50A | LG PDU (B2), #07 / 2P 50A | 5-DaHall 1-PDU-21-50-7 | 5-DaHall 1-PDU-22-50-7 | 220 | 50 | 21 | 7 | 220 | 50 | 22 | 7 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 736.5 | 717.7 | #N/A | 4047.8 |  |  | 5.4406 | -5.4406 | 사용초과 | 0 | 0
C804 | RTX Rack#4 / R1-4 | LG CNS | 13 | RTX Rack#4 / R1-4-1 | RTX Rack#4 / R1-4-2 |  |  | 5-DaHall 1-PDU-19-50-23 | 5-DaHall 1-PDU-20-50-23 | 220 | 50 | 19 | 23 | 220 | 50 | 20 | 23 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 632 | 659.7 | #N/A | 2554.1 | '23.12.05 투입 |  | 3.4329 | 9.5671 | 적정함
|  |  |  | RTX Rack#4 / R1-4-3 | RTX Rack#4 / R1-4-4 |  |  | 5-DaHall 1-PDU-21-50-23 | 5-DaHall 1-PDU-22-50-23 | 220 | 50 | 21 | 23 | 220 | 50 | 22 | 23 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 619.6 | 642.8 | #N/A | 2554.1 |  |  | 3.4329 | -3.4329 | 사용초과 | 0 | 0
C805 | RTX Rack#3 / R1-3 | LG CNS | 13 | RTX Rack#3 / R1-3-1 | RTX Rack#3 / R1-3-2 | LG PDU(A1), #05 / 2P 50A | LG PDU (B1), #05 /2P 50A | 5-DaHall 1-PDU-19-50-5 | 5-DaHall 1-PDU-20-50-5 | 220 | 50 | 19 | 5 | 220 | 50 | 20 | 5 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | #N/A | 648.4 |  |  | 0.87151 | 12.1285 | 적정함
|  |  |  | RTX Rack#3 / R1-3-3 | RTX Rack#3 / R1-3-4 | LG PDU(A2), #05 / 2P 50A | LG PDU (B2), #05 / 2P 50A | 5-DaHall 1-PDU-21-50-5 | 5-DaHall 1-PDU-22-50-5 | 220 | 50 | 21 | 5 | 220 | 50 | 22 | 5 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 332.7 | 315.7 | #N/A | 648.4 |  |  | 0.87151 | -0.87151 | 사용초과 | 0 | 0
C806 | RTX Rack#2 / R1-2 | LG CNS | 13 | RTX Rack#2 / R1-2-1 | RTX Rack#2 / R1-2-2 | LG PDU(A1), #03 / 2P 50A | LG PDU (B1), #03 /2P 50A | 5-DaHall 1-PDU-19-50-3 | 5-DaHall 1-PDU-20-50-3 | 220 | 50 | 19 | 3 | 220 | 50 | 20 | 3 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 824.9 | 836.1 | #N/A | 3818.2 |  |  | 5.132 | 7.868 | 적정함
|  |  |  | RTX Rack#2 / R1-2-3 | RTX Rack#2 / R1-2-4 | LG PDU(A2), #03 / 2P 50A | LG PDU (B2), #03 / 2P 50A | 5-DaHall 1-PDU-21-50-3 | 5-DaHall 1-PDU-22-50-3 | 220 | 50 | 21 | 3 | 220 | 50 | 22 | 3 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 1058.7 | 1098.5 | #N/A | 3818.2 |  |  | 5.132 | -5.132 | 사용초과 | 0 | 0
C807 | RTX Rack#1 / R1-1 | LG CNS | 13 | RTX Rack#1 / R1-1-1 | RTX Rack#1 / R1-1-2 | LG PDU(A1), #01 / 2P 50A | LG PDU (B1), #01 /2P 50A | 5-DaHall 1-PDU-19-50-1 | 5-DaHall 1-PDU-20-50-1 | 220 | 50 | 19 | 1 | 220 | 50 | 20 | 1 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 595.8 | 791.4 | #N/A | 3811.6 |  |  | 5.1231 | 7.8769 | 적정함
|  |  |  | RTX Rack#1 / R1-1-3 | RTX Rack#1 / R1-1-4 | LG PDU(A2), #01 / 2P 50A | LG PDU (B2), #01 / 2P 50A | 5-DaHall 1-PDU-21-50-1 | 5-DaHall 1-PDU-22-50-1 | 220 | 50 | 21 | 1 | 220 | 50 | 22 | 1 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | 1186.6 | 1237.8 | #N/A | 3811.6 |  |  | 5.1231 | -5.1231 | 사용초과 | 0 | 0 | 0 | 0 | 0
C901 | 5F-H11 |  |  | 3A-11-1 | 3B-11-1 | U5-3A-02 / 2P 30A | U5-3B-02 / 2P 30A | 5-DaHall 1-PDU-05-30-2 | 5-DaHall 1-PDU-06-30-2 | 220 | 30 | 05 | 2 | 220 | 30 | 06 | 2 | U5-3A 4P 300A | U5-3B 4P 300A | LV-5A #03 3P 320A | LV-5B #03 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
C902 | 5F-H12 |  |  | 3A-11-2 | 3B-11-2 | U5-3A-04 / 2P 30A | U5-3B-04 / 2P 30A | 5-DaHall 1-PDU-05-30-4 | 5-DaHall 1-PDU-06-30-4 | 220 | 30 | 05 | 4 | 220 | 30 | 06 | 4 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
C903 | 5F-H13 |  |  | 3A-11-3 | 3B-11-3 | U5-3A-06 / 2P 30A | U5-3B-06 / 2P 30A | 5-DaHall 1-PDU-05-30-6 | 5-DaHall 1-PDU-06-30-6 | 220 | 30 | 05 | 6 | 220 | 30 | 06 | 6 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
C904 | 5F-H14 |  |  | 3A-11-4 | 3B-11-4 | U5-3A-08 / 2P 30A | U5-3B-08 / 2P 30A | 5-DaHall 1-PDU-05-30-8 | 5-DaHall 1-PDU-06-30-8 | 220 | 30 | 05 | 8 | 220 | 30 | 06 | 8 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
C905 | 5F-H15 |  |  | 3A-11-5 | 3B-11-5 | U5-3A-10 / 2P 30A | U5-3B-10 / 2P 30A | 5-DaHall 1-PDU-05-30-10 | 5-DaHall 1-PDU-06-30-10 | 220 | 30 | 05 | 10 | 220 | 30 | 06 | 10 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
C906 | 5F-H16 |  |  | 3A-11-6 | 3B-11-6 | U5-3A-12 / 2P 30A | U5-3B-12 / 2P 30A | 5-DaHall 1-PDU-05-30-12 | 5-DaHall 1-PDU-06-30-12 | 220 | 30 | 05 | 12 | 220 | 30 | 06 | 12 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
C907 | 5F-H17 |  |  | 3A-11-7 | 3B-11-7 | U5-3A-14 / 2P 30A | U5-3B-16 / 2P 30A | 5-DaHall 1-PDU-05-30-14 | 5-DaHall 1-PDU-06-30-16 | 220 | 30 | 05 | 14 | 220 | 30 | 06 | 16 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
C908 | 5F-H18 |  |  | 3A-11-8 | 3B-11-8 | U5-3A-16 / 2P 30A | U5-3B-18 / 2P 30A | 5-DaHall 1-PDU-05-30-16 | 5-DaHall 1-PDU-06-30-18 | 220 | 30 | 05 | 16 | 220 | 30 | 06 | 18 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
C909 | [32 empty] | 0 | 0 | 무부하 랙
C910 | [32 empty] | 0 | 0 | 무부하 랙
C1001 | 5F-G11 |  |  | 3A-12-1 | 3B-12-1 | U5-3A-18 / 2P 30A | U5-3B-20 / 2P 30A | 5-DaHall 1-PDU-05-30-18 | 5-DaHall 1-PDU-06-30-20 | 220 | 30 | 05 | 18 | 220 | 30 | 06 | 20 | U5-3A 4P 300A | U5-3B 4P 300A | LV-5A #03 3P 320A | LV-5B #03 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
C1002 | 5F-G12 |  |  | 3A-12-2 | 3B-12-2 | U5-3A-20 / 2P 30A | U5-3B-22 / 2P 30A | 5-DaHall 1-PDU-05-30-20 | 5-DaHall 1-PDU-06-30-22 | 220 | 30 | 05 | 20 | 220 | 30 | 06 | 22 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
C1003 | 5F-G13 |  |  | 3A-12-3 | 3B-12-3 | U5-3A-22 / 2P 30A | U5-3B-24 / 2P 30A | 5-DaHall 1-PDU-05-30-22 | 5-DaHall 1-PDU-06-30-24 | 220 | 30 | 05 | 22 | 220 | 30 | 06 | 24 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
C1004 | 5F-G14 |  |  | 3A-12-4 | 3B-12-4 | U5-3A-24 / 2P 30A | U5-3B-26 / 2P 30A | 5-DaHall 1-PDU-05-30-24 | 5-DaHall 1-PDU-06-30-26 | 220 | 30 | 05 | 24 | 220 | 30 | 06 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
C1005 | 5F-G15 |  |  | 3A-12-5 | 3B-12-5 | U5-3A-26 / 2P 30A | U5-3B-28 / 2P 30A | 5-DaHall 1-PDU-05-30-26 | 5-DaHall 1-PDU-06-30-28 | 220 | 30 | 05 | 26 | 220 | 30 | 06 | 28 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
C1006 | 5F-G16 |  |  | 3A-12-6 | 3B-12-6 | U5-3A-28 / 2P 30A | U5-3B-30 / 2P 30A | 5-DaHall 1-PDU-05-30-28 | 5-DaHall 1-PDU-06-30-30 | 220 | 30 | 05 | 28 | 220 | 30 | 06 | 30 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
C1007 | 5F-G17 |  |  | 3A-12-7 | 3B-12-7 | U5-3A-30 / 2P 30A | U5-3B-34 / 2P 30A | 5-DaHall 1-PDU-05-30-30 | 5-DaHall 1-PDU-06-30-34 | 220 | 30 | 05 | 30 | 220 | 30 | 06 | 34 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
C1008 | 5F-G18 |  |  | 3A-12-8 | 3B-12-8 | U5-3A-32 / 2P 30A | U5-3B-36 / 2P 30A | 5-DaHall 1-PDU-05-30-32 | 5-DaHall 1-PDU-06-30-36 | 220 | 30 | 05 | 32 | 220 | 30 | 06 | 36 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF |  | 0 | 0 | 무부하 랙
C1009 | [32 empty] | 0 | 0 | 무부하 랙
C1010 | [32 empty] | 0 | 0 | 무부하 랙
|  |  |  | 1A-1-1 | 1B-1-1 | U5-1A-01 / 2P 30A | U5-1B-01 / 2P 30A | 5-DaHall 1-PDU-01-30-1 | 5-DaHall 1-PDU-02-30-1 | 220 | 30 | 01 | 1 | 220 | 30 | 02 | 1 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-R12 |  |  | 1A-1-2 | 1B-1-2 | U5-1A-03 / 2P 30A | U5-1B-03 / 2P 30A | 5-DaHall 1-PDU-01-30-3 | 5-DaHall 1-PDU-02-30-3 | 220 | 30 | 01 | 3 | 220 | 30 | 02 | 3 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-R13 |  |  | 1A-1-3 | 1B-1-3 | U5-1A-05 / 2P 30A | U5-1B-05 / 2P 30A | 5-DaHall 1-PDU-01-30-5 | 5-DaHall 1-PDU-02-30-5 | 220 | 30 | 01 | 5 | 220 | 30 | 02 | 5 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-R14 |  |  | 1A-1-4 | 1B-1-4 | U5-1A-07 / 2P 30A | U5-1B-07 / 2P 30A | 5-DaHall 1-PDU-01-30-7 | 5-DaHall 1-PDU-02-30-7 | 220 | 30 | 01 | 7 | 220 | 30 | 02 | 7 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 5.682 | 0 |  |  | 0 | 0 | 무부하 랙
G1101 | 5F-R15 | Cloudflare | 5 | 1A-1-5 | 1B-1-5 | U5-1A-09 / 2P 30A | U5-1B-09 / 2P 30A | 5-DaHall 1-PDU-01-30-9 | 5-DaHall 1-PDU-02-30-9 | 220 | 30 | 01 | 9 | 220 | 30 | 02 | 9 | [6 empty] | 12.4089 | 10.4156 | 22.8245 | 1973.1 | 1656 | 2.874 | 3629.1 |  |  | 4.8778 | 0.12218 | 적정함
G1102 | 5F-R16 | Cloudflare | 5 | 1A-1-6 | 1B-1-6 | U5-1A-11 / 2P 30A | U5-1B-11 / 2P 30A | 5-DaHall 1-PDU-01-30-11 | 5-DaHall 1-PDU-02-30-11 | 220 | 30 | 01 | 11 | 220 | 30 | 02 | 11 | [6 empty] | 11.186 | 12.7078 | 23.8938 | 1730.2 | 1978.2 | 0.18 | 3708.4 |  |  | 4.9844 | 0.015591 | 적정함
G1103 | 5F-R17 | Cloudflare | 5 | 1A-1-7 | 1B-1-7 | U5-1A-13 / 2P 30A | U5-1B-13 / 2P 30A | 5-DaHall 1-PDU-01-30-13 | 5-DaHall 1-PDU-02-30-13 | 220 | 30 | 01 | 13 | 220 | 30 | 02 | 13 | [6 empty] | 13.2166 | 10.9951 | 24.2118 | 2058.1 | 1697.8 | 0.604 | 3755.9 |  |  | 5.0483 | -0.048253 | 사용초과 | Cloudflare | G1103
G1104 | 5F-R18 | Cloudflare | 5 | 1A-1-8 | 1B-1-8 | U5-1A-15 / 2P 30A | U5-1B-15 / 2P 30A | 5-DaHall 1-PDU-01-30-15 | 5-DaHall 1-PDU-02-30-15 | 220 | 30 | 01 | 15 | 220 | 30 | 02 | 15 | [6 empty] | 3.1842 | 3.0387 | 6.2229 | 326.6 | 307 | 0 | 633.6 |  |  | 0.85161 | 4.1484 | 적정함
G1105 | 5F-R19 | Cloudflare | 5 | 1A-1-9 | 1B-1-9 | U5-1A-17 / 2P 30A | U5-1B-17 / 2P 30A | 5-DaHall 1-PDU-01-30-17 | 5-DaHall 1-PDU-02-30-17 | 220 | 30 | 01 | 17 | 220 | 30 | 02 | 17 | [6 empty] | 0 | 3.0577 | 3.0577 | 0 | 309.3 | 5.481 | 309.3 |  |  | 0.41573 | 4.5843 | 적정함
G1201 | 번호없음 | Cloudflare | 5 | 1A-2-1 | 1B-2-1 | U5-1A-31 / 2P 30A | U5-1B-31 / 2P 30A | 5-DaHall 1-PDU-01-30-31 | 5-DaHall 1-PDU-02-30-31 | 220 | 30 | 01 | 31 | 220 | 30 | 02 | 31 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA |  | 11.1759 | 11.5619 | 22.7378 | 1821.6 | 1879.7 | #N/A | 3701.3 |  |  | 4.9749 | 0.025134 | 적정함
G1202 | 5F-Q12 | Cloudflare | 5 | 1A-2-2 | 1B-2-2 | U5-1A-33 / 2P 30A | U5-1B-33 / 2P 30A | 5-DaHall 1-PDU-01-30-33 | 5-DaHall 1-PDU-02-30-33 | 220 | 30 | 01 | 33 | 220 | 30 | 02 | 33 | [6 empty] | 9.8387 | 11.5925 | 21.4312 | 1603 | 1896.6 | #N/A | 3499.6 |  |  | 4.7038 | 0.29624 | 적정함
G1203 | 5F-Q13 | Cloudflare | 5 | 1A-2-3 | 1B-2-3 | U5-1A-35 / 2P 30A | U5-1B-35 / 2P 30A | 5-DaHall 1-PDU-01-30-35 | 5-DaHall 1-PDU-02-30-35 | 220 | 30 | 01 | 35 | 220 | 30 | 02 | 35 | [6 empty] | 11.6822 | 9.714 | 21.3962 | 1917 | 1591.9 | #N/A | 3508.9 |  |  | 4.7163 | 0.28374 | 적정함
G1204 | 5F-Q14 | Cloudflare | 5 | 1A-2-4 | 1B-2-4 | U5-1A-37 / 2P 30A | U5-1B-37 / 2P 30A | 5-DaHall 1-PDU-01-30-37 | 5-DaHall 1-PDU-02-30-37 | 220 | 30 | 01 | 37 | 220 | 30 | 02 | 37 | [6 empty] | 9.5743 | 11.4477 | 21.022 | 1567.9 | 1877.2 | #N/A | 3445.1 |  |  | 4.6305 | 0.36949 | 적정함
G1205 | 5F-Q15 | Cloudflare | 5 | 1A-2-5 | 1B-2-5 | U5-1A-39 / 2P 30A | U5-1B-39 / 2P 30A | 5-DaHall 1-PDU-01-30-39 | 5-DaHall 1-PDU-02-30-39 | 220 | 30 | 01 | 39 | 220 | 30 | 02 | 39 | [6 empty] | 11.7622 | 9.4716 | 21.2338 | 1813.7 | 1451 | #N/A | 3264.7 |  |  | 4.388 | 0.61196 | 적정함
| 5F-Q16 |  |  | 1A-2-6 | 1B-2-6 | U5-1A-41 / 2P 30A | U5-1B-41 / 2P 30A | 5-DaHall 1-PDU-01-30-41 | 5-DaHall 1-PDU-02-30-41 | 220 | 30 | 01 | 41 | 220 | 30 | 02 | 41 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-Q17 |  |  | 1A-2-7 | 1B-2-7 | U5-1A-43 / 2P 30A | U5-1B-43 / 2P 30A | 5-DaHall 1-PDU-01-30-43 | 5-DaHall 1-PDU-02-30-43 | 220 | 30 | 01 | 43 | 220 | 30 | 02 | 43 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-Q18 |  |  | 1A-2-8 | 1B-2-8 | U5-1A-45 / 2P 30A | U5-1B-45 / 2P 30A | 5-DaHall 1-PDU-01-30-45 | 5-DaHall 1-PDU-02-30-45 | 220 | 30 | 01 | 45 | 220 | 30 | 02 | 45 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-Q19 |  |  | 1A-2-9 | 1B-2-9 | U5-1A-47 / 2P 30A | U5-1B-47 / 2P 30A | 5-DaHall 1-PDU-01-30-47 | 5-DaHall 1-PDU-02-30-47 | 220 | 30 | 01 | 47 | 220 | 30 | 02 | 47 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  |  | 0 | 0 | 무부하 랙
G2101 | 5F-P-12 | LG U Plus | 2.2 | 1A-1-10 | 1B-1-10 | U5-1A-19 / 2P 30A | U5-1B-19 / 2P 30A | 5-DaHall 1-PDU-01-30-19 | 5-DaHall 1-PDU-02-30-19 | 220 | 30 | 01 | 19 | 220 | 30 | 02 | 19 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 1.0387 | 0 | 1.0387 | 127.6 | 0 | 5.171 | 127.6 | 구글104 |  | 0.17151 | 2.0285 | 적정함
G2102 | 5F-P-13 | LG U Plus | 2.2 | 1A-1-11 | 1B-1-11 | U5-1A-21 / 2P 30A | U5-1B-21 / 2P 30A | 5-DaHall 1-PDU-01-30-21 | 5-DaHall 1-PDU-02-30-21 | 220 | 30 | 01 | 21 | 220 | 30 | 02 | 21 | [6 empty] | 1.4715 | 1.6336 | 3.1052 | 192 | 226.5 | 4.986 | 418.5 | 구글103 |  | 0.5625 | 1.6375 | 적정함
G2103 | 5F-P-14 | LG U Plus | 2.2 | 1A-1-12 | 1B-1-12 | U5-1A-23 / 2P 30A | U5-1B-23 / 2P 30A | 5-DaHall 1-PDU-01-30-23 | 5-DaHall 1-PDU-02-30-23 | 220 | 30 | 01 | 23 | 220 | 30 | 02 | 23 | [6 empty] | 1.5393 | 1.3191 | 2.8584 | 233.9 | 199.1 | 0 | 433 | 구글102 |  | 0.58199 | 1.618 | 적정함
G2104 | 5F-P-15 | LG U Plus | 2.2 | 1A-1-13 | 1B-1-13 | U5-1A-25 / 2P 30A | U5-1B-25 / 2P 30A | 5-DaHall 1-PDU-01-30-25 | 5-DaHall 1-PDU-02-30-25 | 220 | 30 | 01 | 25 | 220 | 30 | 02 | 25 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 구글101 |  | 0 | 2.2 | 무부하 랙
| 번호없음 |  |  | 1A-4-1 |  | U5-1A-42 / 2P 30A |  | 5-DaHall 1-PDU-01-30-42 |  | 220 | 30 | 01 | 42 |  |  |  |  | U5-1A 4P 300A |  | LV-5A #01 3P 320A |  | TR-5A 1000KVA |  | 0 |  | 0 | 0 |  | #N/A | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-O12 |  |  | 1A-4-2 | 1B-4-2 | U5-1A-44 / 2P 30A | U5-1B-44 / 2P 30A | 5-DaHall 1-PDU-01-30-44 | 5-DaHall 1-PDU-02-30-44 | 220 | 30 | 01 | 44 | 220 | 30 | 02 | 44 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  |  | 0 | 0 | 무부하 랙
G2203 | 5F-O-14 | LG U Plus | 2.2 | 1A-2-12 | 1B-2-12 | U5-1A-04 / 2P 30A | U5-1B-04 / 2P 30A | 5-DaHall 1-PDU-01-30-4 | 5-DaHall 1-PDU-02-30-4 | 220 | 30 | 01 | 4 | 220 | 30 | 02 | 4 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 구글202 |  | 0 | 2.2 | 무부하 랙
G2204 | 5F-O-15 | LG U Plus | 2.2 | 1A-2-13 | 1B-2-13 | U5-1A-06 / 2P 30A | U5-1B-06 / 2P 30A | 5-DaHall 1-PDU-01-30-6 | 5-DaHall 1-PDU-02-30-6 | 220 | 30 | 01 | 6 | 220 | 30 | 02 | 6 | [6 empty] | 1.5779 | 1.308 | 2.886 | 232.1 | 194.1 | 5.531 | 426.2 | 구글201 |  | 0.57285 | 1.6272 | 적정함
| 시스템박스 | LG U Plus |  | 1A-2-15 |  | U5-1A-10 / 2P 30A |  | 5-DaHall 1-PDU-01-30-10 |  | 220 | 30 | 01 | 10 | [10 empty] | 0 |  | 0 | 0 |  | 0 | 0 | 구글 |  | 0 | 0 | 무부하 랙
| 지문인식기 | LG U Plus |  |  | 1B-2-15 |  | U5-1B-10 / 2P 30A |  | 5-DaHall 1-PDU-02-30-10 |  |  |  |  | 220 | 30 | 02 | 10 |  | U5-1B 4P 300A |  | LV-5B #01 3P 320A |  |  |  | 0 | 0 |  | 0 | 1.347 | 0 | 구글 |  | 0 | 0 | 무부하 랙
G3101 | 5F-M-04 | Vodafone Enterprise Global Limited | 2.2 | [22 empty] | 0 |  |  |  | 0 | 보다폰#3 |  | 0 | 2.2 | 무부하 랙
G3102 | 5F-M-05 | Vodafone Enterprise Global Limited | 2.2 | - | - | U5-1A-50 / 2P 30A | U5-1B-50 / 2P 30A | 5-DaHall 1-PDU-01-30-50 | 5-DaHall 1-PDU-02-30-50 | 220 | 30 | 01 | 50 | 220 | 30 | 02 | 50 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | 보다폰#2 | 1A-4-5 | 0 | 2.2 | 무부하 랙
G3103 | 5F-M-06 | Vodafone Enterprise Global Limited | 2.2 | - | - | U5-1A-3P-02 / 3P 60A | U5-1B-3P-02 / 3P 60A | 5-DaHall 1-PDU-01-60-2 | 5-DaHall 1-PDU-02-60-2 | 380 | 60 | 01 | 2 | 380 | 60 | 02 | 2 | [6 empty] | 1.3161 | 1.3873 | 5.5409 | 33.9 | 33.8 | 0 | 67.7 | 보다폰 정류기 |  | 0.090995 | 2.109 | 적정함
|  |  |  | - | - | U5-1A-48 / 2P 30A | U5-1B-48 / 2P 30A | 5-DaHall 1-PDU-01-30-48 | 5-DaHall 1-PDU-02-30-48 | 220 | 30 | 01 | 48 | 220 | 30 | 02 | 48 | [6 empty] | 1.7327 | 1.1048 |  | 278.1 | 179.7 | #N/A | 457.8 | 보다폰#1 | 1A-4-4 | 0.61532 | -0.61532 | 사용초과 | 0 | 0
| 번호없음 |  |  | 2A-5-1 | 2B-5-1 | U5-2A-21 / 2P 30A | U5-2B-21 / 2P 30A | 5-DaHall 1-PDU-03-30-21 | 5-DaHall 1-PDU-04-30-21 | 220 | 30 | 03 | 21 | 220 | 30 | 04 | 21 | U5-2A 4P 300A | U5-2B 4P 300A | LV-5A #02 3P 320A | LV-5B #02 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 |  | 0 | OFF |  | 0 | 0 | 무부하 랙
| 5F-N12 |  |  | 2A-5-2 | 2B-5-2 | U5-2A-23 / 2P 30A | U5-2B-23 / 2P 30A | 5-DaHall 1-PDU-03-30-23 | 5-DaHall 1-PDU-04-30-23 | 220 | 30 | 03 | 23 | 220 | 30 | 04 | 23 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-N13 |  |  | 2A-5-3 | 2B-5-3 | U5-2A-25 / 2P 30A | U5-2B-25 / 2P 30A | 5-DaHall 1-PDU-03-30-25 | 5-DaHall 1-PDU-04-30-25 | 220 | 30 | 03 | 25 | 220 | 30 | 04 | 25 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-N14 |  |  | 2A-5-4 | 2B-5-4 | U5-2A-27 / 2P 30A | U5-2B-27 / 2P 30A | 5-DaHall 1-PDU-03-30-27 | 5-DaHall 1-PDU-04-30-27 | 220 | 30 | 03 | 27 | 220 | 30 | 04 | 27 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-N15 |  |  | 2A-5-5 | 2B-5-5 | U5-2A-29 / 2P 30A | U5-2B-29 / 2P 30A | 5-DaHall 1-PDU-03-30-29 | 5-DaHall 1-PDU-04-30-29 | 220 | 30 | 03 | 29 | 220 | 30 | 04 | 29 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-N16 |  |  | 2A-5-6 | 2B-5-6 | U5-2A-31 / 2P 30A | U5-2B-31 / 2P 30A | 5-DaHall 1-PDU-03-30-31 | 5-DaHall 1-PDU-04-30-31 | 220 | 30 | 03 | 31 | 220 | 30 | 04 | 31 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-N17 |  |  | 2A-5-7 | 2B-5-7 | U5-2A-33 / 2P 30A | U5-2B-33 / 2P 30A | 5-DaHall 1-PDU-03-30-33 | 5-DaHall 1-PDU-04-30-33 | 220 | 30 | 03 | 33 | 220 | 30 | 04 | 33 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-O16 |  |  | 2A-4-6 | 2B-4-6 | U5-2A-01 / 2P 30A | U5-2B-01 / 2P 30A | 5-DaHall 1-PDU-03-30-1 | 5-DaHall 1-PDU-04-30-1 | 220 | 30 | 03 | 1 | 220 | 30 | 04 | 1 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-O17 |  |  | 2A-4-7 | 2B-4-7 | U5-2A-03 / 2P 30A | U5-2B-03 / 2P 30A | 5-DaHall 1-PDU-03-30-3 | 5-DaHall 1-PDU-04-30-3 | 220 | 30 | 03 | 3 | 220 | 30 | 04 | 3 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 번호없음 |  |  | 1A-3-1 | 1B-3-1 | U5-1A-12 / 2P 30A | U5-1B-12 / 2P 30A | 5-DaHall 1-PDU-01-30-12 | 5-DaHall 1-PDU-02-30-12 | 220 | 30 | 01 | 12 | 220 | 30 | 02 | 12 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 |  | 0 | OFF |  | 0 | 0 | 무부하 랙
| 5F-P12 |  |  | 1A-3-2 | 1B-3-2 | U5-1A-14 / 2P 30A | U5-1B-14 / 2P 30A | 5-DaHall 1-PDU-01-30-14 | 5-DaHall 1-PDU-02-30-14 | 220 | 30 | 01 | 14 | 220 | 30 | 02 | 14 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-P13 |  |  | 1A-3-3 | 1B-3-3 | U5-1A-16 / 2P 30A | U5-1B-16 / 2P 30A | 5-DaHall 1-PDU-01-30-16 | 5-DaHall 1-PDU-02-30-16 | 220 | 30 | 01 | 16 | 220 | 30 | 02 | 16 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-P14 |  |  | 1A-3-4 | 1B-3-4 | U5-1A-18 / 2P 30A | U5-1B-18 / 2P 30A | 5-DaHall 1-PDU-01-30-18 | 5-DaHall 1-PDU-02-30-18 | 220 | 30 | 01 | 18 | 220 | 30 | 02 | 18 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-P15 |  |  | 1A-3-5 | 1B-3-5 | U5-1A-20 / 2P 30A | U5-1B-20 / 2P 30A | 5-DaHall 1-PDU-01-30-20 | 5-DaHall 1-PDU-02-30-20 | 220 | 30 | 01 | 20 | 220 | 30 | 02 | 20 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-P16 |  |  | 1A-3-6 | 1B-3-6 | U5-1A-22 / 2P 30A | U5-1B-22 / 2P 30A | 5-DaHall 1-PDU-01-30-22 | 5-DaHall 1-PDU-02-30-22 | 220 | 30 | 01 | 22 | 220 | 30 | 02 | 22 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-P17 |  |  | 1A-3-7 | 1B-3-7 | U5-1A-24 / 2P 30A | U5-1B-24 / 2P 30A | 5-DaHall 1-PDU-01-30-24 | 5-DaHall 1-PDU-02-30-24 | 220 | 30 | 01 | 24 | 220 | 30 | 02 | 24 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-P18 |  |  | 1A-3-8 | 1B-3-8 | U5-1A-26 / 2P 30A | U5-1B-26 / 2P 30A | 5-DaHall 1-PDU-01-30-26 | 5-DaHall 1-PDU-02-30-26 | 220 | 30 | 01 | 26 | 220 | 30 | 02 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-P19 |  |  | 1A-3-9 | 1B-3-9 | U5-1A-28 / 2P 30A | U5-1B-28 / 2P 30A | 5-DaHall 1-PDU-01-30-28 | 5-DaHall 1-PDU-02-30-28 | 220 | 30 | 01 | 28 | 220 | 30 | 02 | 28 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-P20 |  |  | 1A-3-10 | 1B-3-10 | U5-1A-30 / 2P 30A | U5-1B-30 / 2P 30A | 5-DaHall 1-PDU-01-30-30 | 5-DaHall 1-PDU-02-30-30 | 220 | 30 | 01 | 30 | 220 | 30 | 02 | 30 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-P21 |  |  | 1A-3-11 | 1B-3-11 | U5-1A-32 / 2P 30A | U5-1B-32 / 2P 30A | 5-DaHall 1-PDU-01-30-32 | 5-DaHall 1-PDU-02-30-32 | 220 | 30 | 01 | 32 | 220 | 30 | 02 | 32 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-P22 |  |  | 1A-3-12 | 1B-3-12 | U5-1A-34 / 2P 30A | U5-1B-34 / 2P 30A | 5-DaHall 1-PDU-01-30-34 | 5-DaHall 1-PDU-02-30-34 | 220 | 30 | 01 | 34 | 220 | 30 | 02 | 34 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-P23 |  |  | 1A-3-13 | 1B-3-13 | U5-1A-36 / 2P 30A | U5-1B-36 / 2P 30A | 5-DaHall 1-PDU-01-30-36 | 5-DaHall 1-PDU-02-30-36 | 220 | 30 | 01 | 36 | 220 | 30 | 02 | 36 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-P24 |  |  | 1A-3-14 | 1B-3-14 | U5-1A-38 / 2P 30A | U5-1B-38 / 2P 30A | 5-DaHall 1-PDU-01-30-38 | 5-DaHall 1-PDU-02-30-38 | 220 | 30 | 01 | 38 | 220 | 30 | 02 | 38 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 번호없음 |  |  |  | 1B-3-15 |  | U5-1B-40 / 2P 30A |  | 5-DaHall 1-PDU-02-30-40 |  |  |  |  | 220 | 30 | 02 | 40 | [7 empty] | 0 | 0 |  | 0 |  | 0 | 미구축 |  | 0 | 0 | 무부하 랙
| 5F-Q20 |  |  | 1A-2-10 | 1B-2-10 | U5-1A-49 / 2P 30A | U5-1B-49 / 2P 30A | 5-DaHall 1-PDU-01-30-49 | 5-DaHall 1-PDU-02-30-49 | 220 | 30 | 01 | 49 | 220 | 30 | 02 | 49 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-Q21 |  |  | 1A-2-11 | 1B-2-11 | U5-1A-02 / 2P 30A | U5-1B-02 / 2P 30A | 5-DaHall 1-PDU-01-30-2 | 5-DaHall 1-PDU-02-30-2 | 220 | 30 | 01 | 2 | 220 | 30 | 02 | 2 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-Q24 |  |  | 1A-2-14 | 1B-2-14 | U5-1A-08 / 2P 30A | U5-1B-08 / 2P 30A | 5-DaHall 1-PDU-01-30-8 | 5-DaHall 1-PDU-02-30-8 | 220 | 30 | 01 | 8 | 220 | 30 | 02 | 8 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 5F-R24 |  |  | 1A-1-14 | 1B-1-14 | U5-1A-27 / 2P 30A | U5-1B-27 / 2P 30A | 5-DaHall 1-PDU-01-30-27 | 5-DaHall 1-PDU-02-30-27 | 220 | 30 | 01 | 27 | 220 | 30 | 02 | 27 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 무부하 랙
| 번호없음 |  |  | 1A-1-15 | 1B-1-15 | U5-1A-29 / 2P 30A | U5-1B-29 / 2P 30A | 5-DaHall 1-PDU-01-30-29 | 5-DaHall 1-PDU-02-30-29 | 220 | 30 | 01 | 29 | 220 | 30 | 02 | 29 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | OFF |  | 0 | 0 | 무부하 랙
[7 empty] | PDU(B)-2-32 / 3P 20A |  | 5-DaHall 1-PDU-14-20-32 |  |  |  |  | 220 | 20 | 14 | 32 |  | PDU(B)-2 4P 150A |  | UPS출력 배전반(B), #04 3P 150A |  | TR-5B 1000KVA |  | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
| pacnet 내 분전반2식 | 5-DaHall 1-PDU-17 싱텔 분전반(A) | 22 | - | - | - | - |  |  |  |  | - | - |  |  | - | - | PDU-08-A 4P 200A |  | UPS출력 배전반(A), #08 3P 200A |  | TR-5A 1000KVA |  | 15.2235 |  | 15.2235 |  |  |  |  | 싱텔 PDU 월간 계측값 입력 필요 |  | 0 | 22 | 무부하 랙
|  | 5-DaHall 1-PDU-18 싱텔 분전반(B) |  | - | - | - | - |  |  |  |  | - | - |  |  | - | - |  | PDU-08-B 4P 200A |  | UPS출력 배전반(B), #08 3P 200A |  | TR-5B 1000KVA |  | 11.0171 | 11.0171 | [6 empty] | 0 | 0 | 무부하 랙
| 싱텔 | 싱텔 SKB CWDM |  | 싱텔 SKB CWDM A전원 | 싱텔 SKB CWDM B전원 | PDU(A)-3-13 / 2P 30A | PDU(B)-3-13 / 2P 30A | 5-DaHall 1-PDU-15-30-13 | 5-DaHall 1-PDU-16-30-13 | 220 | 30 | 15 | 13 | 220 | 30 | 16 | 13 | PDU(A)-3 4P 300A | PDU(B)-3 4P 300A | UPS출력 배전반(A), #01 3P 300A | UPS출력 배전반(B), #01, 3P 300A | TR-5A 1000KVA | TR-5B 1000KVA | 0.61654 | 1.6658 | 2.2823 | 84.8 | 271.3 | 0.503 | 356.1 |  |  | 0.47863 | -0.47863 | 사용초과 | 싱텔 SKB CWDM | 0
|  | single-2 |  | PUD(A)-2-21 |  | PDU(A)-3-23 / 2P 20A |  | 5-DaHall 1-PDU-15-20-23 |  | 220 | 20 | 15 | 23 | [10 empty] | 2.3094 |  | 2.3094 | 362.5 |  | 0.497 | 362.5 |  |  | 0.48723 | -0.48723 | 사용초과 | single-2 | 0
|  | single-2 |  | PUD(A)-2-27 |  | PDU(A)-3-29 / 2P 20A |  | 5-DaHall 1-PDU-15-20-29 |  | 220 | 20 | 15 | 29 | [10 empty] | 0.36265 |  | 0.36265 | 22.9 |  | 0.036 | 22.9 |  |  | 0.03078 | -0.03078 | 사용초과 | single-2 | 0
|  | KT Rack #2 (소형 임시정류기) |  |  | KT Rack #2 (소형 임시정류기) |  | PDU(B)-3-15 / 2P 20A |  | 5-DaHall 1-PDU-16-20-15 |  |  |  |  | 220 | 20 | 16 | 15 |  | PDU(B)-3 4P 300A |  | UPS출력 배전반(B), #01 3P 300A |  | TR-5B 1000KVA |  | 2.4403 | 2.4403 |  | 392 | 0.734 | 392 |  |  | 0.52688 | -0.52688 | 사용초과 | KT Rack #2 (소형 임시정류기) | 0
|  | KT Rack #3 (소형 임시정류기) |  |  | KT Rack #3 (소형 임시정류기) |  | PDU(B)-3-17 / 2P 20A |  | 5-DaHall 1-PDU-16-20-17 |  |  |  |  | 220 | 20 | 16 | 17 | [7 empty] | 1.5901 | 1.5901 |  | 249.3 | 0.741 | 249.3 |  |  | 0.33508 | -0.33508 | 사용초과 | KT Rack #3 (소형 임시정류기) | 0
|  | KT Rack #4 (소형 임시정류기) |  |  | KT Rack #4 (소형 임시정류기) |  | PDU(B)-3-19 / 2P 20A |  | 5-DaHall 1-PDU-16-20-19 |  |  |  |  | 220 | 20 | 16 | 19 | [7 empty] | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
|  | single-2 |  |  | DACOM EOS |  | PDU(B)-3-23 / 2P 20A |  | 5-DaHall 1-PDU-16-20-23 |  |  |  |  | 220 | 20 | 16 | 23 | [7 empty] | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 무부하 랙
|  | single-2 |  |  |  |  | PDU(B)-3-25 / 2P 20A |  | 5-DaHall 1-PDU-16-20-25 |  |  |  |  | 220 | 20 | 16 | 25 | [7 empty] | 0.42399 | 0.42399 |  | 59.2 | 0.093 | 59.2 |  |  | 0.07957 | -0.07957 | 사용초과 | single-2 | 0
|  | single-2 |  |  | SKB2.5G전용 PDU B3 27 |  | PDU(B)-3-27 / 2P 20A |  | 5-DaHall 1-PDU-16-20-27 |  |  |  |  | 220 | 20 | 16 | 27 | [7 empty] | 1.4873 | 1.4873 |  | 232 | 0.324 | 232 |  |  | 0.31183 | -0.31183 | 사용초과 | single-2 | 0
|  | single-2 |  |  | 데이콤 AC전원 |  | PDU(B)-3-29 / 2P 20A |  | 5-DaHall 1-PDU-16-20-29 |  |  |  |  | 220 | 20 | 16 | 29 | [7 empty] | 2.2198 | 2.2198 |  | 349.2 | 0.482 | 349.2 |  |  | 0.46935 | -0.46935 | 사용초과 | single-2 | 0
|  | single-2 |  |  | kt mspp 전원 |  | PDU(B)-3-24 / 2P 20A |  | 5-DaHall 1-PDU-16-20-24 |  |  |  |  | 220 | 20 | 16 | 24 | [7 empty] | 1.4604 | 1.4604 |  | 218.4 | 0.439 | 218.4 |  |  | 0.29355 | -0.29355 | 사용초과 | single-2 | 0
|  | single-2 |  |  | TNSI A |  | PDU(B)-3-30 / 2P 20A |  | 5-DaHall 1-PDU-16-20-30 |  |  |  |  | 220 | 20 | 16 | 30 | [7 empty] | 0.49261 | 0.49261 |  | 42.2 | 0.064 | 42.2 |  |  | 0.05672 | -0.05672 | 사용초과 | single-2 | 0
| 텔스트라 | Telstra | 80 | C2C 정류기 B1 | C2C 정류기 A1 | - | - |  |  |  |  | - | - | 380 |  | - | - | - | - | UPS출력 배전반(A), #12 3P 100A | UPS출력 배전반(B), #12 3P 100A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 |  |  | 0 |  | 별도 측정 필요 |  | 0 | 80 | 무부하 랙
|  | Telstra |  | C2C 정류기 B2 | C2C 정류기 A2 | - | - |  |  |  |  | - | - | 380 |  | - | - | - | - | UPS출력 배전반(A), #11 3P 100A | UPS출력 배전반(B), #11 3P 100A |  |  | 0 | 0 | 0 |  |  | 0 |  | 별도 측정 필요 |  | 0 | 0 | 무부하 랙
|  | Telstra |  | AC PDU-3#A |  | PDU(A)-3-01(3상) / 3P 50A |  | 5-DaHall 1-PDU-15-50-1 |  | 380 | 50 | 15 | 1 |  |  |  |  | PDU(A)-3 4P 300A |  | UPS출력 배전반(A), #01 3P 300A |  |  |  | 15.216 |  | 23.3994 | 2224.1 |  | 3.012 | 2224.1 |  |  | 2.9894 | -2.9894 | 사용초과 | Telstra | 0
|  | Telstra |  | AC PDU(A)-3A |  | PDU(A)-3-02(3상) / 3P 50A |  | 5-DaHall 1-PDU-15-50-2 |  | 380 | 50 | 15 | 2 | [10 empty] | 8.1834 |  |  | 1292.1 |  | 1.779 | 1292.1 |  |  | 1.7367 | -1.7367 | 사용초과 | Telstra | 0
|  | Telstra |  |  | AC PDU-3#B |  | PDU(B)-3-01(3상) / 3P 50A |  | 5-DaHall 1-PDU-16-50-1 |  |  |  |  | 380 | 50 | 16 | 1 |  | PDU(B)-3 4P 300A |  | UPS출력 배전반(B), #01 3P 300A |  |  |  | 12.1025 | 20.2651 |  | 1679.8 | 2.273 | 1679.8 |  |  | 2.2578 | -2.2578 | 사용초과 | Telstra | 0
|  | Telstra |  |  | PDU(B)-3A |  | PDU(B)-3-02(3상) / 3P 50A |  | 5-DaHall 1-PDU-16-50-2 |  |  |  |  | 380 | 50 | 16 | 2 | [7 empty] | 8.1626 |  |  | 1289.6 | 1.751 | 1289.6 |  |  | 1.7333 | -1.7333 | 사용초과 | Telstra | 0
|  | Telstra | [6 empty] | 5-DaHall 1-PDU-16-20-21 |  |  |  |  | 220 | 20 | 16 | 21 | [7 empty] | 0.29432 | 0.29432 |  | 18.4 | 0.064 | 18.4 |  |  | 0.024731 | -0.024731 | 사용초과 | Telstra | 0
| 신규 BMS(4F TPS실) Rack |  | 2.2 | [5 empty] | 5-DaHall 1-PDU-16-50-20 | 220 |  |  |  | 220 | 50 | 16 | 20 | [7 empty] | 0.59852 | 0.59852 |  | 80.8 | 0.122 | 80.8 |  |  | 0.1086 | 2.0914 | 적정함
| 신규 BMS(5F TPS실) Rack |  | 2.2 | [5 empty] | 5-DaHall 1-PDU-16-50-22 | 220 |  |  |  | 220 | 50 | 16 | 22 | [7 empty] | 0.58994 | 0.58994 |  | 80.1 | 0.115 | 80.1 |  |  | 0.10766 | 2.0923 | 적정함
[25 empty] | 합 계 | 630.6109 | 81.8131 | 75.8006
오차

## 4층_랙별_계통 및_부하량
4층 랙별 전기공급계통 | [46 empty] | 미디어꾼 | 계약용량 | 시간당 전력량 | 남은 전력량 | 전력초과여부 | 피크값 | 평균값 | 0
[7 empty] | 층/분전반명/차단기용량/차단기번호 | [40 empty] | 0 | 0 | 0 | 미사용 랙 | 0 | #DIV/0!
열 구분 (부스바명) | DEKR No. | 고객명 | 계약용량 | 세종 관리 Name (IDC 관리명). | 차단기 정보 |  | DEK Naming Convention 적용 명칭(NEW) |  | DEK차단기 정보수정 | [7 empty] | 분전반 정보 |  | 배전반 정보 |  | TR 정보 |  | 월 평균 전류 |  |  | 월 유효전력량 |  | kW(전월최대유효전력) | 월간 사용전력량[kwh] | 비 고 |  |  | 시간당 전력량 [kwh] | 남은 전력량 | 전력초과여부 | 사용초과 고객 수 | 적정함 | 무부하 랙 | 열 구분 (부스바명) | DEKR No. | 고객명 | 계약용량 | DEK Naming Convention 적용 명칭(NEW) |  | 월 평균 전류 |  |  | 월 유효전력량 |  | kW(전월최대유효전력) | 월간 사용전력량[kWh] | 비 고
|  |  | kW |  | 상 | 하 | 상 | 하 | 상 |  |  |  | 하 |  |  |  | 상 | 하 | 상 | 하 | 상 | 하 | 상 | 하 | 합계 | 상 | 하 |  |  |  | 합계 |  |  |  |  | 165 | 29 | 101 |  |  |  | kW | 상 | 하 | 상 | 하 | 합계 | 상 | 하
정류기 | 4-Sejong-Rect-1 | Sejong Telecom Inc. | 4 | 정류기1호기 | KEN 1 #01 / 4P 100A |  | 4-DaHall 1-PDU-02-100-1 |  | 380 | 100 | 02 | 1 |  |  |  |  | KEN 1 4P 300A |  | LV-4B #01 (3P 320A) |  | TR-4B (1000kVA) |  | 2.3258 |  | 2.3258 | 227.7 |  | 0.391 | 227.7 |  | 2.3 | 0.025781 | 0.30605 | 3.694 | 적정함 |  |  |  | 찾을 수 없음 |  |  |  | 찾을 수 없음 |  | 찾을 수 없음
| 4-Sejong-Rect-2 | Sejong Telecom Inc. | 4 | 정류기2호기 |  | KEN 8 #01 / 4P 100A |  | 4-DaHall 1-PDU-01-100-1 |  |  |  |  | 380 | 100 | 01 | 1 |  | KEN 8 4P 300A |  | LV-4A #01 (3P 320A) |  | TR-4A (1000kVA) |  | 4.0163 | 4.0163 |  | 450.8 | 0.696 | 450.8 |  | 3.2 | 0.81634 | 0.60591 | 3.3941 | 적정함
항온항습기 |  | CRAC 4E-1호기(20RT) |  | CRAC 4E-1호기(20RT) | KEN 7 #02 / 4P 200A |  | 4-DaHall 1-PDU-10-200-2 |  | 380 | 200 | 10 | 2 |  |  |  |  | KEN 7 4P 300A |  | LV-4B #05 (3P 320A) |  | TR-4B (1000kVA) |  | 89.0837 |  | 89.0837 | 13236.5 |  | 19.682 | 13236.5 |  | 83.5 | 5.5837 | 17.791 | -17.791 | 사용초과
|  | CRAC 4E-2호기(20RT) |  | CRAC 4E-2호기(20RT) | KEN 7 #03 / 4P 200A |  | 4-DaHall 1-PDU-10-200-3 |  | 380 | 200 | 10 | 3 | [10 empty] | 44.9647 |  | 44.9647 | 6847.3 |  | 17.48 | 6847.3 |  | 43.8 | 1.1647 | 9.2034 | -9.2034 | 사용초과
101~111Bay /POP B열 | G4601-G4611 | Sejong Telecom Inc. | 17.6 | 세종인터넷 | KEN 1 #03 / 2P 100A | KEN 8 #03 / 2P 100A | 4-DaHall 1-PDU-02-100-3 | 4-DaHall 1-PDU-01-100-3 | 220 | 100 | 02 | 3 | 220 | 100 | 01 | 3 | KEN 1 4P 300A | KEN 8 4P 300A | LV-4B #01 (3P 320A) | LV-4A #01 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 32.4505 | 34.2061 | 66.6565 | 5102.3 | 5395 | 14.317 | 10497.3 | 세종 Core Room | 68.1 | -1.4435 | 14.1093 | 3.4907 | 적정함
201~211Bay /POP C열 | G4501-G4511 | Sejong Telecom Inc. | 17.6 | 세종인터넷 | KEN 1 #04 / 2P 100A | KEN 8 #04 / 2P 100A | 4-DaHall 1-PDU-02-100-4 | 4-DaHall 1-PDU-01-100-4 | 220 | 100 | 02 | 4 | 220 | 100 | 01 | 4 | [6 empty] | 35.8779 | 37.1317 | 73.0096 | 5538.1 | 5765.4 | 15.279 | 11303.5 |  | 74.1 | -1.0904 | 15.1929 | 2.4071 | 적정함
301~311Bay /POP D열 | G4401-G4411 | Sejong Telecom Inc. | 17.6 | 세종인터넷 | KEN 1 #05 / 2P 100A | KEN 8 #05 / 2P 100A | 4-DaHall 1-PDU-02-100-5 | 4-DaHall 1-PDU-01-100-5 | 220 | 100 | 02 | 5 | 220 | 100 | 01 | 5 | [6 empty] | 40.9814 | 41.454 | 82.4355 | 6686.9 | 6731.3 | 18.469 | 13418.2 |  | 80.3 | 2.1355 | 18.0352 | -0.43522 | 사용초과
401~411Bay /POP E열 | G4301-G4311 | Sejong Telecom Inc. | 17.6 | 세종인터넷 | KEN 1 #02 / 2P 100A | KEN 8 #02 / 2P 100A | 4-DaHall 1-PDU-02-100-2 | 4-DaHall 1-PDU-01-100-2 | 220 | 100 | 02 | 2 | 220 | 100 | 01 | 2 | [6 empty] | 35.0725 | 37.4027 | 72.4752 | 5510.8 | 5920.3 | 15.489 | 11431.1 |  | 73.6 | -1.1248 | 15.3644 | 2.2356 | 적정함
501~511Bay /POP F열 | G4201-G4211 | Sejong Telecom Inc. | 17.6 | 세종인터넷 | KEN 2 #02 / 2P 100A | KEN 9 #02 / 2P 100A | 4-DaHall 1-PDU-04-100-2 | 4-DaHall 1-PDU-03-100-2 | 220 | 100 | 04 | 2 | 220 | 100 | 03 | 2 | KEN 2 4P 300A | KEN 9 4P 300A | LV-4B #06 (3P 320A) | LV-4A #06 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 39.458 | 32.2014 | 71.6595 | 6295.6 | 5187.4 | 16.236 | 11483 |  | 73.2 | -1.5405 | 15.4341 | 2.1659 | 적정함
601~611Bay /1구역 B열 | G4101-G4111 | Sejong Telecom Inc. | 17.6 | 세종인터넷 | KEN 2 #03 / 2P 100A | KEN 9 #03 / 2P 100A | 4-DaHall 1-PDU-04-100-3 | 4-DaHall 1-PDU-03-100-3 | 220 | 100 | 04 | 3 | 220 | 100 | 03 | 3 | [6 empty] | 28.4812 | 28.08 | 56.5612 | 4603.6 | 4489.6 | 12.522 | 9093.2 |  | 57.5 | -0.93882 | 12.222 | 5.378 | 적정함
[30 empty] | 철거 ('21.10월) | 0 | 0 | 0 | 0 | 무부하 랙
K 3-1 | G1101 | Media Player | 13.2 | 4F Cage2-R15 | KEN 6 #02 / 2P 100A | KEN 13 #02 / 2P 100A | 4-DaHall 1-PDU-08-100-2 | 4-DaHall 1-PDU-07-100-2 | 220 | 100 | 08 | 2 | 220 | 100 | 07 | 2 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 33.2786 | 33.5524 | 66.831 | 5247.1 | 5316.5 | 15.074 | 10563.6 | 미디어꾼(구)윈텔) | 67.9 | -1.069 | 14.1984 | -0.99839 | 사용초과
| G1102 | Media Player |  | 4F Cage2-R16 | [23 empty] | 15.074 | 10563.6 |  | 0 | 0 | 14.1984 | -14.1984 | 사용초과
| G1103 | Media Player |  | 4F Cage2-R17 | [23 empty] | 15.074 | 10563.6 |  | 0 | 0 | 14.1984 | -14.1984 | 사용초과
| G1104 | Media Player |  | 4F Cage2-R18 | [23 empty] | 15.074 | 10563.6 |  | 0 | 0 | 14.1984 | -14.1984 | 사용초과
| G1105 | Media Player |  | 4F Cage2-R19 | [23 empty] | 15.074 | 10563.6 |  | 0 | 0 | 14.1984 | -14.1984 | 사용초과
| G1106 | Media Player |  | 4F Cage2-R20 | [23 empty] | 15.074 | 10563.6 |  | 0 | 0 | 14.1984 | -14.1984 | 사용초과
K 3-3 | G1201 | Media Player | 6.6 | 4F Cage2-R08 | KEN 6 #06 / 2P 100A | KEN 13 #06 / 2P 100A | 4-DaHall 1-PDU-08-100-6 | 4-DaHall 1-PDU-07-100-6 | 220 | 100 | 08 | 6 | 220 | 100 | 07 | 6 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 12.136 | 15.8815 | 28.0175 | 1711.6 | 2280.3 | 6.172 | 3991.9 | 미디어꾼(구)윈텔) | 28.2 | -0.18253 | 5.3655 | 1.2345 | 적정함
| G1202 | Media Player |  | 4F Cage2-R09 | [23 empty] | 6.172 | 3991.9 |  | 0 | 0 | 5.3655 | -5.3655 | 사용초과
| G1302 | Media Player |  | 4F Cage2-R02 | [23 empty] | 6.172 | 3991.9 |  | 0 | 0 | 5.3655 | -5.3655 | 사용초과
K 3-2 | G1203 | Media Player | 11 | 4F Cage2-R10 | KEN 6 #04 / 2P 100A | KEN 13 #04 / 2P 100A | 4-DaHall 1-PDU-08-100-4 | 4-DaHall 1-PDU-07-100-4 | 220 | 100 | 08 | 4 | 220 | 100 | 07 | 4 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 9.4757 | 10.3815 | 19.8571 | 1483.1 | 1565.4 | 4.317 | 3048.5 | 미디어꾼(구)윈텔) | 20.2 | -0.34286 | 4.0974 | 6.9026 | 적정함
| G1204 | Media Player |  | 4F Cage2-R11 | [23 empty] | 4.317 | 3048.5 |  | 0 | 0 | 4.0974 | -4.0974 | 사용초과
| G1205 | Media Player |  | 4F Cage2-R12 | [23 empty] | 4.317 | 3048.5 |  | 0 | 0 | 4.0974 | -4.0974 | 사용초과
| G1206 | Media Player |  | 4F Cage2-R13 | [23 empty] | 4.317 | 3048.5 |  | 0 | 0 | 4.0974 | -4.0974 | 사용초과
| G1207 | Media Player |  | 4F Cage2-R14 | [23 empty] | 4.317 | 3048.5 |  | 0 | 0 | 4.0974 | -4.0974 | 사용초과
K 3-4 | G1301 | Media Player | 13.2 | 4F Cage2-R01 | KEN 6 #08 / 2P 100A | KEN 13 #08 / 2P 100A | 4-DaHall 1-PDU-08-100-8 | 4-DaHall 1-PDU-07-100-8 | 220 | 100 | 08 | 8 | 220 | 100 | 07 | 8 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 26.6682 | 34.5307 | 61.1989 | 3990.1 | 5348.9 | 14.799 | 9339 | 미디어꾼(구)윈텔) | 61.3 | -0.10114 | 12.5524 | 0.64758 | 적정함
| G1303 | Media Player |  | 4F Cage2-R03 | [23 empty] | 14.799 | 9339 |  | 0 | 0 | 12.5524 | -12.5524 | 사용초과
| G1304 | Media Player |  | 4F Cage2-R04 | [23 empty] | 14.799 | 9339 |  | 0 | 0 | 12.5524 | -12.5524 | 사용초과
| G1305 | Media Player |  | 4F Cage2-R05 | [23 empty] | 14.799 | 9339 |  | 0 | 0 | 12.5524 | -12.5524 | 사용초과
| G1306 | Media Player |  | 4F Cage2-R06 | [23 empty] | 14.799 | 9339 |  | 0 | 0 | 12.5524 | -12.5524 | 사용초과
| G1307 | Media Player |  | 4F Cage2-R07 | [23 empty] | 14.799 | 9339 |  | 0 | 0 | 12.5524 | -12.5524 | 사용초과
K 2-4 | G2103 | Settle Bank Co., Ltd. | 8.8 | 4F Cage3-R16 | KEN 6 #07 / 2P 100A | KEN 13 #07 / 2P 100A | 4-DaHall 1-PDU-08-100-7 | 4-DaHall 1-PDU-07-100-7 | 220 | 100 | 08 | 7 | 220 | 100 | 07 | 7 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 13.0373 | 13.8157 | 26.8529 | 1809.7 | 1920.6 | 5.05 | 3730.3 | 세틀뱅크 | 27.4 | -0.54705 | 5.0138 | 3.7862 | 적정함
| G2104 | Settle Bank Co., Ltd. |  | 4F Cage3-R15 | [23 empty] | 5.05 | 3730.3 |  | 0 | 0 | 5.0138 | -5.0138 | 사용초과
| G2105 | Settle Bank Co., Ltd. |  | 4F Cage3-R14 | [23 empty] | 5.05 | 3730.3 |  | 0 | 0 | 5.0138 | -5.0138 | 사용초과
| G2106 | Settle Bank Co., Ltd. |  | 4F Cage3-R13 | [23 empty] | 5.05 | 3730.3 |  | 0 | 0 | 5.0138 | -5.0138 | 사용초과
K 2-2 | G2201 | Settle Bank Co., Ltd. | 6.6 | 4F Cage3-R12 | KEN 6 #03 / 2P 100A | KEN 13 #03 / 2P 100A | 4-DaHall 1-PDU-08-100-3 | 4-DaHall 1-PDU-07-100-3 | 220 | 100 | 08 | 3 | 220 | 100 | 07 | 3 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 5.3758 | 5.2835 | 10.6593 | 823.9 | 801.5 | 2.298 | 1625.4 | 세틀뱅크 | 10.8 | -0.14073 | 2.1847 | 4.4153 | 적정함
| G2203 | Settle Bank Co., Ltd. |  | 4F Cage3-R10 | [23 empty] | 2.298 | 1625.4 |  | 0 | 0 | 2.1847 | -2.1847 | 사용초과
| G2205 | Settle Bank Co., Ltd. |  | 4F Cage3-R08 | [23 empty] | 2.298 | 1625.4 |  | 0 | 0 | 2.1847 | -2.1847 | 사용초과
K 2-3 | G2202 | Settle Bank Co., Ltd. | 6.6 | 4F Cage3-R11 | KEN 6 #05 / 2P 100A | KEN 13 #05 / 2P 100A | 4-DaHall 1-PDU-08-100-5 | 4-DaHall 1-PDU-07-100-5 | 220 | 100 | 08 | 5 | 220 | 100 | 07 | 5 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 7.4283 | 6.0018 | 13.4301 | 1134.6 | 892 | 2.946 | 2026.6 | 세틀뱅크 | 13.5 | -0.069945 | 2.7239 | 3.8761 | 적정함
| G2204 | Settle Bank Co., Ltd. |  | 4F Cage3-R09 | [23 empty] | 2.946 | 2026.6 |  | 0 | 0 | 2.7239 | -2.7239 | 사용초과
| G2206 | Settle Bank Co., Ltd. |  | 4F Cage3-R07 | [23 empty] | 2.946 | 2026.6 |  | 0 | 0 | 2.7239 | -2.7239 | 사용초과
K 2-1 | G2301 | Settle Bank Co., Ltd. | 13.2 | 4F Cage3-R06 | KEN 6 #01 / 2P 100A | KEN 13 #01 / 2P 100A | 4-DaHall 1-PDU-08-100-1 | 4-DaHall 1-PDU-07-100-1 | 220 | 100 | 08 | 1 | 220 | 100 | 07 | 1 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 22.8002 | 20.5084 | 43.3085 | 3569.5 | 3182.9 | 9.848 | 6752.4 | 세틀뱅크 | 44.2 | -0.89145 | 9.0758 | 4.1242 | 적정함
| G2302 | Settle Bank Co., Ltd. |  | 4F Cage3-R05 | [23 empty] | 9.848 | 6752.4 |  | 0 | 0 | 9.0758 | -9.0758 | 사용초과
| G2303 | Settle Bank Co., Ltd. |  | 4F Cage3-R04 | [23 empty] | 9.848 | 6752.4 |  | 0 | 0 | 9.0758 | -9.0758 | 사용초과
| G2304 | Settle Bank Co., Ltd. |  | 4F Cage3-R03 | [23 empty] | 9.848 | 6752.4 |  | 0 | 0 | 9.0758 | -9.0758 | 사용초과
| G2305 | Settle Bank Co., Ltd. |  | 4F Cage3-R02 | [23 empty] | 9.848 | 6752.4 |  | 0 | 0 | 9.0758 | -9.0758 | 사용초과
| G2306 | Settle Bank Co., Ltd. |  | 4F Cage3-R01 | [23 empty] | 9.848 | 6752.4 |  | 0 | 0 | 9.0758 | -9.0758 | 사용초과
K 1-2 |  |  |  |  | KEN 6 #10 / 2P 100A | KEN 13 #10 / 2P 100A | 4-DaHall 1-PDU-08-100-10 | 4-DaHall 1-PDU-07-100-10 | 220 | 100 | 08 | 10 | 220 | 100 | 07 | 10 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
[28 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
[28 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
K 1-1 | G3201 |  |  |  | KEN 6 #09 / 2P 100A | KEN 13 #09 / 2P 100A | 4-DaHall 1-PDU-08-100-9 | 4-DaHall 1-PDU-07-100-9 | 220 | 100 | 08 | 9 | 220 | 100 | 07 | 9 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Cage 1-1-02 & 03 (총 4회로) | 1.4 | -1.4 | 0 | 0 | 무부하 랙
| G3202 | [26 empty] | 0 | 0 | Café 1-1-01 (2회로) | 0 | 0 | 0 | 0 | 무부하 랙
[31 empty] | 0 | 0 | 0 | 0 | 무부하 랙
[31 empty] | 0 | 0 | 0 | 0 | 무부하 랙
[31 empty] | 0 | 0 | 0 | 0 | 무부하 랙
[31 empty] | 0 | 0 | 0 | 0 | 무부하 랙
[31 empty] | 0 | 0 | 0 | 0 | 무부하 랙
[31 empty] | 0 | 0 | 0 | 0 | 무부하 랙
3구역 S열 | B115 | Media Player | 20.9 | 4F-S20 | KEN 3 #10 / 2P 100A | KEN 10 #10 / 2P 100A | 4-DaHall 1-PDU-06-100-10 | 4-DaHall 1-PDU-05-100-10 | 220 | 100 | 06 | 10 | 220 | 100 | 05 | 10 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 38.5282 | 31.9029 | 70.4311 | 6001.7 | 4916.7 | 15.148 | 10918.4 |  | 70.2 | 0.23113 | 14.6753 | 6.2247 | 적정함
| B116 |  |  | 4F-S19 | [23 empty] | 15.148 | 10918.4 |  | 0 | 0 | 14.6753 | -14.6753 | 사용초과
| B117 | Suntech Solution |  | 4F-S18 | [23 empty] | 15.148 | 10918.4 |  | 0 | 0 | 14.6753 | -14.6753 | 사용초과
| B118 | Suntech Solution |  | 4F-S17 | [23 empty] | 15.148 | 10918.4 |  | 0 | 0 | 14.6753 | -14.6753 | 사용초과
| B119 | Suntech Solution |  | 4F-S16 | [23 empty] | 15.148 | 10918.4 |  | 0 | 0 | 14.6753 | -14.6753 | 사용초과
| B120 | Suntech Solution |  | 4F-S15 | [23 empty] | 15.148 | 10918.4 |  | 0 | 0 | 14.6753 | -14.6753 | 사용초과
| B121 | Suntech Solution |  | 4F-S14 | [23 empty] | 15.148 | 10918.4 |  | 0 | 0 | 14.6753 | -14.6753 | 사용초과
| B122 | Suntech Solution |  | 4F-S13 | [23 empty] | 15.148 | 10918.4 |  | 0 | 0 | 14.6753 | -14.6753 | 사용초과
| B123 | Suntech Solution |  | 4F-S12 | [23 empty] | 15.148 | 10918.4 |  | 0 | 0 | 14.6753 | -14.6753 | 사용초과
| B124 | Suntech Solution |  | 4F-S11 | [23 empty] | 15.148 | 10918.4 |  | 0 | 0 | 14.6753 | -14.6753 | 사용초과
3구역 R열 |  |  |  | 4F-R20 | KEN 3 #9 / 2P 100A | KEN 10 #9 / 2P 100A | 4-DaHall 1-PDU-06-100-9 | 4-DaHall 1-PDU-05-100-9 | 220 | 100 | 06 | 9 | 220 | 100 | 05 | 9 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
|  |  |  | 4F-R19 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
|  |  |  | 4F-R18 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
|  |  |  | 4F-R17 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
|  |  |  | 4F-R16 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
|  |  |  | 4F-R15 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
|  |  |  | 4F-R14 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
|  |  |  | 4F-R13 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
|  |  |  | 4F-R12 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
|  |  |  | 4F-R11 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
3구역 Q열 | B315 |  | 13.2 | 4F-Q20 | KEN 3 #8 / 2P 100A | KEN 10 #8 / 2P 100A | 4-DaHall 1-PDU-06-100-8 | 4-DaHall 1-PDU-05-100-8 | 220 | 100 | 06 | 8 | 220 | 100 | 05 | 8 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 13.8972 | 13.3068 | 27.204 | 2082.2 | 1997.5 | 5.855 | 4079.7 |  | 26 | 1.204 | 5.4835 | 7.7165 | 적정함
| B316 | Suntech Solution |  | 4F-Q19 | [23 empty] | 5.855 | 4079.7 |  | 0 | 0 | 5.4835 | -5.4835 | 사용초과
| B317 | Suntech Solution |  | 4F-Q18 | [23 empty] | 5.855 | 4079.7 |  | 0 | 0 | 5.4835 | -5.4835 | 사용초과
| B318 |  |  | 4F-Q17 | [23 empty] | 5.855 | 4079.7 |  | 0 | 0 | 5.4835 | -5.4835 | 사용초과
| B319 |  |  | 4F-Q16 | [23 empty] | 5.855 | 4079.7 |  | 0 | 0 | 5.4835 | -5.4835 | 사용초과
| B320 |  |  | 4F-Q15 | [23 empty] | 5.855 | 4079.7 |  | 0 | 0 | 5.4835 | -5.4835 | 사용초과
| B321 | Sysone Co., Ltd. |  | 4F-Q14 | [23 empty] | 5.855 | 4079.7 |  | 0 | 0 | 5.4835 | -5.4835 | 사용초과
| B322 | Sysone Co., Ltd. |  | 4F-Q13 | [23 empty] | 5.855 | 4079.7 |  | 0 | 0 | 5.4835 | -5.4835 | 사용초과
| B323 | Sysone Co., Ltd. |  | 4F-Q12 | [23 empty] | 5.855 | 4079.7 |  | 0 | 0 | 5.4835 | -5.4835 | 사용초과
| B324 | Digital Edge Korea |  | 4F-Q11 | [23 empty] | 5.855 | 4079.7 |  | 0 | 0 | 5.4835 | -5.4835 | 사용초과
3구역 P열 | B415 |  | 7.15 | 4F-P20 | KEN 3 #7 / 2P 100A | KEN 10 #7 / 2P 100A | 4-DaHall 1-PDU-06-100-7 | 4-DaHall 1-PDU-05-100-7 | 220 | 100 | 06 | 7 | 220 | 100 | 05 | 7 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 8.5589 | 6.7918 | 15.3507 | 1262.5 | 979 | 3.447 | 2241.5 |  | 15.7 | -0.34928 | 3.0128 | 4.1372 | 적정함
| B416 | DEK, 층간 Patch Cabinet |  | 4F-P19 | [23 empty] | 3.447 | 2241.5 |  | 0 | 0 | 3.0128 | -3.0128 | 사용초과
| B417 |  |  | 4F-P18 | [23 empty] | 3.447 | 2241.5 |  | 0 | 0 | 3.0128 | -3.0128 | 사용초과
| B418 | Sejong Telecom Inc. |  | 4F-P17 | [23 empty] | 3.447 | 2241.5 |  | 0 | 0 | 3.0128 | -3.0128 | 사용초과
| B419 | Sejong Telecom Inc. |  | 4F-P16 | [23 empty] | 3.447 | 2241.5 |  | 0 | 0 | 3.0128 | -3.0128 | 사용초과
| B420 | Digital Edge Korea |  | 4F-P15 | [23 empty] | 3.447 | 2241.5 |  | 0 | 0 | 3.0128 | -3.0128 | 사용초과
| B421 |  |  | 4F-P14 | [23 empty] | 3.447 | 2241.5 |  | 0 | 0 | 3.0128 | -3.0128 | 사용초과
| B422 | Digital Edge Korea |  | 4F-P13 | [23 empty] | 3.447 | 2241.5 |  | 0 | 0 | 3.0128 | -3.0128 | 사용초과
| B423 |  |  | 4F-P12 | [23 empty] | 3.447 | 2241.5 |  | 0 | 0 | 3.0128 | -3.0128 | 사용초과
| B424 |  |  | 4F-P11 | [23 empty] | 3.447 | 2241.5 |  | 0 | 0 | 3.0128 | -3.0128 | 사용초과
3구역 O열 |  |  | 11.55 |  | KEN 3 #6 / 2P 100A | KEN 10 #6 / 2P 100A | 4-DaHall 1-PDU-06-100-6 | 4-DaHall 1-PDU-05-100-6 | 220 | 100 | 06 | 6 | 220 | 100 | 05 | 6 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 0 | 12.8443 | 12.8443 | 0 | 1771.4 | 2.57 | 1771.4 | O #01 | 36.3 | -23.4557 | 2.3809 | 9.1691 | 적정함
[28 empty] | 2.57 | 1771.4 | O #03 | 0 | 0 | 2.3809 | -2.3809 | 사용초과
| B515 |  |  | 4F-O20 | [23 empty] | 2.57 | 1771.4 |  | 0 | 0 | 2.3809 | -2.3809 | 사용초과
| B516 | Ellis Information Technology Co., Ltd. |  | 4F-O19 | [23 empty] | 2.57 | 1771.4 |  | 0 | 0 | 2.3809 | -2.3809 | 사용초과
| B517 | SCG Lab |  | 4F-O18 | [23 empty] | 2.57 | 1771.4 |  | 0 | 0 | 2.3809 | -2.3809 | 사용초과
| B518 | Netoz Co., Ltd. |  | 4F-O17 | [23 empty] | 2.57 | 1771.4 |  | 0 | 0 | 2.3809 | -2.3809 | 사용초과
| B519 | Hi Auto Club Co., Ltd. |  | 4F-O16 | [23 empty] | 2.57 | 1771.4 |  | 0 | 0 | 2.3809 | -2.3809 | 사용초과
| B520 |  |  | 4F-O15 | [23 empty] | 2.57 | 1771.4 |  | 0 | 0 | 2.3809 | -2.3809 | 사용초과
| B521 |  |  | 4F-O14 | [23 empty] | 2.57 | 1771.4 |  | 0 | 0 | 2.3809 | -2.3809 | 사용초과
| B522 | Hi Auto Club Co., Ltd. |  | 4F-O13 | [23 empty] | 2.57 | 1771.4 |  | 0 | 0 | 2.3809 | -2.3809 | 사용초과
| B523 | Daerim I&T |  | 4F-O12 | [23 empty] | 2.57 | 1771.4 |  | 0 | 0 | 2.3809 | -2.3809 | 사용초과
| B524 | Oriental Moon Co., Ltd. |  | 4F-O11 | [23 empty] | 2.57 | 1771.4 |  | 0 | 0 | 2.3809 | -2.3809 | 사용초과
3구역 Z열 |  |  |  | 4F-Z11 | KEN 3 #5 / 2P 100A | KEN 10 #5 / 2P 100A | 4-DaHall 1-PDU-06-100-5 | 4-DaHall 1-PDU-05-100-5 | 220 | 100 | 06 | 5 | 220 | 100 | 05 | 5 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | spare | 35.5 | -35.5 | 0 | 0 | 무부하 랙
|  |  |  | 4F-Z12 | [23 empty] | 0 | 0 | spare | 0 | 0 | 0 | 0 | 무부하 랙
|  |  |  | 4F-Z13 | [23 empty] | 0 | 0 | spare | 0 | 0 | 0 | 0 | 무부하 랙
|  |  |  | 4F-Z14 | [23 empty] | 0 | 0 | spare | 0 | 0 | 0 | 0 | 무부하 랙
[28 empty] | 0 | 0 | N #02 | 0 | 0 | 0 | 0 | 무부하 랙
[28 empty] | 0 | 0 | N #04 & N #05 | 0 | 0 | 0 | 0 | 무부하 랙
[28 empty] | 0 | 0 | N #01 & N #03 | 0 | 0 | 0 | 0 | 무부하 랙
[28 empty] | 0 | 0 | N #06 | 0 | 0 | 0 | 0 | 무부하 랙
2구역 M열 | C101 |  | 6.6 | 4F-N11 | KEN 3 #04 / 2P 100A | KEN 10 #04 / 2P 100A | 4-DaHall 1-PDU-06-100-4 | 4-DaHall 1-PDU-05-100-4 | 220 | 100 | 06 | 4 | 220 | 100 | 05 | 4 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 6.9198 | 7.2079 | 14.1277 | 1030.5 | 1070.4 | 3.038 | 2100.9 | 미설치 | 14.5 | -0.3723 | 2.8238 | 3.7762 | 적정함
| C102 |  |  | 4F-N12 | [23 empty] | 3.038 | 2100.9 | 미설치 | 0 | 0 | 2.8238 | -2.8238 | 사용초과
| C103 |  |  | 4F-N13 | [23 empty] | 3.038 | 2100.9 | 미설치 | 0 | 0 | 2.8238 | -2.8238 | 사용초과
| C104 |  |  | 4F-N14 | [23 empty] | 3.038 | 2100.9 |  | 0 | 0 | 2.8238 | -2.8238 | 사용초과
| C105 |  |  | 4F-N15 | [23 empty] | 3.038 | 2100.9 |  | 0 | 0 | 2.8238 | -2.8238 | 사용초과
| C106 | Sysone Co., Ltd. |  | 4F-N16 | [23 empty] | 3.038 | 2100.9 |  | 0 | 0 | 2.8238 | -2.8238 | 사용초과
| C107 |  |  | 4F-N17 | [23 empty] | 3.038 | 2100.9 |  | 0 | 0 | 2.8238 | -2.8238 | 사용초과
| C108 | Sysone Co., Ltd. |  | 4F-N18 | [23 empty] | 3.038 | 2100.9 |  | 0 | 0 | 2.8238 | -2.8238 | 사용초과
| C109 | Sysone Co., Ltd. |  | 4F-N19 | [23 empty] | 3.038 | 2100.9 |  | 0 | 0 | 2.8238 | -2.8238 | 사용초과
| C110 |  |  | 4F-N20 | [23 empty] | 3.038 | 2100.9 | 미설치 | 0 | 0 | 2.8238 | -2.8238 | 사용초과
| C111 |  |  | 4F-N21 | [23 empty] | 3.038 | 2100.9 | 미설치 | 0 | 0 | 2.8238 | -2.8238 | 사용초과
2구역 L열 | C201 | Digital Edge Korea | 5.5 | 4F-M11 | KEN 3 #03 / 2P 100A | KEN 10 #03 / 2P 100A | 4-DaHall 1-PDU-06-100-3 | 4-DaHall 1-PDU-05-100-3 | 220 | 100 | 06 | 3 | 220 | 100 | 05 | 3 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 8.9381 | 7.7143 | 16.6524 | 1397.2 | 1150.2 | 3.484 | 2547.4 |  | 17.4 | -0.74756 | 3.4239 | 2.0761 | 적정함
| C202 |  |  | 4F-M12 | [23 empty] | 3.484 | 2547.4 |  | 0 | 0 | 3.4239 | -3.4239 | 사용초과
| C203 | Singapore Telecom Korea Limited |  | 4F-M13 | [23 empty] | 3.484 | 2547.4 |  | 0 | 0 | 3.4239 | -3.4239 | 사용초과
| C204 | Singapore Telecom Korea Limited |  | 4F-M14 | [23 empty] | 3.484 | 2547.4 |  | 0 | 0 | 3.4239 | -3.4239 | 사용초과
| C205 |  |  | 4F-M15 | [23 empty] | 3.484 | 2547.4 |  | 0 | 0 | 3.4239 | -3.4239 | 사용초과
| C206 | Singapore Telecom Korea Limited |  | 4F-M16 | [23 empty] | 3.484 | 2547.4 |  | 0 | 0 | 3.4239 | -3.4239 | 사용초과
| C207 |  |  | 4F-M17 | [23 empty] | 3.484 | 2547.4 |  | 0 | 0 | 3.4239 | -3.4239 | 사용초과
| C208 |  |  | 4F-M18 | [23 empty] | 3.484 | 2547.4 |  | 0 | 0 | 3.4239 | -3.4239 | 사용초과
| C209 |  |  | 4F-M19 | [23 empty] | 3.484 | 2547.4 |  | 0 | 0 | 3.4239 | -3.4239 | 사용초과
| C210 |  |  | 4F-M20 | [23 empty] | 3.484 | 2547.4 |  | 0 | 0 | 3.4239 | -3.4239 | 사용초과
| C211 |  |  | 4F-M21 | [23 empty] | 3.484 | 2547.4 |  | 0 | 0 | 3.4239 | -3.4239 | 사용초과
2구역 K열 | C301 |  |  | 4F-L11 | KEN 3 #02 / 2P 100A | KEN 10 #02 / 2P 100A | 4-DaHall 1-PDU-06-100-2 | 4-DaHall 1-PDU-05-100-2 | 220 | 100 | 06 | 2 | 220 | 100 | 05 | 2 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
| C302 |  |  | 4F-L12 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
| C303 |  |  | 4F-L13 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
| C304 |  |  | 4F-L14 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
| C305 |  |  | 4F-L15 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
| C306 |  |  | 4F-L16 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
| C307 |  |  | 4F-L17 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
| C308 |  |  | 4F-L18 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
| C309 |  |  | 4F-L19 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
| C310 |  |  | 4F-L20 | [23 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 무부하 랙
2구역 J열 | C401 | DEK, 층간 Patch Cabinet | 4.95 | 4F-K11 | KEN 3 #01 / 2P 100A | KEN 10 #01 / 2P 100A | 4-DaHall 1-PDU-06-100-1 | 4-DaHall 1-PDU-05-100-1 | 220 | 100 | 06 | 1 | 220 | 100 | 05 | 1 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 10.5706 | 8.9845 | 19.5551 | 1654 | 1414.2 | 4.537 | 3068.2 |  | 20 | -0.4449 | 4.1239 | 0.82608 | 적정함
| C402 |  |  | 4F-K12 | [23 empty] | 4.537 | 3068.2 |  | 0 | 0 | 4.1239 | -4.1239 | 사용초과
| C403 |  |  | 4F-K13 | [23 empty] | 4.537 | 3068.2 |  | 0 | 0 | 4.1239 | -4.1239 | 사용초과
| C404 | CASTIS CO.,LTD. |  | 4F-K14 | [23 empty] | 4.537 | 3068.2 |  | 0 | 0 | 4.1239 | -4.1239 | 사용초과
| C405 | Sysone Co., Ltd. |  | 4F-K15 | [23 empty] | 4.537 | 3068.2 |  | 0 | 0 | 4.1239 | -4.1239 | 사용초과
| C406 |  |  | 4F-K16 | [23 empty] | 4.537 | 3068.2 |  | 0 | 0 | 4.1239 | -4.1239 | 사용초과
| C407 | TNC Technology |  | 4F-K17 | [23 empty] | 4.537 | 3068.2 |  | 0 | 0 | 4.1239 | -4.1239 | 사용초과
| C408 |  |  | 4F-K18 | [23 empty] | 4.537 | 3068.2 |  | 0 | 0 | 4.1239 | -4.1239 | 사용초과
| C409 |  |  | 4F-K19 | [23 empty] | 4.537 | 3068.2 |  | 0 | 0 | 4.1239 | -4.1239 | 사용초과
| C410 |  |  | 4F-K20 | [23 empty] | 4.537 | 3068.2 |  | 0 | 0 | 4.1239 | -4.1239 | 사용초과
2구역 I열 | C501 | Digital Edge Korea | 6.05 | 4F-J11 | KEN 1 #06 / 2P 100A | KEN 8 #06 | 4-DaHall 1-PDU-02-100-6 | 4-DaHall 1-PDU-01-100-6 | 220 | 100 | 02 | 6 | 220 | 100 | 01 | 6 | KEN 1 4P 300A | KEN 8 4P 300A | LV-4B #01 (3P 320A) | LV-4A #01 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 12.237 | 23.6876 | 35.9246 | 1841.8 | 3598.1 | 7.685 | 5439.9 |  | 37.1 | -1.1754 | 7.3117 | -1.2617 | 사용초과
| C502 |  |  | 4F-J12 | [23 empty] | 7.685 | 5439.9 |  | 0 | 0 | 7.3117 | -7.3117 | 사용초과
| C503 | Plus Eye Co., Ltd. |  | 4F-J13 | [23 empty] | 7.685 | 5439.9 |  | 0 | 0 | 7.3117 | -7.3117 | 사용초과
| C504 |  |  | 4F-J14 | [23 empty] | 7.685 | 5439.9 |  | 0 | 0 | 7.3117 | -7.3117 | 사용초과
| C505 |  |  | 4F-J15 | [23 empty] | 7.685 | 5439.9 |  | 0 | 0 | 7.3117 | -7.3117 | 사용초과
| C506 | Hecto Financial Co., Ltd. |  | 4F-J16 | [23 empty] | 7.685 | 5439.9 |  | 0 | 0 | 7.3117 | -7.3117 | 사용초과
| C507 | Hecto Financial Co., Ltd. |  | 4F-J17 | [23 empty] | 7.685 | 5439.9 |  | 0 | 0 | 7.3117 | -7.3117 | 사용초과
| C508 |  |  | 4F-J18 | [23 empty] | 7.685 | 5439.9 |  | 0 | 0 | 7.3117 | -7.3117 | 사용초과
| C509 | BS Printech |  | 4F-J19 | [23 empty] | 7.685 | 5439.9 |  | 0 | 0 | 7.3117 | -7.3117 | 사용초과
| C510 |  |  | 4F-J20 | [23 empty] | 7.685 | 5439.9 |  | 0 | 0 | 7.3117 | -7.3117 | 사용초과
1구역 H열 | C601 | Jongro Hakpyung | 18.7 | 4F-H11 | KEN 1 #07 / 2P 100A | KEN 8 #07 / 2P 100A | 4-DaHall 1-PDU-02-100-7 | 4-DaHall 1-PDU-01-100-7 | 220 | 100 | 02 | 7 | 220 | 100 | 01 | 7 | KEN 1 4P 300A | KEN 8 4P 300A | LV-4B #01 (3P 320A) | LV-4A #01 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 28.9762 | 12.6612 | 41.6375 | 4472.4 | 1852.3 | 8.855 | 6324.7 |  | 40.7 | 0.93746 | 8.5009 | 10.1991 | 적정함
| C602 |  |  | 4F-H12 | [23 empty] | 8.855 | 6324.7 | 22/05/01 해지 | 0 | 0 | 8.5009 | -8.5009 | 사용초과
| C603 | Jongro Hakpyung |  | 4F-H13 | [23 empty] | 8.855 | 6324.7 |  | 0 | 0 | 8.5009 | -8.5009 | 사용초과
| C604 | JS Data Systems Korea |  | 4F-H14 | [23 empty] | 8.855 | 6324.7 |  | 0 | 0 | 8.5009 | -8.5009 | 사용초과
| C605 | Settle Bank Co., Ltd. |  | 4F-H15 | [23 empty] | 8.855 | 6324.7 |  | 0 | 0 | 8.5009 | -8.5009 | 사용초과
| C606 | Settle Bank Co., Ltd. |  | 4F-H16 | [23 empty] | 8.855 | 6324.7 |  | 0 | 0 | 8.5009 | -8.5009 | 사용초과
| C607 | JS Data Systems Korea |  | 4F-H17 | [23 empty] | 8.855 | 6324.7 |  | 0 | 0 | 8.5009 | -8.5009 | 사용초과
| C608 | Settle Bank Co., Ltd. |  | 4F-H18 | [23 empty] | 8.855 | 6324.7 |  | 0 | 0 | 8.5009 | -8.5009 | 사용초과
| C609 | Settle Bank Co., Ltd. |  | 4F-H19 | [23 empty] | 8.855 | 6324.7 |  | 0 | 0 | 8.5009 | -8.5009 | 사용초과
| C610 |  |  | 4F-H20 | [23 empty] | 8.855 | 6324.7 |  | 0 | 0 | 8.5009 | -8.5009 | 사용초과
| C611 | CoinNet |  | 4F-H21 | [23 empty] | 8.855 | 6324.7 |  | 0 | 0 | 8.5009 | -8.5009 | 사용초과
1구역 G열 | C701 | Winnet System Co., Ltd. | 13.75 | 4F-G11 | KEN 2 #08 / 2P 100A | KEN 9 #08 / 2P 100A | 4-DaHall 1-PDU-04-100-8 | 4-DaHall 1-PDU-03-100-8 | 220 | 100 | 04 | 8 | 220 | 100 | 03 | 8 | KEN 2 4P 300A | KEN 9 4P 300A | LV-4B #06 (3P 320A) | LV-4A #06 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 22.1764 | 18.4772 | 40.6535 | 3301 | 2694.4 | 8.69 | 5995.4 |  | 39 | 1.6535 | 8.0583 | 5.6917 | 적정함
| C702 |  |  | 4F-G12 | [23 empty] | 8.69 | 5995.4 |  | 0 | 0 | 8.0583 | -8.0583 | 사용초과
| C703 |  |  | 4F-G13 | [23 empty] | 8.69 | 5995.4 |  | 0 | 0 | 8.0583 | -8.0583 | 사용초과
| C704 | Sysone Co., Ltd. |  | 4F-G14 | [23 empty] | 8.69 | 5995.4 |  | 0 | 0 | 8.0583 | -8.0583 | 사용초과
| C705 | JS Data Systems Korea |  | 4F-G15 | [23 empty] | 8.69 | 5995.4 |  | 0 | 0 | 8.0583 | -8.0583 | 사용초과
| C706 | Digital Edge Korea |  | 4F-G16 | [23 empty] | 8.69 | 5995.4 |  | 0 | 0 | 8.0583 | -8.0583 | 사용초과
| C707 |  |  | 4F-G17 | [23 empty] | 8.69 | 5995.4 |  | 0 | 0 | 8.0583 | -8.0583 | 사용초과
| C708 | Sysone Co., Ltd. |  | 4F-G18 | [23 empty] | 8.69 | 5995.4 |  | 0 | 0 | 8.0583 | -8.0583 | 사용초과
| C709 | Settle Bank Co., Ltd. |  | 4F-G19 | [23 empty] | 8.69 | 5995.4 |  | 0 | 0 | 8.0583 | -8.0583 | 사용초과
| C710 | Settle Bank Co., Ltd. |  | 4F-G20 | [23 empty] | 8.69 | 5995.4 |  | 0 | 0 | 8.0583 | -8.0583 | 사용초과
| C711 | Settle Bank Co., Ltd. |  | 4F-G21 | [23 empty] | 8.69 | 5995.4 |  | 0 | 0 | 8.0583 | -8.0583 | 사용초과
| C712 |  |  | 4F-G22 | [23 empty] | 8.69 | 5995.4 |  | 0 | 0 | 8.0583 | -8.0583 | 사용초과
1구역 F열 | C801 | Digital Edge Korea | 17.6 | 4F-F11 | KEN 2 #07 / 2P 100A | KEN 9 #07 / 2P 100A | 4-DaHall 1-PDU-04-100-7 | 4-DaHall 1-PDU-03-100-7 | 220 | 100 | 04 | 7 | 220 | 100 | 03 | 7 | KEN 2 4P 300A | KEN 9 4P 300A | LV-4B #06 (3P 320A) | LV-4A #06 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 21.233 | 28.9908 | 50.2238 | 3121.7 | 4443.1 | 10.939 | 7564.8 |  | 49.6 | 0.62383 | 10.1677 | 7.4323 | 적정함
| C802 | ANEXIA |  | 4F-F12 | [23 empty] | 10.939 | 7564.8 |  | 0 | 0 | 10.1677 | -10.1677 | 사용초과
| C803 |  |  | 4F-F13 | [23 empty] | 10.939 | 7564.8 |  | 0 | 0 | 10.1677 | -10.1677 | 사용초과
| C804 |  |  | 4F-F14 | [23 empty] | 10.939 | 7564.8 |  | 0 | 0 | 10.1677 | -10.1677 | 사용초과
| C805 |  |  | 4F-F15 | [23 empty] | 10.939 | 7564.8 |  | 0 | 0 | 10.1677 | -10.1677 | 사용초과
| C806 | Settle Bank Co., Ltd. |  | 4F-F16 | [23 empty] | 10.939 | 7564.8 |  | 0 | 0 | 10.1677 | -10.1677 | 사용초과
| C807 | Settle Bank Co., Ltd. |  | 4F-F17 | [23 empty] | 10.939 | 7564.8 |  | 0 | 0 | 10.1677 | -10.1677 | 사용초과
| C808 | Settle Bank Co., Ltd. |  | 4F-F18 | [23 empty] | 10.939 | 7564.8 |  | 0 | 0 | 10.1677 | -10.1677 | 사용초과
| C809 | Settle Bank Co., Ltd. |  | 4F-F19 | [23 empty] | 10.939 | 7564.8 |  | 0 | 0 | 10.1677 | -10.1677 | 사용초과
| C810 | Settle Bank Co., Ltd. |  | 4F-F20 | [23 empty] | 10.939 | 7564.8 |  | 0 | 0 | 10.1677 | -10.1677 | 사용초과
| C811 |  |  | 4F-F21 | [23 empty] | 10.939 | 7564.8 |  | 0 | 0 | 10.1677 | -10.1677 | 사용초과
| C812 | Shoot |  | 4F-F22 | [23 empty] | 10.939 | 7564.8 |  | 0 | 0 | 10.1677 | -10.1677 | 사용초과
1구역 E열 | C901 |  | 4.4 | 4F-E11 | KEN 2 #06 / 2P 100A | KEN 9 #06 / 2P 100A | 4-DaHall 1-PDU-04-100-6 | 4-DaHall 1-PDU-03-100-6 | 220 | 100 | 04 | 6 | 220 | 100 | 03 | 6 | KEN 2 4P 300A | KEN 9 4P 300A | LV-4B #06 (3P 320A) | LV-4A #06 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 14.2855 | 10.2225 | 24.508 | 2259.6 | 1528.2 | 5.368 | 3787.8 |  | 25 | -0.49199 | 5.0911 | -0.69113 | 사용초과
| C902 | MS Information Communication Co., Ltd. |  | 4F-E12 | [23 empty] | 5.368 | 3787.8 |  | 0 | 0 | 5.0911 | -5.0911 | 사용초과
| C903 |  |  | 4F-E13 | [23 empty] | 5.368 | 3787.8 |  | 0 | 0 | 5.0911 | -5.0911 | 사용초과
| C904 | Kyungdong Corporation |  | 4F-E14 | [23 empty] | 5.368 | 3787.8 |  | 0 | 0 | 5.0911 | -5.0911 | 사용초과
| C905 | Kyungdong Corporation |  | 4F-E15 | [23 empty] | 5.368 | 3787.8 |  | 0 | 0 | 5.0911 | -5.0911 | 사용초과
| C906 |  |  | 4F-E16 | [23 empty] | 5.368 | 3787.8 |  | 0 | 0 | 5.0911 | -5.0911 | 사용초과
| C907 |  |  | 4F-E17 | [23 empty] | 5.368 | 3787.8 |  | 0 | 0 | 5.0911 | -5.0911 | 사용초과
| C908 |  |  | 4F-E18 | [23 empty] | 5.368 | 3787.8 |  | 0 | 0 | 5.0911 | -5.0911 | 사용초과
| C909 |  |  | 4F-E19 | [23 empty] | 5.368 | 3787.8 |  | 0 | 0 | 5.0911 | -5.0911 | 사용초과
| C910 |  |  | 4F-E20 | [23 empty] | 5.368 | 3787.8 |  | 0 | 0 | 5.0911 | -5.0911 | 사용초과
| C911 |  |  | 4F-E21 | [23 empty] | 5.368 | 3787.8 |  | 0 | 0 | 5.0911 | -5.0911 | 사용초과
| C912 | Wiz Communication Co., Ltd. |  | 4F-E22 | [23 empty] | 5.368 | 3787.8 |  | 0 | 0 | 5.0911 | -5.0911 | 사용초과
1구역 D열 | C1001 | Spark & ​​Associates Co., Ltd. | 3.3 | 4F-D11 | KEN 2 #05 / 2P 100A | KEN 9 #05 / 2P 100A | 4-DaHall 1-PDU-04-100-5 | 4-DaHall 1-PDU-03-100-5 | 220 | 100 | 04 | 5 | 220 | 100 | 03 | 5 | KEN 2 4P 300A | KEN 9 4P 300A | LV-4B #06 (3P 320A) | LV-4A #06 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 9.7623 | 6.394 | 16.1562 | 1518.2 | 1012.6 | 3.509 | 2530.8 |  | 16.2 | -0.043756 | 3.4016 | -0.10161 | 사용초과
| C1002 |  |  | 4F-D12 | [23 empty] | 3.509 | 2530.8 |  | 0 | 0 | 3.4016 | -3.4016 | 사용초과
| C1003 |  |  | 4F-D13 | [23 empty] | 3.509 | 2530.8 |  | 0 | 0 | 3.4016 | -3.4016 | 사용초과
| C1004 |  |  | 4F-D14 | [23 empty] | 3.509 | 2530.8 |  | 0 | 0 | 3.4016 | -3.4016 | 사용초과
| C1005 |  |  | 4F-D15 | [23 empty] | 3.509 | 2530.8 |  | 0 | 0 | 3.4016 | -3.4016 | 사용초과
| C1006 |  |  | 4F-D16 | [23 empty] | 3.509 | 2530.8 |  | 0 | 0 | 3.4016 | -3.4016 | 사용초과
| C1007 |  |  | 4F-D17 | [23 empty] | 3.509 | 2530.8 |  | 0 | 0 | 3.4016 | -3.4016 | 사용초과
| C1008 | Sejong Telecom Inc. |  | 4F-D18 | [23 empty] | 3.509 | 2530.8 |  | 0 | 0 | 3.4016 | -3.4016 | 사용초과
| C1009 |  |  | 4F-D19 | [23 empty] | 3.509 | 2530.8 |  | 0 | 0 | 3.4016 | -3.4016 | 사용초과
| C1010 |  |  | 4F-D20 | [23 empty] | 3.509 | 2530.8 |  | 0 | 0 | 3.4016 | -3.4016 | 사용초과
| C1011 |  |  | 4F-D21 | [23 empty] | 3.509 | 2530.8 |  | 0 | 0 | 3.4016 | -3.4016 | 사용초과
| C1012 |  |  | 4F-D22 | [23 empty] | 3.509 | 2530.8 |  | 0 | 0 | 3.4016 | -3.4016 | 사용초과
| A401 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-7 | 4-DaHall 1-PDU-11-30-7 | 220 | 30 | 12 | 7 | 220 | 30 | 11 | 7 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 68.1 | -68.1 | 0 | 2 | 무부하 랙
| A402 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-8 | 4-DaHall 1-PDU-11-30-8 | 220 | 30 | 12 | 8 | 220 | 30 | 11 | 8 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
[7 empty] | 4-DaHall 1-PDU-12-30-37 | 4-DaHall 1-PDU-11-30-37 | 220 | 30 | 12 | 37 | 220 | 30 | 11 | 37 | [6 empty] | 0 | 0 |  | 0 | 0 | #N/A |  |  | 74.1 | -74.1 | 0 | 0 | 무부하 랙
| A403 | GS ITM | 미계약 |  |  |  | 4-DaHall 1-PDU-12-30-9 | 4-DaHall 1-PDU-11-30-9 | 220 | 30 | 12 | 9 | 220 | 30 | 11 | 9 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | #VALUE! | #VALUE!
| A404 | GS ITM | 4 |  |  |  | 4-DaHall 1-PDU-12-30-10 | 4-DaHall 1-PDU-11-30-10 | 220 | 30 | 12 | 10 | 220 | 30 | 11 | 10 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0.1 |  | 74.1 | -74.1 | 0.00013441 | 3.9999 | 적정함
[7 empty] | 4-DaHall 1-RPP-02-30-1 | 4-DaHall 1-RPP-01-30-1 | 208 | 30 | 2 | 1 | 208 | 30 | 1 | 1 | [6 empty] | 0 | 0 |  | 0.1 | 0 | #N/A |  |  | 74.1 | -74.1 | 0 | 0 | 무부하 랙
| A405 | GS ITM | 미계약 |  |  |  | 4-DaHall 1-PDU-12-30-11 | 4-DaHall 1-PDU-11-30-11 | 220 | 30 | 12 | 11 | 220 | 30 | 11 | 11 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | #VALUE! | #VALUE!
| A406 | GS ITM | 4 |  |  |  | 4-DaHall 1-PDU-12-30-12 | 4-DaHall 1-PDU-11-30-12 | 220 | 30 | 12 | 12 | 220 | 30 | 11 | 12 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0.1 |  | 74.1 | -74.1 | 0.00013441 | 3.9999 | 적정함
[7 empty] | 4-DaHall 1-RPP-02-30-2 | 4-DaHall 1-RPP-01-30-2 | 208 | 30 | 2 | 2 | 208 | 30 | 1 | 2 | [6 empty] | 0 | 0 |  | 0.1 | 0 | #N/A |  |  | 74.1 | -74.1 | 0 | 0 | 무부하 랙
| A407 | GS ITM | 미계약 |  |  |  | 4-DaHall 1-PDU-12-30-13 | 4-DaHall 1-PDU-11-30-13 | 220 | 30 | 12 | 13 | 220 | 30 | 11 | 13 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | #VALUE! | #VALUE!
| A408 | GS ITM | 4 |  |  |  | 4-DaHall 1-PDU-12-30-14 | 4-DaHall 1-PDU-11-30-14 | 220 | 30 | 12 | 14 | 220 | 30 | 11 | 14 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0.1 |  | 74.1 | -74.1 | 0.00013441 | 3.9999 | 적정함
[7 empty] | 4-DaHall 1-RPP-02-30-3 | 4-DaHall 1-RPP-01-30-3 | 208 | 30 | 2 | 3 | 208 | 30 | 1 | 3 | [6 empty] | 0 | 0 |  | 0.1 | 0 | #N/A |  |  | 74.1 | -74.1 | 0 | 0 | 무부하 랙
| A409 | GS ITM | 미계약 |  |  |  | 4-DaHall 1-PDU-12-30-15 | 4-DaHall 1-PDU-11-30-15 | 220 | 30 | 12 | 15 | 220 | 30 | 11 | 15 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | #VALUE! | #VALUE!
| A410 | GS ITM | 미계약 |  |  |  | 4-DaHall 1-PDU-12-30-16 | 4-DaHall 1-PDU-11-30-16 | 220 | 30 | 12 | 16 | 220 | 30 | 11 | 16 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | #VALUE! | #VALUE!
| A501 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-17 | 4-DaHall 1-PDU-11-30-17 | 220 | 30 | 12 | 17 | 220 | 30 | 11 | 17 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A502 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-18 | 4-DaHall 1-PDU-11-30-18 | 220 | 30 | 12 | 18 | 220 | 30 | 11 | 18 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A503 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-19 | 4-DaHall 1-PDU-11-30-19 | 220 | 30 | 12 | 19 | 220 | 30 | 11 | 19 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
[7 empty] | 4-DaHall 1-PDU-12-30-38 | 4-DaHall 1-PDU-11-30-38 | 220 | 30 | 12 | 38 | 220 | 30 | 11 | 38 | [6 empty] | 0 | 0 |  | 0 | 0 | #N/A |  |  | 74.1 | -74.1 | 0 | 0 | 무부하 랙
| A504 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-20 | 4-DaHall 1-PDU-11-30-20 | 220 | 30 | 12 | 20 | 220 | 30 | 11 | 20 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A505 | GS ITM | 4 |  |  |  | 4-DaHall 1-PDU-12-30-21 | 4-DaHall 1-PDU-11-30-21 | 220 | 30 | 12 | 21 | 220 | 30 | 11 | 21 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 4 | 무부하 랙
| A506 | GS ITM | 4 |  |  |  | 4-DaHall 1-PDU-12-30-22 | 4-DaHall 1-PDU-11-30-22 | 220 | 30 | 12 | 22 | 220 | 30 | 11 | 22 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 4 | 무부하 랙
[7 empty] | 4-DaHall 1-PDU-12-30-39 | 4-DaHall 1-PDU-11-30-39 | 208 | 30 | 12 | 39 | 208 | 30 | 11 | 39 | [6 empty] | 0 | 0 |  | 0 | 0 | #N/A |  |  | 74.1 | -74.1 | 0 | 0 | 무부하 랙
| A507 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-23 | 4-DaHall 1-PDU-11-30-23 | 220 | 30 | 12 | 23 | 220 | 30 | 11 | 23 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A508 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-24 | 4-DaHall 1-PDU-11-30-24 | 220 | 30 | 12 | 24 | 220 | 30 | 11 | 24 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A509 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-25 | 4-DaHall 1-PDU-11-30-25 | 220 | 30 | 12 | 25 | 220 | 30 | 11 | 25 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A510 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-26 | 4-DaHall 1-PDU-11-30-26 | 220 | 30 | 12 | 26 | 220 | 30 | 11 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A601 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-27 | 4-DaHall 1-PDU-11-30-27 | 220 | 30 | 12 | 27 | 220 | 30 | 11 | 27 | [6 empty] | 2.1701 | 0.28 | 2.4501 | 18.1 | 1.4 | #N/A | 19.5 |  | 74.1 | -71.6499 | 0.02621 | 1.9738 | 적정함
| A602 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-28 | 4-DaHall 1-PDU-11-30-28 | 220 | 30 | 12 | 28 | 220 | 30 | 11 | 28 | [6 empty] | 0.94375 | 0.22021 | 1.164 | 11 | 1.4 | #N/A | 12.4 |  | 74.1 | -72.936 | 0.016667 | 1.9833 | 적정함
| A603 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-29 | 4-DaHall 1-PDU-11-30-29 | 220 | 30 | 12 | 29 | 220 | 30 | 11 | 29 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A604 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-30 | 4-DaHall 1-PDU-11-30-30 | 220 | 30 | 12 | 30 | 220 | 30 | 11 | 30 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A605 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-31 | 4-DaHall 1-PDU-11-30-31 | 220 | 30 | 12 | 31 | 220 | 30 | 11 | 31 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A606 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-32 | 4-DaHall 1-PDU-11-30-32 | 220 | 30 | 12 | 32 | 220 | 30 | 11 | 32 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A607 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-33 | 4-DaHall 1-PDU-11-30-33 | 220 | 30 | 12 | 33 | 220 | 30 | 11 | 33 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A608 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-34 | 4-DaHall 1-PDU-11-30-34 | 220 | 30 | 12 | 34 | 220 | 30 | 11 | 34 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A609 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-35 | 4-DaHall 1-PDU-11-30-35 | 220 | 30 | 12 | 35 | 220 | 30 | 11 | 35 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A610 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-12-30-36 | 4-DaHall 1-PDU-11-30-36 | 220 | 30 | 12 | 36 | 220 | 30 | 11 | 36 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A701 | GS ITM | 4 |  |  |  | 4-DaHall 1-PDU-14-30-5 | 4-DaHall 1-PDU-13-30-5 | 220 | 30 | 14 | 5 | 220 | 30 | 13 | 5 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 4 | 무부하 랙
[7 empty] | 4-DaHall 1-PDU-14-30-6 | 4-DaHall 1-PDU-13-30-6 | 220 | 30 | 14 | 6 | 220 | 30 | 13 | 6 | [6 empty] | 0 | 0 |  | 0 | 0 | #N/A |  |  | 74.1 | -74.1 | 0 | 0 | 무부하 랙
| A702 | GS ITM | 4 |  |  |  | 4-DaHall 1-PDU-14-30-7 | 4-DaHall 1-PDU-13-30-7 | 220 | 30 | 14 | 7 | 220 | 30 | 13 | 7 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 4 | 무부하 랙
[7 empty] | 4-DaHall 1-PDU-14-30-8 | 4-DaHall 1-PDU-13-30-8 | 220 | 30 | 14 | 8 | 220 | 30 | 13 | 8 | [6 empty] | 0 | 0 |  | 0 | 0 | #N/A |  |  | 74.1 | -74.1 | 0 | 0 | 무부하 랙
| A703 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-9 | 4-DaHall 1-PDU-13-30-9 | 220 | 30 | 14 | 9 | 220 | 30 | 13 | 9 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A704 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-10 | 4-DaHall 1-PDU-13-30-10 | 220 | 30 | 14 | 10 | 220 | 30 | 13 | 10 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A705 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-11 | 4-DaHall 1-PDU-13-30-11 | 220 | 30 | 14 | 11 | 220 | 30 | 13 | 11 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A706 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-12 | 4-DaHall 1-PDU-13-30-12 | 220 | 30 | 14 | 12 | 220 | 30 | 13 | 12 | [6 empty] | 0 | 0 | 0.0040306 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.096 | 0 | 2 | 무부하 랙
[7 empty] | 4-DaHall 1-PDU-14-30-38 | 4-DaHall 1-PDU-13-30-38 | 220 | 30 | 14 | 38 | 220 | 30 | 13 | 38 | [6 empty] | 0.0040306 | 0 |  | 0 | 0 | #N/A |  |  | 74.1 | -74.1 | 0 | 0 | 무부하 랙
| A707 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-13 | 4-DaHall 1-PDU-13-30-13 | 220 | 30 | 14 | 13 | 220 | 30 | 13 | 13 | [6 empty] | 0.00045139 | 0 | 0.00045139 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.0995 | 0 | 2 | 무부하 랙
| A708 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-14 | 4-DaHall 1-PDU-13-30-14 | 220 | 30 | 14 | 14 | 220 | 30 | 13 | 14 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A709 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-15 | 4-DaHall 1-PDU-13-30-15 | 220 | 30 | 14 | 15 | 220 | 30 | 13 | 15 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A710 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-16 | 4-DaHall 1-PDU-13-30-16 | 220 | 30 | 14 | 16 | 220 | 30 | 13 | 16 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A801 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-17 | 4-DaHall 1-PDU-13-30-17 | 220 | 30 | 14 | 17 | 220 | 30 | 13 | 17 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A802 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-18 | 4-DaHall 1-PDU-13-30-18 | 220 | 30 | 14 | 18 | 220 | 30 | 13 | 18 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A803 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-19 | 4-DaHall 1-PDU-13-30-19 | 220 | 30 | 14 | 19 | 220 | 30 | 13 | 19 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A804 | GS ITM | 4 |  |  |  | 4-DaHall 1-RPP-02-30-4 | 4-DaHall 1-RPP-01-30-4 | 208 | 30 | 2 | 4 | 208 | 30 | 1 | 4 | [6 empty] | 0 | 0 | 0 | 0.1 | #N/A | #N/A | #N/A |  | 74.1 | -74.1 | #N/A | #N/A | #N/A
| A805 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-20 | 4-DaHall 1-PDU-13-30-20 | 220 | 30 | 14 | 20 | 220 | 30 | 13 | 20 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
[7 empty] | 4-DaHall 1-PDU-14-30-21 | 4-DaHall 1-PDU-13-30-21 | 220 | 30 | 14 | 21 | 220 | 30 | 13 | 21 | [6 empty] | 0 | 0 |  | 0 | 0 | #N/A |  |  | 74.1 | -74.1 | 0 | 0 | 무부하 랙
| A806 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-22 | 4-DaHall 1-PDU-13-30-22 | 220 | 30 | 14 | 22 | 220 | 30 | 13 | 22 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
[7 empty] | 4-DaHall 1-PDU-14-30-39 | 4-DaHall 1-PDU-13-30-39 | 220 | 30 | 14 | 39 | 220 | 30 | 13 | 39 | [6 empty] | 0 | 0 |  | 0 | 0 | #N/A |  |  | 74.1 | -74.1 | 0 | 0 | 무부하 랙
| A807 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-23 | 4-DaHall 1-PDU-13-30-23 | 220 | 30 | 14 | 23 | 220 | 30 | 13 | 23 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A808 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-24 | 4-DaHall 1-PDU-13-30-24 | 220 | 30 | 14 | 24 | 220 | 30 | 13 | 24 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A809 | GS ITM | 4 |  |  |  | 4-DaHall 1-PDU-14-30-25 | 4-DaHall 1-PDU-13-30-25 | 220 | 30 | 14 | 25 | 220 | 30 | 13 | 25 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 4 | 무부하 랙
| A810 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-26 | 4-DaHall 1-PDU-13-30-26 | 220 | 30 | 14 | 26 | 220 | 30 | 13 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A901 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-27 | 4-DaHall 1-PDU-13-30-27 | 220 | 30 | 14 | 27 | 220 | 30 | 13 | 27 | [6 empty] | 0.0040625 | 0 | 0.0040625 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.0959 | 0 | 2 | 무부하 랙
| A902 | GS ITM | 4 |  |  |  | 4-DaHall 1-PDU-14-30-29 | 4-DaHall 1-PDU-13-30-29 | 220 | 30 | 14 | 29 | 220 | 30 | 13 | 29 | [6 empty] | 0.0041626 | 0 | 0.0041626 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.0958 | 0 | 4 | 무부하 랙
| A903 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-30 | 4-DaHall 1-PDU-13-30-30 | 220 | 30 | 14 | 30 | 220 | 30 | 13 | 30 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A904 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-31 | 4-DaHall 1-PDU-13-30-31 | 220 | 30 | 14 | 31 | 220 | 30 | 13 | 31 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A905 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-32 | 4-DaHall 1-PDU-13-30-32 | 220 | 30 | 14 | 32 | 220 | 30 | 13 | 32 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A906 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-33 | 4-DaHall 1-PDU-13-30-33 | 220 | 30 | 14 | 33 | 220 | 30 | 13 | 33 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A907 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-34 | 4-DaHall 1-PDU-13-30-34 | 220 | 30 | 14 | 34 | 220 | 30 | 13 | 34 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
[7 empty] | 4-DaHall 1-PDU-14-30-28 | 4-DaHall 1-PDU-13-30-28 | 220 | 30 | 14 | 28 | 220 | 30 | 13 | 28 | [6 empty] | 0 | 0 |  | 0 | 0 | #N/A |  |  | 74.1 | -74.1 | 0 | 0 | 무부하 랙
| A908 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-35 | 4-DaHall 1-PDU-13-30-35 | 220 | 30 | 14 | 35 | 220 | 30 | 13 | 35 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A909 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-36 | 4-DaHall 1-PDU-13-30-36 | 220 | 30 | 14 | 36 | 220 | 30 | 13 | 36 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
| A910 | GS ITM | 2 |  |  |  | 4-DaHall 1-PDU-14-30-37 | 4-DaHall 1-PDU-13-30-37 | 220 | 30 | 14 | 37 | 220 | 30 | 13 | 37 | [6 empty] | 0 | 0 | 0 | 0 | 0 | #N/A | 0 |  | 74.1 | -74.1 | 0 | 2 | 무부하 랙
-59.0877
[25 empty] | 1084.5638 | 103.7612
오차
Note on A115: 이현상: 랙 배치도 참고하세요

## 7층~4층_매핑테이블
| 4층 랙별 전기공급계통 | [7 empty] | 5층 랙별 전기공급계통 | [7 empty] | 6층 랙별 전기공급계통 | [5 empty] | 0 |  | 7층 랙별 전기공급계통
| DEK Naming Convention 적용 명칭(NEW) |  |  | 1 |  |  |  |  | DEK Naming Convention 적용 명칭(NEW) | [7 empty] | DEK Naming Convention 적용 명칭(NEW) | [7 empty] | DEK Naming Convention 적용 명칭(NEW) |  | 23 | 20
| ↓여기에 층별 PDU리스트 복사 및 붙여넣기 하세요! |  | [branch#001] [A] W | [branch#003] [A] W | [branch#0] [A] W |  | 8 |  | ↓여기에 층별 PDU리스트 복사 및 붙여넣기 하세요! |  | 2 | [5 empty] | ↓여기에 층별 PDU리스트 복사 및 붙여넣기 하세요! |  | 2 | [5 empty] | ↓여기에 층별 PDU리스트 복사 및 붙여넣기 하세요! |  |  | 1
4층 상.하 키값 | 상(A) | 하(B) | 4층 상 PDU번호 | 4층 상 차단기번호 | 4층 하 PDU번호 | 4층 하 차단기번호 | 4층 kW(전월최대유효전력) | 5층 상.하 키값 | 상(A) | 하(B) | 5층 상 PDU번호 | 5층 상 차단기번호 | 5층 하 PDU번호 | 5층 하 차단기번호 | 5층 kW(전월최대유효전력) | 6층 상.하 키값 | 상(A) | 하(B) | 6층 상 PDU번호 | 6층 상 차단기번호 | 6층 하 PDU번호 | 6층 하 차단기번호 | 6층 kW(전월최대유효전력) | 7층 상.하 키값 | 상(A) | 하(B) | 7층 상 PDU번호 | 7층 상 차단기번호 | 7층 하 PDU번호 | 7층 하 차단기번호 | 7층 kW(전월최대유효전력)
4-DaHall 1-PDU-02-100-1 | 4-DaHall 1-PDU-02-100-1 |  | 4-DaHall 1-PDU-02 | [branch#001] [A] W |  |  | 0.391 | 5-DaHall 1-PDU-11-30-35-DaHall 1-PDU-12-30-3 | 5-DaHall 1-PDU-11-30-3 | 5-DaHall 1-PDU-12-30-3 | 5-DaHall 1-PDU-11 | [branch#003] [A] W | 5-DaHall 1-PDU-12 | [branch#003] [A] W | 0 | 6-DaHall 1-PDU-07-30-366-DaHall 1-PDU-08-30-36 | 6-DaHall 1-PDU-07-30-36 | 6-DaHall 1-PDU-08-30-36 | 6-DaHall 1-PDU-07 | [branch#036] [A] W | 6-DaHall 1-PDU-08 | [branch#036] [A] W | 0 | 7-DaHall 1-PDU-03-225-6 | 7-DaHall 1-PDU-03-225-6 |  | 7-DaHall 1-PDU-03 | [branch#006] [A] W |  |  | 32.356
4-DaHall 1-PDU-01-100-1 |  | 4-DaHall 1-PDU-01-100-1 |  |  | 4-DaHall 1-PDU-01 | [branch#001] [A] W | 0.696 | 5-DaHall 1-PDU-11-30-55-DaHall 1-PDU-12-30-5 | 5-DaHall 1-PDU-11-30-5 | 5-DaHall 1-PDU-12-30-5 | 5-DaHall 1-PDU-11 | [branch#005] [A] W | 5-DaHall 1-PDU-12 | [branch#005] [A] W | 0 | 6-DaHall 1-PDU-07-30-386-DaHall 1-PDU-08-30-38 | 6-DaHall 1-PDU-07-30-38 | 6-DaHall 1-PDU-08-30-38 | 6-DaHall 1-PDU-07 | [branch#038] [A] W | 6-DaHall 1-PDU-08 | [branch#038] [A] W | 0 | 7-DaHall 1-PDU-04-150-1 |  | 7-DaHall 1-PDU-04-150-1 |  |  | 7-DaHall 1-PDU-04 | [branch#001] [A] W | 28.323
4-DaHall 1-PDU-10-200-2 | 4-DaHall 1-PDU-10-200-2 |  | 4-DaHall 1-PDU-10 | [branch#002] [A] W |  |  | 19.682 | 5-DaHall 1-PDU-11-30-95-DaHall 1-PDU-12-20-26 | 5-DaHall 1-PDU-11-30-9 | 5-DaHall 1-PDU-12-20-26 | 5-DaHall 1-PDU-11 | [branch#009] [A] W | 5-DaHall 1-PDU-12 | [branch#026] [A] W | 2.225 | 6-DaHall 1-PDU-07-30-406-DaHall 1-PDU-08-30-40 | 6-DaHall 1-PDU-07-30-40 | 6-DaHall 1-PDU-08-30-40 | 6-DaHall 1-PDU-07 | [branch#040] [A] W | 6-DaHall 1-PDU-08 | [branch#040] [A] W | 0 | 7-DaHall 1-A-4-35-327-DaHall 1-B-4-35-32 | 7-DaHall 1-A-4-35-32 | 7-DaHall 1-B-4-35-32 | 7-DaHall 1-A-4-35 | [branch#032] [A] W | 7-DaHall 1-B-4-35 | [branch#032] [A] W | #N/A
4-DaHall 1-PDU-10-200-3 | 4-DaHall 1-PDU-10-200-3 |  | 4-DaHall 1-PDU-10 | [branch#003] [A] W |  |  | 17.48 | 5-DaHall 1-PDU-11-20-265-DaHall 1-PDU-12-20-30 | 5-DaHall 1-PDU-11-20-26 | 5-DaHall 1-PDU-12-20-30 | 5-DaHall 1-PDU-11 | [branch#026] [A] W | 5-DaHall 1-PDU-12 | [branch#030] [A] W | 2.608 | 6-DaHall 1-PDU-07-30-426-DaHall 1-PDU-08-30-42 | 6-DaHall 1-PDU-07-30-42 | 6-DaHall 1-PDU-08-30-42 | 6-DaHall 1-PDU-07 | [branch#042] [A] W | 6-DaHall 1-PDU-08 | [branch#042] [A] W | 0 | 7-DaHall 1-PDU-01-30-377-DaHall 1-PDU-02-30-37 | 7-DaHall 1-PDU-01-30-37 | 7-DaHall 1-PDU-02-30-37 | 7-DaHall 1-PDU-01 | [branch#037] [A] W | 7-DaHall 1-PDU-02 | [branch#037] [A] W | 0.093
4-DaHall 1-PDU-02-100-34-DaHall 1-PDU-01-100-3 | 4-DaHall 1-PDU-02-100-3 | 4-DaHall 1-PDU-01-100-3 | 4-DaHall 1-PDU-02 | [branch#003] [A] W | 4-DaHall 1-PDU-01 | [branch#003] [A] W | 14.317 | 5-DaHall 1-PDU-11-30-115-DaHall 1-PDU-12-30-9 | 5-DaHall 1-PDU-11-30-11 | 5-DaHall 1-PDU-12-30-9 | 5-DaHall 1-PDU-11 | [branch#011] [A] W | 5-DaHall 1-PDU-12 | [branch#009] [A] W | 0.626 | 6-DaHall 1-PDU-07-30-446-DaHall 1-PDU-08-30-44 | 6-DaHall 1-PDU-07-30-44 | 6-DaHall 1-PDU-08-30-44 | 6-DaHall 1-PDU-07 | [branch#044] [A] W | 6-DaHall 1-PDU-08 | [branch#044] [A] W | 0 | 7-DaHall 1-A-4-100-587-DaHall 1-B-4-100-58 | 7-DaHall 1-A-4-100-58 | 7-DaHall 1-B-4-100-58 | 7-DaHall 1-A-4-10 | [branch#058] [A] W | 7-DaHall 1-B-4-10 | [branch#058] [A] W | #N/A
4-DaHall 1-PDU-02-100-44-DaHall 1-PDU-01-100-4 | 4-DaHall 1-PDU-02-100-4 | 4-DaHall 1-PDU-01-100-4 | 4-DaHall 1-PDU-02 | [branch#004] [A] W | 4-DaHall 1-PDU-01 | [branch#004] [A] W | 15.279 | 5-DaHall 1-PDU-11-30-135-DaHall 1-PDU-12-30-11 | 5-DaHall 1-PDU-11-30-13 | 5-DaHall 1-PDU-12-30-11 | 5-DaHall 1-PDU-11 | [branch#013] [A] W | 5-DaHall 1-PDU-12 | [branch#011] [A] W | 0.431 | 6-DaHall 1-PDU-07-30-466-DaHall 1-PDU-08-30-46 | 6-DaHall 1-PDU-07-30-46 | 6-DaHall 1-PDU-08-30-46 | 6-DaHall 1-PDU-07 | [branch#046] [A] W | 6-DaHall 1-PDU-08 | [branch#046] [A] W | 0 | 7-DaHall 1-A-4-100-567-DaHall 1-B-4-35-56 | 7-DaHall 1-A-4-100-56 | 7-DaHall 1-B-4-35-56 | 7-DaHall 1-A-4-10 | [branch#056] [A] W | 7-DaHall 1-B-4-35 | [branch#056] [A] W | #N/A
4-DaHall 1-PDU-02-100-54-DaHall 1-PDU-01-100-5 | 4-DaHall 1-PDU-02-100-5 | 4-DaHall 1-PDU-01-100-5 | 4-DaHall 1-PDU-02 | [branch#005] [A] W | 4-DaHall 1-PDU-01 | [branch#005] [A] W | 18.469 | 5-DaHall 1-PDU-07-30-15-DaHall 1-PDU-08-30-7 | 5-DaHall 1-PDU-07-30-1 | 5-DaHall 1-PDU-08-30-7 | 5-DaHall 1-PDU-07 | [branch#001] [A] W | 5-DaHall 1-PDU-08 | [branch#007] [A] W | 2.794 | [7 empty] | 0 | 7-DaHall 1-A-4-50-597-DaHall 1-B-4-50-59 | 7-DaHall 1-A-4-50-59 | 7-DaHall 1-B-4-50-59 | 7-DaHall 1-A-4-50 | [branch#059] [A] W | 7-DaHall 1-B-4-50 | [branch#059] [A] W | #N/A
4-DaHall 1-PDU-02-100-24-DaHall 1-PDU-01-100-2 | 4-DaHall 1-PDU-02-100-2 | 4-DaHall 1-PDU-01-100-2 | 4-DaHall 1-PDU-02 | [branch#002] [A] W | 4-DaHall 1-PDU-01 | [branch#002] [A] W | 15.489 | 5-DaHall 1-PDU-07-30-35-DaHall 1-PDU-08-30-3 | 5-DaHall 1-PDU-07-30-3 | 5-DaHall 1-PDU-08-30-3 | 5-DaHall 1-PDU-07 | [branch#003] [A] W | 5-DaHall 1-PDU-08 | [branch#003] [A] W | 0.341 | [7 empty] | 0 | 7-DaHall 1-A-4-50-257-DaHall 1-B-4-50-25 | 7-DaHall 1-A-4-50-25 | 7-DaHall 1-B-4-50-25 | 7-DaHall 1-A-4-50 | [branch#025] [A] W | 7-DaHall 1-B-4-50 | [branch#025] [A] W | #N/A
4-DaHall 1-PDU-04-100-24-DaHall 1-PDU-03-100-2 | 4-DaHall 1-PDU-04-100-2 | 4-DaHall 1-PDU-03-100-2 | 4-DaHall 1-PDU-04 | [branch#002] [A] W | 4-DaHall 1-PDU-03 | [branch#002] [A] W | 16.236 | 5-DaHall 1-PDU-07-30-55-DaHall 1-PDU-08-30-5 | 5-DaHall 1-PDU-07-30-5 | 5-DaHall 1-PDU-08-30-5 | 5-DaHall 1-PDU-07 | [branch#005] [A] W | 5-DaHall 1-PDU-08 | [branch#005] [A] W | 0.082 | [7 empty] | 0 | [7 empty] | 0
4-DaHall 1-PDU-04-100-34-DaHall 1-PDU-03-100-3 | 4-DaHall 1-PDU-04-100-3 | 4-DaHall 1-PDU-03-100-3 | 4-DaHall 1-PDU-04 | [branch#003] [A] W | 4-DaHall 1-PDU-03 | [branch#003] [A] W | 12.522 | 5-DaHall 1-PDU-07-30-25-DaHall 1-PDU-08-30-2 | 5-DaHall 1-PDU-07-30-2 | 5-DaHall 1-PDU-08-30-2 | 5-DaHall 1-PDU-07 | [branch#002] [A] W | 5-DaHall 1-PDU-08 | [branch#002] [A] W | 0.392 | [7 empty] | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-11-20-285-DaHall 1-PDU-12-20-28 | 5-DaHall 1-PDU-11-20-28 | 5-DaHall 1-PDU-12-20-28 | 5-DaHall 1-PDU-11 | [branch#028] [A] W | 5-DaHall 1-PDU-12 | [branch#028] [A] W | 2.506 | 6-DaHall 1-PDU-07-30-546-DaHall 1-PDU-08-30-54 | 6-DaHall 1-PDU-07-30-54 | 6-DaHall 1-PDU-08-30-54 | 6-DaHall 1-PDU-07 | [branch#054] [A] W | 6-DaHall 1-PDU-08 | [branch#054] [A] W | 0 | [7 empty] | 0
4-DaHall 1-PDU-08-100-24-DaHall 1-PDU-07-100-2 | 4-DaHall 1-PDU-08-100-2 | 4-DaHall 1-PDU-07-100-2 | 4-DaHall 1-PDU-08 | [branch#002] [A] W | 4-DaHall 1-PDU-07 | [branch#002] [A] W | 15.074 | 5-DaHall 1-PDU-07-30-45-DaHall 1-PDU-08-30-4 | 5-DaHall 1-PDU-07-30-4 | 5-DaHall 1-PDU-08-30-4 | 5-DaHall 1-PDU-07 | [branch#004] [A] W | 5-DaHall 1-PDU-08 | [branch#004] [A] W | 0 | 6-DaHall 1-PDU-07-30-536-DaHall 1-PDU-08-30-53 | 6-DaHall 1-PDU-07-30-53 | 6-DaHall 1-PDU-08-30-53 | 6-DaHall 1-PDU-07 | [branch#053] [A] W | 6-DaHall 1-PDU-08 | [branch#053] [A] W | 0 | 7-DaHall 1-B-4-100-317-DaHall 1-A-4-100-31 | 7-DaHall 1-B-4-100-31 | 7-DaHall 1-A-4-100-31 | 7-DaHall 1-B-4-10 | [branch#031] [A] W | 7-DaHall 1-A-4-10 | [branch#031] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-07-30-65-DaHall 1-PDU-08-30-6 | 5-DaHall 1-PDU-07-30-6 | 5-DaHall 1-PDU-08-30-6 | 5-DaHall 1-PDU-07 | [branch#006] [A] W | 5-DaHall 1-PDU-08 | [branch#006] [A] W | 0.337 | 6-DaHall 1-PDU-07-30-516-DaHall 1-PDU-08-30-51 | 6-DaHall 1-PDU-07-30-51 | 6-DaHall 1-PDU-08-30-51 | 6-DaHall 1-PDU-07 | [branch#051] [A] W | 6-DaHall 1-PDU-08 | [branch#051] [A] W | 0 | 7-DaHall 1-B-4-100-307-DaHall 1-A-4-100-30 | 7-DaHall 1-B-4-100-30 | 7-DaHall 1-A-4-100-30 | 7-DaHall 1-B-4-10 | [branch#030] [A] W | 7-DaHall 1-A-4-10 | [branch#030] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-11-20-155-DaHall 1-PDU-12-20-13 | 5-DaHall 1-PDU-11-20-15 | 5-DaHall 1-PDU-12-20-13 | 5-DaHall 1-PDU-11 | [branch#015] [A] W | 5-DaHall 1-PDU-12 | [branch#013] [A] W | 0 | 6-DaHall 1-PDU-07-30-496-DaHall 1-PDU-08-30-49 | 6-DaHall 1-PDU-07-30-49 | 6-DaHall 1-PDU-08-30-49 | 6-DaHall 1-PDU-07 | [branch#049] [A] W | 6-DaHall 1-PDU-08 | [branch#049] [A] W | 0 | 7-DaHall 1-A-4-100-297-DaHall 1-B-4-100-29 | 7-DaHall 1-A-4-100-29 | 7-DaHall 1-B-4-100-29 | 7-DaHall 1-A-4-10 | [branch#029] [A] W | 7-DaHall 1-B-4-10 | [branch#029] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-11-20-175-DaHall 1-PDU-12-20-15 | 5-DaHall 1-PDU-11-20-17 | 5-DaHall 1-PDU-12-20-15 | 5-DaHall 1-PDU-11 | [branch#017] [A] W | 5-DaHall 1-PDU-12 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-03-30-166-DaHall 1-PDU-04-30-16 | 6-DaHall 1-PDU-03-30-16 | 6-DaHall 1-PDU-04-30-16 | 6-DaHall 1-PDU-03 | [branch#016] [A] W | 6-DaHall 1-PDU-04 | [branch#016] [A] W | 0 | 7-DaHall 1-A-4-35-347-DaHall 1-B-4-35-34 | 7-DaHall 1-A-4-35-34 | 7-DaHall 1-B-4-35-34 | 7-DaHall 1-A-4-35 | [branch#034] [A] W | 7-DaHall 1-B-4-35 | [branch#034] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-15-30-115-DaHall 1-PDU-16-30-11 | 5-DaHall 1-PDU-15-30-11 | 5-DaHall 1-PDU-16-30-11 | 5-DaHall 1-PDU-15 | [branch#011] [A] W | 5-DaHall 1-PDU-16 | [branch#011] [A] W | 0 | 6-DaHall 1-PDU-03-30-186-DaHall 1-PDU-04-30-18 | 6-DaHall 1-PDU-03-30-18 | 6-DaHall 1-PDU-04-30-18 | 6-DaHall 1-PDU-03 | [branch#018] [A] W | 6-DaHall 1-PDU-04 | [branch#018] [A] W | 0 | 7-DaHall 1-A-4-100-37-DaHall 1-B-4-100-3 | 7-DaHall 1-A-4-100-3 | 7-DaHall 1-B-4-100-3 | 7-DaHall 1-A-4-10 | [branch#003] [A] W | 7-DaHall 1-B-4-10 | [branch#003] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-15-30-145-DaHall 1-PDU-16-30-14 | 5-DaHall 1-PDU-15-30-14 | 5-DaHall 1-PDU-16-30-14 | 5-DaHall 1-PDU-15 | [branch#014] [A] W | 5-DaHall 1-PDU-16 | [branch#014] [A] W | 0.539 | [7 empty] | 0 | 7-DaHall 1-A-4-50-417-DaHall 1-B-4-50-41 | 7-DaHall 1-A-4-50-41 | 7-DaHall 1-B-4-50-41 | 7-DaHall 1-A-4-50 | [branch#041] [A] W | 7-DaHall 1-B-4-50 | [branch#041] [A] W | #N/A
4-DaHall 1-PDU-08-100-64-DaHall 1-PDU-07-100-6 | 4-DaHall 1-PDU-08-100-6 | 4-DaHall 1-PDU-07-100-6 | 4-DaHall 1-PDU-08 | [branch#006] [A] W | 4-DaHall 1-PDU-07 | [branch#006] [A] W | 6.172 | 5-DaHall 1-PDU-11-20-195-DaHall 1-PDU-12-20-17 | 5-DaHall 1-PDU-11-20-19 | 5-DaHall 1-PDU-12-20-17 | 5-DaHall 1-PDU-11 | [branch#019] [A] W | 5-DaHall 1-PDU-12 | [branch#017] [A] W | 0 | [7 empty] | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-11-20-215-DaHall 1-PDU-12-20-19 | 5-DaHall 1-PDU-11-20-21 | 5-DaHall 1-PDU-12-20-19 | 5-DaHall 1-PDU-11 | [branch#021] [A] W | 5-DaHall 1-PDU-12 | [branch#019] [A] W | 1.108 | 6-DaHall 1-PDU-07-30-86-DaHall 1-PDU-08-30-8 | 6-DaHall 1-PDU-07-30-8 | 6-DaHall 1-PDU-08-30-8 | 6-DaHall 1-PDU-07 | [branch#008] [A] W | 6-DaHall 1-PDU-08 | [branch#008] [A] W | 0 | 7-DaHall 1-PDU-01-30-57-DaHall 1-PDU-02-30-3 | 7-DaHall 1-PDU-01-30-5 | 7-DaHall 1-PDU-02-30-3 | 7-DaHall 1-PDU-01 | [branch#005] [A] W | 7-DaHall 1-PDU-02 | [branch#003] [A] W | 1.987
[7 empty] | 0 | 5-DaHall 1-PDU-11-20-235-DaHall 1-PDU-12-20-21 | 5-DaHall 1-PDU-11-20-23 | 5-DaHall 1-PDU-12-20-21 | 5-DaHall 1-PDU-11 | [branch#023] [A] W | 5-DaHall 1-PDU-12 | [branch#021] [A] W | 2.318 | 6-DaHall 1-PDU-07-30-106-DaHall 1-PDU-08-30-10 | 6-DaHall 1-PDU-07-30-10 | 6-DaHall 1-PDU-08-30-10 | 6-DaHall 1-PDU-07 | [branch#010] [A] W | 6-DaHall 1-PDU-08 | [branch#010] [A] W | 0 | 7-DaHall 1-RPP-01-30-407-DaHall 1-RPP-02-30-38 | 7-DaHall 1-RPP-01-30-40 | 7-DaHall 1-RPP-02-30-38 | 7-DaHall 1-RPP-01 | [branch#040] [A] W | 7-DaHall 1-RPP-02 | [branch#038] [A] W | 2.152
4-DaHall 1-PDU-08-100-44-DaHall 1-PDU-07-100-4 | 4-DaHall 1-PDU-08-100-4 | 4-DaHall 1-PDU-07-100-4 | 4-DaHall 1-PDU-08 | [branch#004] [A] W | 4-DaHall 1-PDU-07 | [branch#004] [A] W | 4.317 | 5-DaHall 1-PDU-11-20-255-DaHall 1-PDU-12-20-23 | 5-DaHall 1-PDU-11-20-25 | 5-DaHall 1-PDU-12-20-23 | 5-DaHall 1-PDU-11 | [branch#025] [A] W | 5-DaHall 1-PDU-12 | [branch#023] [A] W | 0 | 6-DaHall 1-PDU-07-30-126-DaHall 1-PDU-08-30-12 | 6-DaHall 1-PDU-07-30-12 | 6-DaHall 1-PDU-08-30-12 | 6-DaHall 1-PDU-07 | [branch#012] [A] W | 6-DaHall 1-PDU-08 | [branch#012] [A] W | 0 | 7-DaHall 1-RPP-01-20-257-DaHall 1-RPP-01-30-20 | 7-DaHall 1-RPP-01-20-25 | 7-DaHall 1-RPP-01-30-20 | 7-DaHall 1-RPP-01 | [branch#025] [A] W | 7-DaHall 1-RPP-01 | [branch#020] [A] W | 0.662
[7 empty] | 0 | 5-DaHall 1-PDU-15-20-285-DaHall 1-PDU-16-20-28 | 5-DaHall 1-PDU-15-20-28 | 5-DaHall 1-PDU-16-20-28 | 5-DaHall 1-PDU-15 | [branch#028] [A] W | 5-DaHall 1-PDU-16 | [branch#028] [A] W | 0.151 | 6-DaHall 1-PDU-07-30-146-DaHall 1-PDU-08-30-14 | 6-DaHall 1-PDU-07-30-14 | 6-DaHall 1-PDU-08-30-14 | 6-DaHall 1-PDU-07 | [branch#014] [A] W | 6-DaHall 1-PDU-08 | [branch#014] [A] W | 0 | 7-DaHall 1-B-4-35-467-DaHall 1-A-4-35-42 | 7-DaHall 1-B-4-35-46 | 7-DaHall 1-A-4-35-42 | 7-DaHall 1-B-4-35 | [branch#046] [A] W | 7-DaHall 1-A-4-35 | [branch#042] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-11-20-275-DaHall 1-PDU-12-20-25 | 5-DaHall 1-PDU-11-20-27 | 5-DaHall 1-PDU-12-20-25 | 5-DaHall 1-PDU-11 | [branch#027] [A] W | 5-DaHall 1-PDU-12 | [branch#025] [A] W | 1.374 | 6-DaHall 1-PDU-01-30-486-DaHall 1-PDU-02-30-48 | 6-DaHall 1-PDU-01-30-48 | 6-DaHall 1-PDU-02-30-48 | 6-DaHall 1-PDU-01 | [branch#048] [A] W | 6-DaHall 1-PDU-02 | [branch#048] [A] W | 0 | 7-DaHall 1-A-4-35-437-DaHall 1-B-4-50-47 | 7-DaHall 1-A-4-35-43 | 7-DaHall 1-B-4-50-47 | 7-DaHall 1-A-4-35 | [branch#043] [A] W | 7-DaHall 1-B-4-50 | [branch#047] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-11-20-295-DaHall 1-PDU-12-20-27 | 5-DaHall 1-PDU-11-20-29 | 5-DaHall 1-PDU-12-20-27 | 5-DaHall 1-PDU-11 | [branch#029] [A] W | 5-DaHall 1-PDU-12 | [branch#027] [A] W | 0 | 6-DaHall 1-PDU-05-30-506-DaHall 1-PDU-06-30-50 | 6-DaHall 1-PDU-05-30-50 | 6-DaHall 1-PDU-06-30-50 | 6-DaHall 1-PDU-05 | [branch#050] [A] W | 6-DaHall 1-PDU-06 | [branch#050] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-15-30-75-DaHall 1-PDU-16-30-7 | 5-DaHall 1-PDU-15-30-7 | 5-DaHall 1-PDU-16-30-7 | 5-DaHall 1-PDU-15 | [branch#007] [A] W | 5-DaHall 1-PDU-16 | [branch#007] [A] W | 1.649 | [7 empty] | 0 | 7-DaHall 1-A-4-35-447-DaHall 1-B-4-35-48 | 7-DaHall 1-A-4-35-44 | 7-DaHall 1-B-4-35-48 | 7-DaHall 1-A-4-35 | [branch#044] [A] W | 7-DaHall 1-B-4-35 | [branch#048] [A] W | #N/A
4-DaHall 1-PDU-08-100-84-DaHall 1-PDU-07-100-8 | 4-DaHall 1-PDU-08-100-8 | 4-DaHall 1-PDU-07-100-8 | 4-DaHall 1-PDU-08 | [branch#008] [A] W | 4-DaHall 1-PDU-07 | [branch#008] [A] W | 14.799 | 5-DaHall 1-PDU-15-30-95-DaHall 1-PDU-16-30-9 | 5-DaHall 1-PDU-15-30-9 | 5-DaHall 1-PDU-16-30-9 | 5-DaHall 1-PDU-15 | [branch#009] [A] W | 5-DaHall 1-PDU-16 | [branch#009] [A] W | 0.604 | [7 empty] | 0 | 7-DaHall 1-PDU-02-30-8 |  | 7-DaHall 1-PDU-02-30-8 |  |  | 7-DaHall 1-PDU-02 | [branch#008] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-13-30-35-DaHall 1-PDU-12-20-32 | 5-DaHall 1-PDU-13-30-3 | 5-DaHall 1-PDU-12-20-32 | 5-DaHall 1-PDU-13 | [branch#003] [A] W | 5-DaHall 1-PDU-12 | [branch#032] [A] W | 2.051 | 6-DaHall 1-PDU-07-30-226-DaHall 1-PDU-08-30-22 | 6-DaHall 1-PDU-07-30-22 | 6-DaHall 1-PDU-08-30-22 | 6-DaHall 1-PDU-07 | [branch#022] [A] W | 6-DaHall 1-PDU-08 | [branch#022] [A] W | 0 | 7-DaHall 1-A-4-35-507-DaHall 1-B-4-35-50 | 7-DaHall 1-A-4-35-50 | 7-DaHall 1-B-4-35-50 | 7-DaHall 1-A-4-35 | [branch#050] [A] W | 7-DaHall 1-B-4-35 | [branch#050] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-13-30-55-DaHall 1-PDU-14-30-3 | 5-DaHall 1-PDU-13-30-5 | 5-DaHall 1-PDU-14-30-3 | 5-DaHall 1-PDU-13 | [branch#005] [A] W | 5-DaHall 1-PDU-14 | [branch#003] [A] W | 1.937 | 6-DaHall 1-PDU-07-30-246-DaHall 1-PDU-08-30-24 | 6-DaHall 1-PDU-07-30-24 | 6-DaHall 1-PDU-08-30-24 | 6-DaHall 1-PDU-07 | [branch#024] [A] W | 6-DaHall 1-PDU-08 | [branch#024] [A] W | 0 | 7-DaHall 1-A-4-50-467-DaHall 1-B-4-50-49 | 7-DaHall 1-A-4-50-46 | 7-DaHall 1-B-4-50-49 | 7-DaHall 1-A-4-50 | [branch#046] [A] W | 7-DaHall 1-B-4-50 | [branch#049] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-07-30-266-DaHall 1-PDU-08-30-26 | 6-DaHall 1-PDU-07-30-26 | 6-DaHall 1-PDU-08-30-26 | 6-DaHall 1-PDU-07 | [branch#026] [A] W | 6-DaHall 1-PDU-08 | [branch#026] [A] W | 0 | 7-DaHall 1-A-4-35-547-DaHall 1-B-4-35-54 | 7-DaHall 1-A-4-35-54 | 7-DaHall 1-B-4-35-54 | 7-DaHall 1-A-4-35 | [branch#054] [A] W | 7-DaHall 1-B-4-35 | [branch#054] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-11-30-65-DaHall 1-PDU-12-30-4 | 5-DaHall 1-PDU-11-30-6 | 5-DaHall 1-PDU-12-30-4 | 5-DaHall 1-PDU-11 | [branch#006] [A] W | 5-DaHall 1-PDU-12 | [branch#004] [A] W | 0.755 | 6-DaHall 1-PDU-07-30-286-DaHall 1-PDU-08-30-28 | 6-DaHall 1-PDU-07-30-28 | 6-DaHall 1-PDU-08-30-28 | 6-DaHall 1-PDU-07 | [branch#028] [A] W | 6-DaHall 1-PDU-08 | [branch#028] [A] W | 0 | 7-DaHall 1-A-4-50-267-DaHall 1-B-4-50-26 | 7-DaHall 1-A-4-50-26 | 7-DaHall 1-B-4-50-26 | 7-DaHall 1-A-4-50 | [branch#026] [A] W | 7-DaHall 1-B-4-50 | [branch#026] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-11-20-85-DaHall 1-PDU-12-30-6 | 5-DaHall 1-PDU-11-20-8 | 5-DaHall 1-PDU-12-30-6 | 5-DaHall 1-PDU-11 | [branch#008] [A] W | 5-DaHall 1-PDU-12 | [branch#006] [A] W | 0 | 6-DaHall 1-PDU-03-30-336-DaHall 1-PDU-04-30-33 | 6-DaHall 1-PDU-03-30-33 | 6-DaHall 1-PDU-04-30-33 | 6-DaHall 1-PDU-03 | [branch#033] [A] W | 6-DaHall 1-PDU-04 | [branch#033] [A] W | 0 | 7-DaHall 1-A-4-50-287-DaHall 1-B-4-50-28 | 7-DaHall 1-A-4-50-28 | 7-DaHall 1-B-4-50-28 | 7-DaHall 1-A-4-50 | [branch#028] [A] W | 7-DaHall 1-B-4-50 | [branch#028] [A] W | #N/A
4-DaHall 1-PDU-08-100-74-DaHall 1-PDU-07-100-7 | 4-DaHall 1-PDU-08-100-7 | 4-DaHall 1-PDU-07-100-7 | 4-DaHall 1-PDU-08 | [branch#007] [A] W | 4-DaHall 1-PDU-07 | [branch#007] [A] W | 5.05 | 5-DaHall 1-PDU-11-20-105-DaHall 1-PDU-12-30-8 | 5-DaHall 1-PDU-11-20-10 | 5-DaHall 1-PDU-12-30-8 | 5-DaHall 1-PDU-11 | [branch#010] [A] W | 5-DaHall 1-PDU-12 | [branch#008] [A] W | 0 | 6-DaHall 1-PDU-03-30-356-DaHall 1-PDU-04-30-35 | 6-DaHall 1-PDU-03-30-35 | 6-DaHall 1-PDU-04-30-35 | 6-DaHall 1-PDU-03 | [branch#035] [A] W | 6-DaHall 1-PDU-04 | [branch#035] [A] W | 0 | 7-DaHall 1-PDU-01-30-97-DaHall 1-PDU-02-30-9 | 7-DaHall 1-PDU-01-30-9 | 7-DaHall 1-PDU-02-30-9 | 7-DaHall 1-PDU-01 | [branch#009] [A] W | 7-DaHall 1-PDU-02 | [branch#009] [A] W | 2.931
[7 empty] | 0 | 5-DaHall 1-PDU-11-20-125-DaHall 1-PDU-12-20-10 | 5-DaHall 1-PDU-11-20-12 | 5-DaHall 1-PDU-12-20-10 | 5-DaHall 1-PDU-11 | [branch#012] [A] W | 5-DaHall 1-PDU-12 | [branch#010] [A] W | 0 | [7 empty] | 0 | 7-DaHall 1-PDU-01-30-77-DaHall 1-PDU-02-30-7 | 7-DaHall 1-PDU-01-30-7 | 7-DaHall 1-PDU-02-30-7 | 7-DaHall 1-PDU-01 | [branch#007] [A] W | 7-DaHall 1-PDU-02 | [branch#007] [A] W | 2.694
[7 empty] | 0 | 5-DaHall 1-PDU-11-20-145-DaHall 1-PDU-12-20-12 | 5-DaHall 1-PDU-11-20-14 | 5-DaHall 1-PDU-12-20-12 | 5-DaHall 1-PDU-11 | [branch#014] [A] W | 5-DaHall 1-PDU-12 | [branch#012] [A] W | 0 | 6-DaHall 1-PDU-03-30-246-DaHall 1-PDU-04-30-24 | 6-DaHall 1-PDU-03-30-24 | 6-DaHall 1-PDU-04-30-24 | 6-DaHall 1-PDU-03 | [branch#024] [A] W | 6-DaHall 1-PDU-04 | [branch#024] [A] W | 0 | 7-DaHall 1-A-4-50-277-DaHall 1-B-4-50-57 | 7-DaHall 1-A-4-50-27 | 7-DaHall 1-B-4-50-57 | 7-DaHall 1-A-4-50 | [branch#027] [A] W | 7-DaHall 1-B-4-50 | [branch#057] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-11-20-165-DaHall 1-PDU-12-20-14 | 5-DaHall 1-PDU-11-20-16 | 5-DaHall 1-PDU-12-20-14 | 5-DaHall 1-PDU-11 | [branch#016] [A] W | 5-DaHall 1-PDU-12 | [branch#014] [A] W | 0 | 6-DaHall 1-PDU-03-30-226-DaHall 1-PDU-04-30-22 | 6-DaHall 1-PDU-03-30-22 | 6-DaHall 1-PDU-04-30-22 | 6-DaHall 1-PDU-03 | [branch#022] [A] W | 6-DaHall 1-PDU-04 | [branch#022] [A] W | 0 | 7-DaHall 1-A-4-50-337-DaHall 1-B-4-50-33 | 7-DaHall 1-A-4-50-33 | 7-DaHall 1-B-4-50-33 | 7-DaHall 1-A-4-50 | [branch#033] [A] W | 7-DaHall 1-B-4-50 | [branch#033] [A] W | #N/A
4-DaHall 1-PDU-08-100-34-DaHall 1-PDU-07-100-3 | 4-DaHall 1-PDU-08-100-3 | 4-DaHall 1-PDU-07-100-3 | 4-DaHall 1-PDU-08 | [branch#003] [A] W | 4-DaHall 1-PDU-07 | [branch#003] [A] W | 2.298 | 5-DaHall 1-PDU-11-20-185-DaHall 1-PDU-12-20-16 | 5-DaHall 1-PDU-11-20-18 | 5-DaHall 1-PDU-12-20-16 | 5-DaHall 1-PDU-11 | [branch#018] [A] W | 5-DaHall 1-PDU-12 | [branch#016] [A] W | 2.145 | 6-DaHall 1-PDU-03-30-266-DaHall 1-PDU-04-30-26 | 6-DaHall 1-PDU-03-30-26 | 6-DaHall 1-PDU-04-30-26 | 6-DaHall 1-PDU-03 | [branch#026] [A] W | 6-DaHall 1-PDU-04 | [branch#026] [A] W | 0 | 7-DaHall 1-A-4-50-107-DaHall 1-B-4-50-43 | 7-DaHall 1-A-4-50-10 | 7-DaHall 1-B-4-50-43 | 7-DaHall 1-A-4-50 | [branch#010] [A] W | 7-DaHall 1-B-4-50 | [branch#043] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-11-20-205-DaHall 1-PDU-12-20-18 | 5-DaHall 1-PDU-11-20-20 | 5-DaHall 1-PDU-12-20-18 | 5-DaHall 1-PDU-11 | [branch#020] [A] W | 5-DaHall 1-PDU-12 | [branch#018] [A] W | 1.145 | 6-DaHall 1-PDU-03-30-386-DaHall 1-PDU-04-30-38 | 6-DaHall 1-PDU-03-30-38 | 6-DaHall 1-PDU-04-30-38 | 6-DaHall 1-PDU-03 | [branch#038] [A] W | 6-DaHall 1-PDU-04 | [branch#038] [A] W | 0 | 7-DaHall 1-A-4-50-117-DaHall 1-B-4-50-44 | 7-DaHall 1-A-4-50-11 | 7-DaHall 1-B-4-50-44 | 7-DaHall 1-A-4-50 | [branch#011] [A] W | 7-DaHall 1-B-4-50 | [branch#044] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-13-20-115-DaHall 1-PDU-14-30-9 | 5-DaHall 1-PDU-13-20-11 | 5-DaHall 1-PDU-14-30-9 | 5-DaHall 1-PDU-13 | [branch#011] [A] W | 5-DaHall 1-PDU-14 | [branch#009] [A] W | 0 | 6-DaHall 1-PDU-03-30-286-DaHall 1-PDU-04-30-28 | 6-DaHall 1-PDU-03-30-28 | 6-DaHall 1-PDU-04-30-28 | 6-DaHall 1-PDU-03 | [branch#028] [A] W | 6-DaHall 1-PDU-04 | [branch#028] [A] W | 0 | 7-DaHall 1-A-4-50-187-DaHall 1-B-4-50-45 | 7-DaHall 1-A-4-50-18 | 7-DaHall 1-B-4-50-45 | 7-DaHall 1-A-4-50 | [branch#018] [A] W | 7-DaHall 1-B-4-50 | [branch#045] [A] W | #N/A
4-DaHall 1-PDU-08-100-54-DaHall 1-PDU-07-100-5 | 4-DaHall 1-PDU-08-100-5 | 4-DaHall 1-PDU-07-100-5 | 4-DaHall 1-PDU-08 | [branch#005] [A] W | 4-DaHall 1-PDU-07 | [branch#005] [A] W | 2.946 | 5-DaHall 1-PDU-13-20-135-DaHall 1-PDU-14-20-11 | 5-DaHall 1-PDU-13-20-13 | 5-DaHall 1-PDU-14-20-11 | 5-DaHall 1-PDU-13 | [branch#013] [A] W | 5-DaHall 1-PDU-14 | [branch#011] [A] W | 0.108 | 6-DaHall 1-PDU-03-30-306-DaHall 1-PDU-04-30-30 | 6-DaHall 1-PDU-03-30-30 | 6-DaHall 1-PDU-04-30-30 | 6-DaHall 1-PDU-03 | [branch#030] [A] W | 6-DaHall 1-PDU-04 | [branch#030] [A] W | 0 | 7-DaHall 1-A-4-50-457-DaHall 1-B-4-50-51 | 7-DaHall 1-A-4-50-45 | 7-DaHall 1-B-4-50-51 | 7-DaHall 1-A-4-50 | [branch#045] [A] W | 7-DaHall 1-B-4-50 | [branch#051] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-13-20-155-DaHall 1-PDU-14-20-13 | 5-DaHall 1-PDU-13-20-15 | 5-DaHall 1-PDU-14-20-13 | 5-DaHall 1-PDU-13 | [branch#015] [A] W | 5-DaHall 1-PDU-14 | [branch#013] [A] W | 0.353 | 6-DaHall 1-PDU-03-30-326-DaHall 1-PDU-04-30-32 | 6-DaHall 1-PDU-03-30-32 | 6-DaHall 1-PDU-04-30-32 | 6-DaHall 1-PDU-03 | [branch#032] [A] W | 6-DaHall 1-PDU-04 | [branch#032] [A] W | 0 | 7-DaHall 1-A-4-35-527-DaHall 1-B-4-35-52 | 7-DaHall 1-A-4-35-52 | 7-DaHall 1-B-4-35-52 | 7-DaHall 1-A-4-35 | [branch#052] [A] W | 7-DaHall 1-B-4-35 | [branch#052] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-13-20-175-DaHall 1-PDU-14-20-15 | 5-DaHall 1-PDU-13-20-17 | 5-DaHall 1-PDU-14-20-15 | 5-DaHall 1-PDU-13 | [branch#017] [A] W | 5-DaHall 1-PDU-14 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-03-30-346-DaHall 1-PDU-04-30-34 | 6-DaHall 1-PDU-03-30-34 | 6-DaHall 1-PDU-04-30-34 | 6-DaHall 1-PDU-03 | [branch#034] [A] W | 6-DaHall 1-PDU-04 | [branch#034] [A] W | 0 | 7-DaHall 1-A-4-35-537-DaHall 1-B-4-35-53 | 7-DaHall 1-A-4-35-53 | 7-DaHall 1-B-4-35-53 | 7-DaHall 1-A-4-35 | [branch#053] [A] W | 7-DaHall 1-B-4-35 | [branch#053] [A] W | #N/A
4-DaHall 1-PDU-08-100-14-DaHall 1-PDU-07-100-1 | 4-DaHall 1-PDU-08-100-1 | 4-DaHall 1-PDU-07-100-1 | 4-DaHall 1-PDU-08 | [branch#001] [A] W | 4-DaHall 1-PDU-07 | [branch#001] [A] W | 9.848 | 5-DaHall 1-PDU-15-30-125-DaHall 1-PDU-16-30-12 | 5-DaHall 1-PDU-15-30-12 | 5-DaHall 1-PDU-16-30-12 | 5-DaHall 1-PDU-15 | [branch#012] [A] W | 5-DaHall 1-PDU-16 | [branch#012] [A] W | 0.856 | 6-DaHall 1-PDU-03-30-366-DaHall 1-PDU-04-30-36 | 6-DaHall 1-PDU-03-30-36 | 6-DaHall 1-PDU-04-30-36 | 6-DaHall 1-PDU-03 | [branch#036] [A] W | 6-DaHall 1-PDU-04 | [branch#036] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-13-20-195-DaHall 1-PDU-14-20-17 | 5-DaHall 1-PDU-13-20-19 | 5-DaHall 1-PDU-14-20-17 | 5-DaHall 1-PDU-13 | [branch#019] [A] W | 5-DaHall 1-PDU-14 | [branch#017] [A] W | 1.382 | [7 empty] | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-11-20-225-DaHall 1-PDU-12-20-22 | 5-DaHall 1-PDU-11-20-22 | 5-DaHall 1-PDU-12-20-22 | 5-DaHall 1-PDU-11 | [branch#022] [A] W | 5-DaHall 1-PDU-12 | [branch#022] [A] W | 0 | [7 empty] | 0 | 7-DaHall 1-A-3-50-477-DaHall 1-B-3-50-47 | 7-DaHall 1-A-3-50-47 | 7-DaHall 1-B-3-50-47 | 7-DaHall 1-A-3-50 | [branch#047] [A] W | 7-DaHall 1-B-3-50 | [branch#047] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-13-20-215-DaHall 1-PDU-14-20-19 | 5-DaHall 1-PDU-13-20-21 | 5-DaHall 1-PDU-14-20-19 | 5-DaHall 1-PDU-13 | [branch#021] [A] W | 5-DaHall 1-PDU-14 | [branch#019] [A] W | 1.267 | 6-DaHall 1-PDU-03-30-406-DaHall 1-PDU-04-30-40 | 6-DaHall 1-PDU-03-30-40 | 6-DaHall 1-PDU-04-30-40 | 6-DaHall 1-PDU-03 | [branch#040] [A] W | 6-DaHall 1-PDU-04 | [branch#040] [A] W | 0 | 7-DaHall 1-A-3-50-467-DaHall 1-B-3-50-46 | 7-DaHall 1-A-3-50-46 | 7-DaHall 1-B-3-50-46 | 7-DaHall 1-A-3-50 | [branch#046] [A] W | 7-DaHall 1-B-3-50 | [branch#046] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-13-20-235-DaHall 1-PDU-14-20-21 | 5-DaHall 1-PDU-13-20-23 | 5-DaHall 1-PDU-14-20-21 | 5-DaHall 1-PDU-13 | [branch#023] [A] W | 5-DaHall 1-PDU-14 | [branch#021] [A] W | 2.987 | 6-DaHall 1-PDU-03-30-426-DaHall 1-PDU-04-30-42 | 6-DaHall 1-PDU-03-30-42 | 6-DaHall 1-PDU-04-30-42 | 6-DaHall 1-PDU-03 | [branch#042] [A] W | 6-DaHall 1-PDU-04 | [branch#042] [A] W | 0 | 7-DaHall 1-A-3-50-447-DaHall 1-B-3-50-44 | 7-DaHall 1-A-3-50-44 | 7-DaHall 1-B-3-50-44 | 7-DaHall 1-A-3-50 | [branch#044] [A] W | 7-DaHall 1-B-3-50 | [branch#044] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-11-20-30 | 5-DaHall 1-PDU-11-20-30 |  | 5-DaHall 1-PDU-11 | [branch#030] [A] W |  |  | 0 | 6-DaHall 1-PDU-03-30-446-DaHall 1-PDU-04-30-44 | 6-DaHall 1-PDU-03-30-44 | 6-DaHall 1-PDU-04-30-44 | 6-DaHall 1-PDU-03 | [branch#044] [A] W | 6-DaHall 1-PDU-04 | [branch#044] [A] W | 0 | 7-DaHall 1-PDU-01-30-487-DaHall 1-PDU-02-30-48 | 7-DaHall 1-PDU-01-30-48 | 7-DaHall 1-PDU-02-30-48 | 7-DaHall 1-PDU-01 | [branch#048] [A] W | 7-DaHall 1-PDU-02 | [branch#048] [A] W | 1.483
4-DaHall 1-PDU-08-100-104-DaHall 1-PDU-07-100-10 | 4-DaHall 1-PDU-08-100-10 | 4-DaHall 1-PDU-07-100-10 | 4-DaHall 1-PDU-08 | [branch#010] [A] W | 4-DaHall 1-PDU-07 | [branch#010] [A] W | 0 | 5-DaHall 1-PDU-13-20-255-DaHall 1-PDU-14-20-23 | 5-DaHall 1-PDU-13-20-25 | 5-DaHall 1-PDU-14-20-23 | 5-DaHall 1-PDU-13 | [branch#025] [A] W | 5-DaHall 1-PDU-14 | [branch#023] [A] W | 1.093 | 6-DaHall 1-PDU-03-30-466-DaHall 1-PDU-04-30-46 | 6-DaHall 1-PDU-03-30-46 | 6-DaHall 1-PDU-04-30-46 | 6-DaHall 1-PDU-03 | [branch#046] [A] W | 6-DaHall 1-PDU-04 | [branch#046] [A] W | 0 | 7-DaHall 1-A-3-50-417-DaHall 1-B-3-50-41 | 7-DaHall 1-A-3-50-41 | 7-DaHall 1-B-3-50-41 | 7-DaHall 1-A-3-50 | [branch#041] [A] W | 7-DaHall 1-B-3-50 | [branch#041] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-13-20-315-DaHall 1-PDU-14-20-29 | 5-DaHall 1-PDU-13-20-31 | 5-DaHall 1-PDU-14-20-29 | 5-DaHall 1-PDU-13 | [branch#031] [A] W | 5-DaHall 1-PDU-14 | [branch#029] [A] W | 0 | 6-DaHall 1-PDU-03-30-486-DaHall 1-PDU-04-30-48 | 6-DaHall 1-PDU-03-30-48 | 6-DaHall 1-PDU-04-30-48 | 6-DaHall 1-PDU-03 | [branch#048] [A] W | 6-DaHall 1-PDU-04 | [branch#048] [A] W | 0 | 7-DaHall 1-A-3-50-107-DaHall 1-B-3-50-10 | 7-DaHall 1-A-3-50-10 | 7-DaHall 1-B-3-50-10 | 7-DaHall 1-A-3-50 | [branch#010] [A] W | 7-DaHall 1-B-3-50 | [branch#010] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-13-30-45-DaHall 1-PDU-14-20-31 | 5-DaHall 1-PDU-13-30-4 | 5-DaHall 1-PDU-14-20-31 | 5-DaHall 1-PDU-13 | [branch#004] [A] W | 5-DaHall 1-PDU-14 | [branch#031] [A] W | 0 | 6-DaHall 1-PDU-07-30-456-DaHall 1-PDU-08-30-47 | 6-DaHall 1-PDU-07-30-45 | 6-DaHall 1-PDU-08-30-47 | 6-DaHall 1-PDU-07 | [branch#045] [A] W | 6-DaHall 1-PDU-08 | [branch#047] [A] W | 0 | 7-DaHall 1-A-3-50-77-DaHall 1-B-3-50-7 | 7-DaHall 1-A-3-50-7 | 7-DaHall 1-B-3-50-7 | 7-DaHall 1-A-3-50 | [branch#007] [A] W | 7-DaHall 1-B-3-50 | [branch#007] [A] W | #N/A
4-DaHall 1-PDU-08-100-94-DaHall 1-PDU-07-100-9 | 4-DaHall 1-PDU-08-100-9 | 4-DaHall 1-PDU-07-100-9 | 4-DaHall 1-PDU-08 | [branch#009] [A] W | 4-DaHall 1-PDU-07 | [branch#009] [A] W | 0 | 5-DaHall 1-PDU-13-30-65-DaHall 1-PDU-14-30-4 | 5-DaHall 1-PDU-13-30-6 | 5-DaHall 1-PDU-14-30-4 | 5-DaHall 1-PDU-13 | [branch#006] [A] W | 5-DaHall 1-PDU-14 | [branch#004] [A] W | 2.953 | 6-DaHall 1-PDU-05-30-16-DaHall 1-PDU-06-30-1 | 6-DaHall 1-PDU-05-30-1 | 6-DaHall 1-PDU-06-30-1 | 6-DaHall 1-PDU-05 | [branch#001] [A] W | 6-DaHall 1-PDU-06 | [branch#001] [A] W | 0 | 7-DaHall 1-A-3-50-67-DaHall 1-B-3-50-6 | 7-DaHall 1-A-3-50-6 | 7-DaHall 1-B-3-50-6 | 7-DaHall 1-A-3-50 | [branch#006] [A] W | 7-DaHall 1-B-3-50 | [branch#006] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-13-30-85-DaHall 1-PDU-14-30-6 | 5-DaHall 1-PDU-13-30-8 | 5-DaHall 1-PDU-14-30-6 | 5-DaHall 1-PDU-13 | [branch#008] [A] W | 5-DaHall 1-PDU-14 | [branch#006] [A] W | 1.54 | 6-DaHall 1-PDU-07-30-436-DaHall 1-PDU-08-30-45 | 6-DaHall 1-PDU-07-30-43 | 6-DaHall 1-PDU-08-30-45 | 6-DaHall 1-PDU-07 | [branch#043] [A] W | 6-DaHall 1-PDU-08 | [branch#045] [A] W | 0 | 7-DaHall 1-A-3-50-57-DaHall 1-B-3-50-5 | 7-DaHall 1-A-3-50-5 | 7-DaHall 1-B-3-50-5 | 7-DaHall 1-A-3-50 | [branch#005] [A] W | 7-DaHall 1-B-3-50 | [branch#005] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-13-30-105-DaHall 1-PDU-14-30-8 | 5-DaHall 1-PDU-13-30-10 | 5-DaHall 1-PDU-14-30-8 | 5-DaHall 1-PDU-13 | [branch#010] [A] W | 5-DaHall 1-PDU-14 | [branch#008] [A] W | 0 | 6-DaHall 1-PDU-05-30-36-DaHall 1-PDU-06-30-3 | 6-DaHall 1-PDU-05-30-3 | 6-DaHall 1-PDU-06-30-3 | 6-DaHall 1-PDU-05 | [branch#003] [A] W | 6-DaHall 1-PDU-06 | [branch#003] [A] W | 0 | 7-DaHall 1-A-2-50-487-DaHall 1-B-2-50-48 | 7-DaHall 1-A-2-50-48 | 7-DaHall 1-B-2-50-48 | 7-DaHall 1-A-2-50 | [branch#048] [A] W | 7-DaHall 1-B-2-50 | [branch#048] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-13-20-125-DaHall 1-PDU-14-30-10 | 5-DaHall 1-PDU-13-20-12 | 5-DaHall 1-PDU-14-30-10 | 5-DaHall 1-PDU-13 | [branch#012] [A] W | 5-DaHall 1-PDU-14 | [branch#010] [A] W | 0 | 6-DaHall 1-PDU-07-30-416-DaHall 1-PDU-08-30-43 | 6-DaHall 1-PDU-07-30-41 | 6-DaHall 1-PDU-08-30-43 | 6-DaHall 1-PDU-07 | [branch#041] [A] W | 6-DaHall 1-PDU-08 | [branch#043] [A] W | 0 | 7-DaHall 1-A-2-35-477-DaHall 1-B-2-35-47 | 7-DaHall 1-A-2-35-47 | 7-DaHall 1-B-2-35-47 | 7-DaHall 1-A-2-35 | [branch#047] [A] W | 7-DaHall 1-B-2-35 | [branch#047] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-13-20-145-DaHall 1-PDU-14-20-12 | 5-DaHall 1-PDU-13-20-14 | 5-DaHall 1-PDU-14-20-12 | 5-DaHall 1-PDU-13 | [branch#014] [A] W | 5-DaHall 1-PDU-14 | [branch#012] [A] W | 0 | [7 empty] | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-13-20-165-DaHall 1-PDU-14-20-14 | 5-DaHall 1-PDU-13-20-16 | 5-DaHall 1-PDU-14-20-14 | 5-DaHall 1-PDU-13 | [branch#016] [A] W | 5-DaHall 1-PDU-14 | [branch#014] [A] W | 1.577 | [7 empty] | 0 | 7-DaHall 1-A-2-35-537-DaHall 1-B-2-35-53 | 7-DaHall 1-A-2-35-53 | 7-DaHall 1-B-2-35-53 | 7-DaHall 1-A-2-35 | [branch#053] [A] W | 7-DaHall 1-B-2-35 | [branch#053] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-11-20-245-DaHall 1-PDU-12-20-24 | 5-DaHall 1-PDU-11-20-24 | 5-DaHall 1-PDU-12-20-24 | 5-DaHall 1-PDU-11 | [branch#024] [A] W | 5-DaHall 1-PDU-12 | [branch#024] [A] W | 0.778 | 6-DaHall 1-PDU-05-30-76-DaHall 1-PDU-06-30-7 | 6-DaHall 1-PDU-05-30-7 | 6-DaHall 1-PDU-06-30-7 | 6-DaHall 1-PDU-05 | [branch#007] [A] W | 6-DaHall 1-PDU-06 | [branch#007] [A] W | 0 | 7-DaHall 1-A-2-16-447-DaHall 1-B-2-16-46 | 7-DaHall 1-A-2-16-44 | 7-DaHall 1-B-2-16-46 | 7-DaHall 1-A-2-16 | [branch#044] [A] W | 7-DaHall 1-B-2-16 | [branch#046] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-13-20-225-DaHall 1-PDU-14-20-20 | 5-DaHall 1-PDU-13-20-22 | 5-DaHall 1-PDU-14-20-20 | 5-DaHall 1-PDU-13 | [branch#022] [A] W | 5-DaHall 1-PDU-14 | [branch#020] [A] W | 0 | 6-DaHall 1-PDU-05-30-96-DaHall 1-PDU-06-30-9 | 6-DaHall 1-PDU-05-30-9 | 6-DaHall 1-PDU-06-30-9 | 6-DaHall 1-PDU-05 | [branch#009] [A] W | 6-DaHall 1-PDU-06 | [branch#009] [A] W | 0 | [7 empty] | 0
4-DaHall 1-PDU-06-100-104-DaHall 1-PDU-05-100-10 | 4-DaHall 1-PDU-06-100-10 | 4-DaHall 1-PDU-05-100-10 | 4-DaHall 1-PDU-06 | [branch#010] [A] W | 4-DaHall 1-PDU-05 | [branch#010] [A] W | 15.148 | 5-DaHall 1-PDU-13-20-245-DaHall 1-PDU-14-20-22 | 5-DaHall 1-PDU-13-20-24 | 5-DaHall 1-PDU-14-20-22 | 5-DaHall 1-PDU-13 | [branch#024] [A] W | 5-DaHall 1-PDU-14 | [branch#022] [A] W | 0 | 6-DaHall 1-PDU-05-30-116-DaHall 1-PDU-06-30-11 | 6-DaHall 1-PDU-05-30-11 | 6-DaHall 1-PDU-06-30-11 | 6-DaHall 1-PDU-05 | [branch#011] [A] W | 6-DaHall 1-PDU-06 | [branch#011] [A] W | 0.669 | 7-DaHall 1-A-2-35-587-DaHall 1-B-2-35-58 | 7-DaHall 1-A-2-35-58 | 7-DaHall 1-B-2-35-58 | 7-DaHall 1-A-2-35 | [branch#058] [A] W | 7-DaHall 1-B-2-35 | [branch#058] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-13-20-265-DaHall 1-PDU-14-20-24 | 5-DaHall 1-PDU-13-20-26 | 5-DaHall 1-PDU-14-20-24 | 5-DaHall 1-PDU-13 | [branch#026] [A] W | 5-DaHall 1-PDU-14 | [branch#024] [A] W | 1.541 | 6-DaHall 1-PDU-05-30-136-DaHall 1-PDU-06-30-13 | 6-DaHall 1-PDU-05-30-13 | 6-DaHall 1-PDU-06-30-13 | 6-DaHall 1-PDU-05 | [branch#013] [A] W | 6-DaHall 1-PDU-06 | [branch#013] [A] W | 0.979 | 7-DaHall 1-RPP-01-20-7 | 7-DaHall 1-RPP-01-20-7 |  | 7-DaHall 1-RPP-01 | [branch#007] [A] W |  |  | 0
[7 empty] | 0 | 5-DaHall 1-PDU-15-30-105-DaHall 1-PDU-16-30-10 | 5-DaHall 1-PDU-15-30-10 | 5-DaHall 1-PDU-16-30-10 | 5-DaHall 1-PDU-15 | [branch#010] [A] W | 5-DaHall 1-PDU-16 | [branch#010] [A] W | 1.57 | 6-DaHall 1-PDU-05-30-156-DaHall 1-PDU-06-30-15 | 6-DaHall 1-PDU-05-30-15 | 6-DaHall 1-PDU-06-30-15 | 6-DaHall 1-PDU-05 | [branch#015] [A] W | 6-DaHall 1-PDU-06 | [branch#015] [A] W | 1.382 | 7-DaHall 1-A-2-50-237-DaHall 1-B-2-50-23 | 7-DaHall 1-A-2-50-23 | 7-DaHall 1-B-2-50-23 | 7-DaHall 1-A-2-50 | [branch#023] [A] W | 7-DaHall 1-B-2-50 | [branch#023] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-13-20-285-DaHall 1-PDU-14-20-26 | 5-DaHall 1-PDU-13-20-28 | 5-DaHall 1-PDU-14-20-26 | 5-DaHall 1-PDU-13 | [branch#028] [A] W | 5-DaHall 1-PDU-14 | [branch#026] [A] W | 0 | 6-DaHall 1-PDU-05-30-176-DaHall 1-PDU-06-30-17 | 6-DaHall 1-PDU-05-30-17 | 6-DaHall 1-PDU-06-30-17 | 6-DaHall 1-PDU-05 | [branch#017] [A] W | 6-DaHall 1-PDU-06 | [branch#017] [A] W | 0.402 | 7-DaHall 1-A-2-50-77-DaHall 1-B-2-50-7 | 7-DaHall 1-A-2-50-7 | 7-DaHall 1-B-2-50-7 | 7-DaHall 1-A-2-50 | [branch#007] [A] W | 7-DaHall 1-B-2-50 | [branch#007] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-15-30-85-DaHall 1-PDU-16-30-8 | 5-DaHall 1-PDU-15-30-8 | 5-DaHall 1-PDU-16-30-8 | 5-DaHall 1-PDU-15 | [branch#008] [A] W | 5-DaHall 1-PDU-16 | [branch#008] [A] W | 1.8 | 6-DaHall 1-PDU-05-30-196-DaHall 1-PDU-06-30-19 | 6-DaHall 1-PDU-05-30-19 | 6-DaHall 1-PDU-06-30-19 | 6-DaHall 1-PDU-05 | [branch#019] [A] W | 6-DaHall 1-PDU-06 | [branch#019] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-13-20-305-DaHall 1-PDU-14-20-28 | 5-DaHall 1-PDU-13-20-30 | 5-DaHall 1-PDU-14-20-28 | 5-DaHall 1-PDU-13 | [branch#030] [A] W | 5-DaHall 1-PDU-14 | [branch#028] [A] W | 0 | [7 empty] | 0 | 7-DaHall 1-A-2-35-627-DaHall 1-B-2-35-62 | 7-DaHall 1-A-2-35-62 | 7-DaHall 1-B-2-35-62 | 7-DaHall 1-A-2-35 | [branch#062] [A] W | 7-DaHall 1-B-2-35 | [branch#062] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-13-20-325-DaHall 1-PDU-14-20-30 | 5-DaHall 1-PDU-13-20-32 | 5-DaHall 1-PDU-14-20-30 | 5-DaHall 1-PDU-13 | [branch#032] [A] W | 5-DaHall 1-PDU-14 | [branch#030] [A] W | 0 | [7 empty] | 0 | 7-DaHall 1-A-2-35-637-DaHall 1-B-2-35-63 | 7-DaHall 1-A-2-35-63 | 7-DaHall 1-B-2-35-63 | 7-DaHall 1-A-2-35 | [branch#063] [A] W | 7-DaHall 1-B-2-35 | [branch#063] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-325-DaHall 1-PDU-04-30-32 | 5-DaHall 1-PDU-03-30-32 | 5-DaHall 1-PDU-04-30-32 | 5-DaHall 1-PDU-03 | [branch#032] [A] W | 5-DaHall 1-PDU-04 | [branch#032] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-A-3-50-577-DaHall 1-B-3-50-57 | 7-DaHall 1-A-3-50-57 | 7-DaHall 1-B-3-50-57 | 7-DaHall 1-A-3-50 | [branch#057] [A] W | 7-DaHall 1-B-3-50 | [branch#057] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-345-DaHall 1-PDU-04-30-34 | 5-DaHall 1-PDU-03-30-34 | 5-DaHall 1-PDU-04-30-34 | 5-DaHall 1-PDU-03 | [branch#034] [A] W | 5-DaHall 1-PDU-04 | [branch#034] [A] W | #N/A | 6-DaHall 1-PDU-05-30-256-DaHall 1-PDU-06-30-25 | 6-DaHall 1-PDU-05-30-25 | 6-DaHall 1-PDU-06-30-25 | 6-DaHall 1-PDU-05 | [branch#025] [A] W | 6-DaHall 1-PDU-06 | [branch#025] [A] W | 4.364 | 7-DaHall 1-A-3-50-587-DaHall 1-B-3-50-58 | 7-DaHall 1-A-3-50-58 | 7-DaHall 1-B-3-50-58 | 7-DaHall 1-A-3-50 | [branch#058] [A] W | 7-DaHall 1-B-3-50 | [branch#058] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-365-DaHall 1-PDU-04-30-36 | 5-DaHall 1-PDU-03-30-36 | 5-DaHall 1-PDU-04-30-36 | 5-DaHall 1-PDU-03 | [branch#036] [A] W | 5-DaHall 1-PDU-04 | [branch#036] [A] W | #N/A | 6-DaHall 1-PDU-05-30-276-DaHall 1-PDU-06-30-27 | 6-DaHall 1-PDU-05-30-27 | 6-DaHall 1-PDU-06-30-27 | 6-DaHall 1-PDU-05 | [branch#027] [A] W | 6-DaHall 1-PDU-06 | [branch#027] [A] W | 2.671 | 7-DaHall 1-A-3-100-17-DaHall 1-B-3-100-1 | 7-DaHall 1-A-3-100-1 | 7-DaHall 1-B-3-100-1 | 7-DaHall 1-A-3-10 | [branch#001] [A] W | 7-DaHall 1-B-3-10 | [branch#001] [A] W | #N/A
4-DaHall 1-PDU-06-100-94-DaHall 1-PDU-05-100-9 | 4-DaHall 1-PDU-06-100-9 | 4-DaHall 1-PDU-05-100-9 | 4-DaHall 1-PDU-06 | [branch#009] [A] W | 4-DaHall 1-PDU-05 | [branch#009] [A] W | 0 | 5-DaHall 1-PDU-03-30-385-DaHall 1-PDU-04-30-38 | 5-DaHall 1-PDU-03-30-38 | 5-DaHall 1-PDU-04-30-38 | 5-DaHall 1-PDU-03 | [branch#038] [A] W | 5-DaHall 1-PDU-04 | [branch#038] [A] W | #N/A | 6-DaHall 1-PDU-05-30-296-DaHall 1-PDU-06-30-29 | 6-DaHall 1-PDU-05-30-29 | 6-DaHall 1-PDU-06-30-29 | 6-DaHall 1-PDU-05 | [branch#029] [A] W | 6-DaHall 1-PDU-06 | [branch#029] [A] W | 0 | 7-DaHall 1-A-3-100-27-DaHall 1-B-3-100-2 | 7-DaHall 1-A-3-100-2 | 7-DaHall 1-B-3-100-2 | 7-DaHall 1-A-3-10 | [branch#002] [A] W | 7-DaHall 1-B-3-10 | [branch#002] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-405-DaHall 1-PDU-04-30-40 | 5-DaHall 1-PDU-03-30-40 | 5-DaHall 1-PDU-04-30-40 | 5-DaHall 1-PDU-03 | [branch#040] [A] W | 5-DaHall 1-PDU-04 | [branch#040] [A] W | #N/A | 6-DaHall 1-PDU-05-30-236-DaHall 1-PDU-06-30-23 | 6-DaHall 1-PDU-05-30-23 | 6-DaHall 1-PDU-06-30-23 | 6-DaHall 1-PDU-05 | [branch#023] [A] W | 6-DaHall 1-PDU-06 | [branch#023] [A] W | 0 | 7-DaHall 1-A-3-50-37-DaHall 1-B-3-50-3 | 7-DaHall 1-A-3-50-3 | 7-DaHall 1-B-3-50-3 | 7-DaHall 1-A-3-50 | [branch#003] [A] W | 7-DaHall 1-B-3-50 | [branch#003] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-425-DaHall 1-PDU-04-30-42 | 5-DaHall 1-PDU-03-30-42 | 5-DaHall 1-PDU-04-30-42 | 5-DaHall 1-PDU-03 | [branch#042] [A] W | 5-DaHall 1-PDU-04 | [branch#042] [A] W | #N/A | 6-DaHall 1-PDU-05-30-316-DaHall 1-PDU-06-30-31 | 6-DaHall 1-PDU-05-30-31 | 6-DaHall 1-PDU-06-30-31 | 6-DaHall 1-PDU-05 | [branch#031] [A] W | 6-DaHall 1-PDU-06 | [branch#031] [A] W | 0.432 | 7-DaHall 1-A-3-50-427-DaHall 1-B-3-50-42 | 7-DaHall 1-A-3-50-42 | 7-DaHall 1-B-3-50-42 | 7-DaHall 1-A-3-50 | [branch#042] [A] W | 7-DaHall 1-B-3-50 | [branch#042] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-445-DaHall 1-PDU-04-30-44 | 5-DaHall 1-PDU-03-30-44 | 5-DaHall 1-PDU-04-30-44 | 5-DaHall 1-PDU-03 | [branch#044] [A] W | 5-DaHall 1-PDU-04 | [branch#044] [A] W | #N/A | 6-DaHall 1-PDU-05-30-336-DaHall 1-PDU-06-30-33 | 6-DaHall 1-PDU-05-30-33 | 6-DaHall 1-PDU-06-30-33 | 6-DaHall 1-PDU-05 | [branch#033] [A] W | 6-DaHall 1-PDU-06 | [branch#033] [A] W | 0.416 | 7-DaHall 1-A-3-50-437-DaHall 1-B-3-50-43 | 7-DaHall 1-A-3-50-43 | 7-DaHall 1-B-3-50-43 | 7-DaHall 1-A-3-50 | [branch#043] [A] W | 7-DaHall 1-B-3-50 | [branch#043] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-465-DaHall 1-PDU-04-30-46 | 5-DaHall 1-PDU-03-30-46 | 5-DaHall 1-PDU-04-30-46 | 5-DaHall 1-PDU-03 | [branch#046] [A] W | 5-DaHall 1-PDU-04 | [branch#046] [A] W | #N/A | 6-DaHall 1-PDU-05-30-356-DaHall 1-PDU-06-30-35 | 6-DaHall 1-PDU-05-30-35 | 6-DaHall 1-PDU-06-30-35 | 6-DaHall 1-PDU-05 | [branch#035] [A] W | 6-DaHall 1-PDU-06 | [branch#035] [A] W | 0.193 | 7-DaHall 1-A-3-50-277-DaHall 1-B-3-50-27 | 7-DaHall 1-A-3-50-27 | 7-DaHall 1-B-3-50-27 | 7-DaHall 1-A-3-50 | [branch#027] [A] W | 7-DaHall 1-B-3-50 | [branch#027] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-485-DaHall 1-PDU-04-30-48 | 5-DaHall 1-PDU-03-30-48 | 5-DaHall 1-PDU-04-30-48 | 5-DaHall 1-PDU-03 | [branch#048] [A] W | 5-DaHall 1-PDU-04 | [branch#048] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-A-3-50-267-DaHall 1-B-3-50-26 | 7-DaHall 1-A-3-50-26 | 7-DaHall 1-B-3-50-26 | 7-DaHall 1-A-3-50 | [branch#026] [A] W | 7-DaHall 1-B-3-50 | [branch#026] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-505-DaHall 1-PDU-04-30-50 | 5-DaHall 1-PDU-03-30-50 | 5-DaHall 1-PDU-04-30-50 | 5-DaHall 1-PDU-03 | [branch#050] [A] W | 5-DaHall 1-PDU-04 | [branch#050] [A] W | #N/A | 6-DaHall 1-PDU-11-30-236-DaHall 1-PDU-12-30-23 | 6-DaHall 1-PDU-11-30-23 | 6-DaHall 1-PDU-12-30-23 | 6-DaHall 1-PDU-11 | [branch#023] [A] W | 6-DaHall 1-PDU-12 | [branch#023] [A] W | 0 | 7-DaHall 1-A-3-35-537-DaHall 1-B-3-35-52 | 7-DaHall 1-A-3-35-53 | 7-DaHall 1-B-3-35-52 | 7-DaHall 1-A-3-35 | [branch#053] [A] W | 7-DaHall 1-B-3-35 | [branch#052] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-475-DaHall 1-PDU-04-30-47 | 5-DaHall 1-PDU-03-30-47 | 5-DaHall 1-PDU-04-30-47 | 5-DaHall 1-PDU-03 | [branch#047] [A] W | 5-DaHall 1-PDU-04 | [branch#047] [A] W | #N/A | 6-DaHall 1-PDU-11-30-256-DaHall 1-PDU-12-30-25 | 6-DaHall 1-PDU-11-30-25 | 6-DaHall 1-PDU-12-30-25 | 6-DaHall 1-PDU-11 | [branch#025] [A] W | 6-DaHall 1-PDU-12 | [branch#025] [A] W | 0 | 7-DaHall 1-A-2-35-527-DaHall 1-B-2-35-52 | 7-DaHall 1-A-2-35-52 | 7-DaHall 1-B-2-35-52 | 7-DaHall 1-A-2-35 | [branch#052] [A] W | 7-DaHall 1-B-2-35 | [branch#052] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-495-DaHall 1-PDU-04-30-49 | 5-DaHall 1-PDU-03-30-49 | 5-DaHall 1-PDU-04-30-49 | 5-DaHall 1-PDU-03 | [branch#049] [A] W | 5-DaHall 1-PDU-04 | [branch#049] [A] W | #N/A | 6-DaHall 1-PDU-11-30-276-DaHall 1-PDU-12-30-27 | 6-DaHall 1-PDU-11-30-27 | 6-DaHall 1-PDU-12-30-27 | 6-DaHall 1-PDU-11 | [branch#027] [A] W | 6-DaHall 1-PDU-12 | [branch#027] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-25-DaHall 1-PDU-04-30-2 | 5-DaHall 1-PDU-03-30-2 | 5-DaHall 1-PDU-04-30-2 | 5-DaHall 1-PDU-03 | [branch#002] [A] W | 5-DaHall 1-PDU-04 | [branch#002] [A] W | 0 | 6-DaHall 1-PDU-11-30-496-DaHall 1-PDU-12-30-49 | 6-DaHall 1-PDU-11-30-49 | 6-DaHall 1-PDU-12-30-49 | 6-DaHall 1-PDU-11 | [branch#049] [A] W | 6-DaHall 1-PDU-12 | [branch#049] [A] W | 0 | 7-DaHall 1-A-2-35-497-DaHall 1-B-2-35-49 | 7-DaHall 1-A-2-35-49 | 7-DaHall 1-B-2-35-49 | 7-DaHall 1-A-2-35 | [branch#049] [A] W | 7-DaHall 1-B-2-35 | [branch#049] [A] W | #N/A
4-DaHall 1-PDU-06-100-84-DaHall 1-PDU-05-100-8 | 4-DaHall 1-PDU-06-100-8 | 4-DaHall 1-PDU-05-100-8 | 4-DaHall 1-PDU-06 | [branch#008] [A] W | 4-DaHall 1-PDU-05 | [branch#008] [A] W | 5.855 | 5-DaHall 1-PDU-03-30-45-DaHall 1-PDU-04-30-4 | 5-DaHall 1-PDU-03-30-4 | 5-DaHall 1-PDU-04-30-4 | 5-DaHall 1-PDU-03 | [branch#004] [A] W | 5-DaHall 1-PDU-04 | [branch#004] [A] W | 0 | 6-DaHall 1-PDU-11-30-296-DaHall 1-PDU-12-30-29 | 6-DaHall 1-PDU-11-30-29 | 6-DaHall 1-PDU-12-30-29 | 6-DaHall 1-PDU-11 | [branch#029] [A] W | 6-DaHall 1-PDU-12 | [branch#029] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-415-DaHall 1-PDU-04-30-41 | 5-DaHall 1-PDU-03-30-41 | 5-DaHall 1-PDU-04-30-41 | 5-DaHall 1-PDU-03 | [branch#041] [A] W | 5-DaHall 1-PDU-04 | [branch#041] [A] W | #N/A | 6-DaHall 1-PDU-11-30-316-DaHall 1-PDU-12-30-31 | 6-DaHall 1-PDU-11-30-31 | 6-DaHall 1-PDU-12-30-31 | 6-DaHall 1-PDU-11 | [branch#031] [A] W | 6-DaHall 1-PDU-12 | [branch#031] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-65-DaHall 1-PDU-04-30-6 | 5-DaHall 1-PDU-03-30-6 | 5-DaHall 1-PDU-04-30-6 | 5-DaHall 1-PDU-03 | [branch#006] [A] W | 5-DaHall 1-PDU-04 | [branch#006] [A] W | 0 | 6-DaHall 1-PDU-11-30-476-DaHall 1-PDU-12-30-47 | 6-DaHall 1-PDU-11-30-47 | 6-DaHall 1-PDU-12-30-47 | 6-DaHall 1-PDU-11 | [branch#047] [A] W | 6-DaHall 1-PDU-12 | [branch#047] [A] W | 0 | 7-DaHall 1-A-2-35-107-DaHall 1-B-2-35-10 | 7-DaHall 1-A-2-35-10 | 7-DaHall 1-B-2-35-10 | 7-DaHall 1-A-2-35 | [branch#010] [A] W | 7-DaHall 1-B-2-35 | [branch#010] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-85-DaHall 1-PDU-04-30-8 | 5-DaHall 1-PDU-03-30-8 | 5-DaHall 1-PDU-04-30-8 | 5-DaHall 1-PDU-03 | [branch#008] [A] W | 5-DaHall 1-PDU-04 | [branch#008] [A] W | 0 | 6-DaHall 1-PDU-11-30-336-DaHall 1-PDU-12-30-33 | 6-DaHall 1-PDU-11-30-33 | 6-DaHall 1-PDU-12-30-33 | 6-DaHall 1-PDU-11 | [branch#033] [A] W | 6-DaHall 1-PDU-12 | [branch#033] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-435-DaHall 1-PDU-04-30-43 | 5-DaHall 1-PDU-03-30-43 | 5-DaHall 1-PDU-04-30-43 | 5-DaHall 1-PDU-03 | [branch#043] [A] W | 5-DaHall 1-PDU-04 | [branch#043] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-A-3-100-607-DaHall 1-B-3-100-60 | 7-DaHall 1-A-3-100-60 | 7-DaHall 1-B-3-100-60 | 7-DaHall 1-A-3-10 | [branch#060] [A] W | 7-DaHall 1-B-3-10 | [branch#060] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-105-DaHall 1-PDU-04-30-10 | 5-DaHall 1-PDU-03-30-10 | 5-DaHall 1-PDU-04-30-10 | 5-DaHall 1-PDU-03 | [branch#010] [A] W | 5-DaHall 1-PDU-04 | [branch#010] [A] W | 0 | [7 empty] | 0 | 7-DaHall 1-A-3-100-287-DaHall 1-B-3-100-28 | 7-DaHall 1-A-3-100-28 | 7-DaHall 1-B-3-100-28 | 7-DaHall 1-A-3-10 | [branch#028] [A] W | 7-DaHall 1-B-3-10 | [branch#028] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-125-DaHall 1-PDU-04-30-12 | 5-DaHall 1-PDU-03-30-12 | 5-DaHall 1-PDU-04-30-12 | 5-DaHall 1-PDU-03 | [branch#012] [A] W | 5-DaHall 1-PDU-04 | [branch#012] [A] W | 0 | [7 empty] | 0 | 7-DaHall 1-A-3-50-157-DaHall 1-B-3-50-15 | 7-DaHall 1-A-3-50-15 | 7-DaHall 1-B-3-50-15 | 7-DaHall 1-A-3-50 | [branch#015] [A] W | 7-DaHall 1-B-3-50 | [branch#015] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-455-DaHall 1-PDU-04-30-45 | 5-DaHall 1-PDU-03-30-45 | 5-DaHall 1-PDU-04-30-45 | 5-DaHall 1-PDU-03 | [branch#045] [A] W | 5-DaHall 1-PDU-04 | [branch#045] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-A-3-50-167-DaHall 1-B-3-50-16 | 7-DaHall 1-A-3-50-16 | 7-DaHall 1-B-3-50-16 | 7-DaHall 1-A-3-50 | [branch#016] [A] W | 7-DaHall 1-B-3-50 | [branch#016] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-145-DaHall 1-PDU-04-30-14 | 5-DaHall 1-PDU-03-30-14 | 5-DaHall 1-PDU-04-30-14 | 5-DaHall 1-PDU-03 | [branch#014] [A] W | 5-DaHall 1-PDU-04 | [branch#014] [A] W | 0 | 6-DaHall 1-PDU-01-30-256-DaHall 1-PDU-02-30-25 | 6-DaHall 1-PDU-01-30-25 | 6-DaHall 1-PDU-02-30-25 | 6-DaHall 1-PDU-01 | [branch#025] [A] W | 6-DaHall 1-PDU-02 | [branch#025] [A] W | 0 | 7-DaHall 1-A-3-50-177-DaHall 1-B-3-50-17 | 7-DaHall 1-A-3-50-17 | 7-DaHall 1-B-3-50-17 | 7-DaHall 1-A-3-50 | [branch#017] [A] W | 7-DaHall 1-B-3-50 | [branch#017] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-375-DaHall 1-PDU-04-30-37 | 5-DaHall 1-PDU-03-30-37 | 5-DaHall 1-PDU-04-30-37 | 5-DaHall 1-PDU-03 | [branch#037] [A] W | 5-DaHall 1-PDU-04 | [branch#037] [A] W | #N/A | 6-DaHall 1-PDU-01-30-276-DaHall 1-PDU-02-30-27 | 6-DaHall 1-PDU-01-30-27 | 6-DaHall 1-PDU-02-30-27 | 6-DaHall 1-PDU-01 | [branch#027] [A] W | 6-DaHall 1-PDU-02 | [branch#027] [A] W | 0.684 | 7-DaHall 1-A-3-35-237-DaHall 1-B-3-35-24 | 7-DaHall 1-A-3-35-23 | 7-DaHall 1-B-3-35-24 | 7-DaHall 1-A-3-35 | [branch#023] [A] W | 7-DaHall 1-B-3-35 | [branch#024] [A] W | #N/A
4-DaHall 1-PDU-06-100-74-DaHall 1-PDU-05-100-7 | 4-DaHall 1-PDU-06-100-7 | 4-DaHall 1-PDU-05-100-7 | 4-DaHall 1-PDU-06 | [branch#007] [A] W | 4-DaHall 1-PDU-05 | [branch#007] [A] W | 3.447 | 5-DaHall 1-PDU-03-30-165-DaHall 1-PDU-04-30-16 | 5-DaHall 1-PDU-03-30-16 | 5-DaHall 1-PDU-04-30-16 | 5-DaHall 1-PDU-03 | [branch#016] [A] W | 5-DaHall 1-PDU-04 | [branch#016] [A] W | 0 | 6-DaHall 1-PDU-01-30-296-DaHall 1-PDU-02-30-29 | 6-DaHall 1-PDU-01-30-29 | 6-DaHall 1-PDU-02-30-29 | 6-DaHall 1-PDU-01 | [branch#029] [A] W | 6-DaHall 1-PDU-02 | [branch#029] [A] W | 0 | 7-DaHall 1-A-3-100-597-DaHall 1-B-3-100-59 | 7-DaHall 1-A-3-100-59 | 7-DaHall 1-B-3-100-59 | 7-DaHall 1-A-3-10 | [branch#059] [A] W | 7-DaHall 1-B-3-10 | [branch#059] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-395-DaHall 1-PDU-04-30-39 | 5-DaHall 1-PDU-03-30-39 | 5-DaHall 1-PDU-04-30-39 | 5-DaHall 1-PDU-03 | [branch#039] [A] W | 5-DaHall 1-PDU-04 | [branch#039] [A] W | #N/A | 6-DaHall 1-PDU-01-30-316-DaHall 1-PDU-02-30-31 | 6-DaHall 1-PDU-01-30-31 | 6-DaHall 1-PDU-02-30-31 | 6-DaHall 1-PDU-01 | [branch#031] [A] W | 6-DaHall 1-PDU-02 | [branch#031] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-185-DaHall 1-PDU-04-30-18 | 5-DaHall 1-PDU-03-30-18 | 5-DaHall 1-PDU-04-30-18 | 5-DaHall 1-PDU-03 | [branch#018] [A] W | 5-DaHall 1-PDU-04 | [branch#018] [A] W | 0 | 6-DaHall 1-PDU-01-30-336-DaHall 1-PDU-02-30-33 | 6-DaHall 1-PDU-01-30-33 | 6-DaHall 1-PDU-02-30-33 | 6-DaHall 1-PDU-01 | [branch#033] [A] W | 6-DaHall 1-PDU-02 | [branch#033] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-205-DaHall 1-PDU-04-30-20 | 5-DaHall 1-PDU-03-30-20 | 5-DaHall 1-PDU-04-30-20 | 5-DaHall 1-PDU-03 | [branch#020] [A] W | 5-DaHall 1-PDU-04 | [branch#020] [A] W | 1.95 | 6-DaHall 1-PDU-01-30-356-DaHall 1-PDU-02-30-35 | 6-DaHall 1-PDU-01-30-35 | 6-DaHall 1-PDU-02-30-35 | 6-DaHall 1-PDU-01 | [branch#035] [A] W | 6-DaHall 1-PDU-02 | [branch#035] [A] W | 0 | 7-DaHall 1-PDU-01-30-29 | 7-DaHall 1-PDU-01-30-29 |  | 7-DaHall 1-PDU-01 | [branch#029] [A] W |  |  | 0.079
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-225-DaHall 1-PDU-04-30-22 | 5-DaHall 1-PDU-03-30-22 | 5-DaHall 1-PDU-04-30-22 | 5-DaHall 1-PDU-03 | [branch#022] [A] W | 5-DaHall 1-PDU-04 | [branch#022] [A] W | 0 | 6-DaHall 1-PDU-01-30-376-DaHall 1-PDU-02-30-37 | 6-DaHall 1-PDU-01-30-37 | 6-DaHall 1-PDU-02-30-37 | 6-DaHall 1-PDU-01 | [branch#037] [A] W | 6-DaHall 1-PDU-02 | [branch#037] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-245-DaHall 1-PDU-04-30-24 | 5-DaHall 1-PDU-03-30-24 | 5-DaHall 1-PDU-04-30-24 | 5-DaHall 1-PDU-03 | [branch#024] [A] W | 5-DaHall 1-PDU-04 | [branch#024] [A] W | 0 | 6-DaHall 1-PDU-01-30-396-DaHall 1-PDU-02-30-39 | 6-DaHall 1-PDU-01-30-39 | 6-DaHall 1-PDU-02-30-39 | 6-DaHall 1-PDU-01 | [branch#039] [A] W | 6-DaHall 1-PDU-02 | [branch#039] [A] W | 0 | 7-DaHall 1-PDU-01-30-187-DaHall 1-PDU-02-30-18 | 7-DaHall 1-PDU-01-30-18 | 7-DaHall 1-PDU-02-30-18 | 7-DaHall 1-PDU-01 | [branch#018] [A] W | 7-DaHall 1-PDU-02 | [branch#018] [A] W | 0.899
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-265-DaHall 1-PDU-04-30-26 | 5-DaHall 1-PDU-03-30-26 | 5-DaHall 1-PDU-04-30-26 | 5-DaHall 1-PDU-03 | [branch#026] [A] W | 5-DaHall 1-PDU-04 | [branch#026] [A] W | 2.737 | 6-DaHall 1-PDU-01-30-416-DaHall 1-PDU-02-30-41 | 6-DaHall 1-PDU-01-30-41 | 6-DaHall 1-PDU-02-30-41 | 6-DaHall 1-PDU-01 | [branch#041] [A] W | 6-DaHall 1-PDU-02 | [branch#041] [A] W | 0.366 | 7-DaHall 1-PDU-01-30-207-DaHall 1-PDU-02-30-20 | 7-DaHall 1-PDU-01-30-20 | 7-DaHall 1-PDU-02-30-20 | 7-DaHall 1-PDU-01 | [branch#020] [A] W | 7-DaHall 1-PDU-02 | [branch#020] [A] W | 1.065
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-285-DaHall 1-PDU-04-30-28 | 5-DaHall 1-PDU-03-30-28 | 5-DaHall 1-PDU-04-30-28 | 5-DaHall 1-PDU-03 | [branch#028] [A] W | 5-DaHall 1-PDU-04 | [branch#028] [A] W | #N/A | 6-DaHall 1-PDU-01-30-496-DaHall 1-PDU-02-30-30 | 6-DaHall 1-PDU-01-30-49 | 6-DaHall 1-PDU-02-30-30 | 6-DaHall 1-PDU-01 | [branch#049] [A] W | 6-DaHall 1-PDU-02 | [branch#030] [A] W | 4.392 | 7-DaHall 1-PDU-01-30-227-DaHall 1-PDU-02-30-22 | 7-DaHall 1-PDU-01-30-22 | 7-DaHall 1-PDU-02-30-22 | 7-DaHall 1-PDU-01 | [branch#022] [A] W | 7-DaHall 1-PDU-02 | [branch#022] [A] W | 0.799
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-305-DaHall 1-PDU-04-30-30 | 5-DaHall 1-PDU-03-30-30 | 5-DaHall 1-PDU-04-30-30 | 5-DaHall 1-PDU-03 | [branch#030] [A] W | 5-DaHall 1-PDU-04 | [branch#030] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-PDU-01-30-247-DaHall 1-PDU-02-30-24 | 7-DaHall 1-PDU-01-30-24 | 7-DaHall 1-PDU-02-30-24 | 7-DaHall 1-PDU-01 | [branch#024] [A] W | 7-DaHall 1-PDU-02 | [branch#024] [A] W | 1.223
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-465-DaHall 1-PDU-02-30-46 | 5-DaHall 1-PDU-01-30-46 | 5-DaHall 1-PDU-02-30-46 | 5-DaHall 1-PDU-01 | [branch#046] [A] W | 5-DaHall 1-PDU-02 | [branch#046] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-PDU-01-30-267-DaHall 1-PDU-02-30-26 | 7-DaHall 1-PDU-01-30-26 | 7-DaHall 1-PDU-02-30-26 | 7-DaHall 1-PDU-01 | [branch#026] [A] W | 7-DaHall 1-PDU-02 | [branch#026] [A] W | 1.476
4-DaHall 1-PDU-06-100-64-DaHall 1-PDU-05-100-6 | 4-DaHall 1-PDU-06-100-6 | 4-DaHall 1-PDU-05-100-6 | 4-DaHall 1-PDU-06 | [branch#006] [A] W | 4-DaHall 1-PDU-05 | [branch#006] [A] W | 2.57 | [7 empty] | 0 | 6-DaHall 1-PDU-01-30-456-DaHall 1-PDU-02-30-45 | 6-DaHall 1-PDU-01-30-45 | 6-DaHall 1-PDU-02-30-45 | 6-DaHall 1-PDU-01 | [branch#045] [A] W | 6-DaHall 1-PDU-02 | [branch#045] [A] W | 0 | 7-DaHall 1-PDU-01-30-287-DaHall 1-PDU-02-30-28 | 7-DaHall 1-PDU-01-30-28 | 7-DaHall 1-PDU-02-30-28 | 7-DaHall 1-PDU-01 | [branch#028] [A] W | 7-DaHall 1-PDU-02 | [branch#028] [A] W | 2.356
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-55-DaHall 1-PDU-04-30-5 | 5-DaHall 1-PDU-03-30-5 | 5-DaHall 1-PDU-04-30-5 | 5-DaHall 1-PDU-03 | [branch#005] [A] W | 5-DaHall 1-PDU-04 | [branch#005] [A] W | 0 | 6-DaHall 1-PDU-01-30-476-DaHall 1-PDU-02-30-47 | 6-DaHall 1-PDU-01-30-47 | 6-DaHall 1-PDU-02-30-47 | 6-DaHall 1-PDU-01 | [branch#047] [A] W | 6-DaHall 1-PDU-02 | [branch#047] [A] W | 0 | 7-DaHall 1-PDU-01- 30AT-407-DaHall 1-PDU-02- 30AT-40 | 7-DaHall 1-PDU-01- 30AT-40 | 7-DaHall 1-PDU-02- 30AT-40 | 7-DaHall 1-PDU-01 | [branch#040] [A] W | 7-DaHall 1-PDU-02 | [branch#040] [A] W | 1.404
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-75-DaHall 1-PDU-04-30-7 | 5-DaHall 1-PDU-03-30-7 | 5-DaHall 1-PDU-04-30-7 | 5-DaHall 1-PDU-03 | [branch#007] [A] W | 5-DaHall 1-PDU-04 | [branch#007] [A] W | 0 | 6-DaHall 1-PDU-05-30-486-DaHall 1-PDU-06-30-48 | 6-DaHall 1-PDU-05-30-48 | 6-DaHall 1-PDU-06-30-48 | 6-DaHall 1-PDU-05 | [branch#048] [A] W | 6-DaHall 1-PDU-06 | [branch#048] [A] W | 0 | 7-DaHall 1-PDU-01- 30AT-387-DaHall 1-PDU-02- 30AT-38 | 7-DaHall 1-PDU-01- 30AT-38 | 7-DaHall 1-PDU-02- 30AT-38 | 7-DaHall 1-PDU-01 | [branch#038] [A] W | 7-DaHall 1-PDU-02 | [branch#038] [A] W | 1.382
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-95-DaHall 1-PDU-04-30-9 | 5-DaHall 1-PDU-03-30-9 | 5-DaHall 1-PDU-04-30-9 | 5-DaHall 1-PDU-03 | [branch#009] [A] W | 5-DaHall 1-PDU-04 | [branch#009] [A] W | 0 | 6-DaHall 1-PDU-01-30-186-DaHall 1-PDU-02-30-34 | 6-DaHall 1-PDU-01-30-18 | 6-DaHall 1-PDU-02-30-34 | 6-DaHall 1-PDU-01 | [branch#018] [A] W | 6-DaHall 1-PDU-02 | [branch#034] [A] W | 0 | 7-DaHall 1-PDU-01- 30AT-367-DaHall 1-PDU-02- 30AT-36 | 7-DaHall 1-PDU-01- 30AT-36 | 7-DaHall 1-PDU-02- 30AT-36 | 7-DaHall 1-PDU-01 | [branch#036] [A] W | 7-DaHall 1-PDU-02 | [branch#036] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-115-DaHall 1-PDU-04-30-11 | 5-DaHall 1-PDU-03-30-11 | 5-DaHall 1-PDU-04-30-11 | 5-DaHall 1-PDU-03 | [branch#011] [A] W | 5-DaHall 1-PDU-04 | [branch#011] [A] W | 0 | 6-DaHall 1-PDU-01-30-206-DaHall 1-PDU-02-30-20 | 6-DaHall 1-PDU-01-30-20 | 6-DaHall 1-PDU-02-30-20 | 6-DaHall 1-PDU-01 | [branch#020] [A] W | 6-DaHall 1-PDU-02 | [branch#020] [A] W | 0 | 7-DaHall 1-A-3-35-227-DaHall 1-B-3-35-22 | 7-DaHall 1-A-3-35-22 | 7-DaHall 1-B-3-35-22 | 7-DaHall 1-A-3-35 | [branch#022] [A] W | 7-DaHall 1-B-3-35 | [branch#022] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-135-DaHall 1-PDU-04-30-13 | 5-DaHall 1-PDU-03-30-13 | 5-DaHall 1-PDU-04-30-13 | 5-DaHall 1-PDU-03 | [branch#013] [A] W | 5-DaHall 1-PDU-04 | [branch#013] [A] W | 0 | 6-DaHall 1-PDU-01-30-226-DaHall 1-PDU-02-30-22 | 6-DaHall 1-PDU-01-30-22 | 6-DaHall 1-PDU-02-30-22 | 6-DaHall 1-PDU-01 | [branch#022] [A] W | 6-DaHall 1-PDU-02 | [branch#022] [A] W | 0 | 7-DaHall 1-A-3-35-517-DaHall 1-B-3-35-51 | 7-DaHall 1-A-3-35-51 | 7-DaHall 1-B-3-35-51 | 7-DaHall 1-A-3-35 | [branch#051] [A] W | 7-DaHall 1-B-3-35 | [branch#051] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-155-DaHall 1-PDU-04-30-15 | 5-DaHall 1-PDU-03-30-15 | 5-DaHall 1-PDU-04-30-15 | 5-DaHall 1-PDU-03 | [branch#015] [A] W | 5-DaHall 1-PDU-04 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-01-30-246-DaHall 1-PDU-02-30-24 | 6-DaHall 1-PDU-01-30-24 | 6-DaHall 1-PDU-02-30-24 | 6-DaHall 1-PDU-01 | [branch#024] [A] W | 6-DaHall 1-PDU-02 | [branch#024] [A] W | 0 | 7-DaHall 1-A-3-35-507-DaHall 1-B-3-35-50 | 7-DaHall 1-A-3-35-50 | 7-DaHall 1-B-3-35-50 | 7-DaHall 1-A-3-35 | [branch#050] [A] W | 7-DaHall 1-B-3-35 | [branch#050] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-175-DaHall 1-PDU-04-30-17 | 5-DaHall 1-PDU-03-30-17 | 5-DaHall 1-PDU-04-30-17 | 5-DaHall 1-PDU-03 | [branch#017] [A] W | 5-DaHall 1-PDU-04 | [branch#017] [A] W | 0 | 6-DaHall 1-PDU-01-30-266-DaHall 1-PDU-02-30-26 | 6-DaHall 1-PDU-01-30-26 | 6-DaHall 1-PDU-02-30-26 | 6-DaHall 1-PDU-01 | [branch#026] [A] W | 6-DaHall 1-PDU-02 | [branch#026] [A] W | 0 | 7-DaHall 1-A-3-50-497-DaHall 1-B-3-35-49 | 7-DaHall 1-A-3-50-49 | 7-DaHall 1-B-3-35-49 | 7-DaHall 1-A-3-50 | [branch#049] [A] W | 7-DaHall 1-B-3-35 | [branch#049] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-01-30-286-DaHall 1-PDU-02-30-28 | 6-DaHall 1-PDU-01-30-28 | 6-DaHall 1-PDU-02-30-28 | 6-DaHall 1-PDU-01 | [branch#028] [A] W | 6-DaHall 1-PDU-02 | [branch#028] [A] W | 0 | 7-DaHall 1-A-3-50-217-DaHall 1-B-3-50-21 | 7-DaHall 1-A-3-50-21 | 7-DaHall 1-B-3-50-21 | 7-DaHall 1-A-3-50 | [branch#021] [A] W | 7-DaHall 1-B-3-50 | [branch#021] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | [7 empty] | 0 | 7-DaHall 1-A-3-35-207-DaHall 1-B-3-50-20 | 7-DaHall 1-A-3-35-20 | 7-DaHall 1-B-3-50-20 | 7-DaHall 1-A-3-35 | [branch#020] [A] W | 7-DaHall 1-B-3-50 | [branch#020] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-05-30-376-DaHall 1-PDU-06-30-37 | 6-DaHall 1-PDU-05-30-37 | 6-DaHall 1-PDU-06-30-37 | 6-DaHall 1-PDU-05 | [branch#037] [A] W | 6-DaHall 1-PDU-06 | [branch#037] [A] W | 4.003 | 7-DaHall 1-A-3-35-527-DaHall 1-B-3-35-23 | 7-DaHall 1-A-3-35-52 | 7-DaHall 1-B-3-35-23 | 7-DaHall 1-A-3-35 | [branch#052] [A] W | 7-DaHall 1-B-3-35 | [branch#023] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-355-DaHall 1-PDU-04-30-35 | 5-DaHall 1-PDU-03-30-35 | 5-DaHall 1-PDU-04-30-35 | 5-DaHall 1-PDU-03 | [branch#035] [A] W | 5-DaHall 1-PDU-04 | [branch#035] [A] W | #N/A | 6-DaHall 1-PDU-05-30-396-DaHall 1-PDU-06-30-39 | 6-DaHall 1-PDU-05-30-39 | 6-DaHall 1-PDU-06-30-39 | 6-DaHall 1-PDU-05 | [branch#039] [A] W | 6-DaHall 1-PDU-06 | [branch#039] [A] W | 0.907 | 7-DaHall 1-A-3-35-557-DaHall 1-B-3-35-54 | 7-DaHall 1-A-3-35-55 | 7-DaHall 1-B-3-35-54 | 7-DaHall 1-A-3-35 | [branch#055] [A] W | 7-DaHall 1-B-3-35 | [branch#054] [A] W | #N/A
4-DaHall 1-PDU-06-100-54-DaHall 1-PDU-05-100-5 | 4-DaHall 1-PDU-06-100-5 | 4-DaHall 1-PDU-05-100-5 | 4-DaHall 1-PDU-06 | [branch#005] [A] W | 4-DaHall 1-PDU-05 | [branch#005] [A] W | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-05-30-416-DaHall 1-PDU-06-30-41 | 6-DaHall 1-PDU-05-30-41 | 6-DaHall 1-PDU-06-30-41 | 6-DaHall 1-PDU-05 | [branch#041] [A] W | 6-DaHall 1-PDU-06 | [branch#041] [A] W | 0.698 | 7-DaHall 1-A-3-35-197-DaHall 1-B-3-50-19 | 7-DaHall 1-A-3-35-19 | 7-DaHall 1-B-3-50-19 | 7-DaHall 1-A-3-35 | [branch#019] [A] W | 7-DaHall 1-B-3-50 | [branch#019] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-05-30-436-DaHall 1-PDU-06-30-43 | 6-DaHall 1-PDU-05-30-43 | 6-DaHall 1-PDU-06-30-43 | 6-DaHall 1-PDU-05 | [branch#043] [A] W | 6-DaHall 1-PDU-06 | [branch#043] [A] W | 2.457 | 7-DaHall 1-A-3-35-187-DaHall 1-B-3-35-18 | 7-DaHall 1-A-3-35-18 | 7-DaHall 1-B-3-35-18 | 7-DaHall 1-A-3-35 | [branch#018] [A] W | 7-DaHall 1-B-3-35 | [branch#018] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-05-30-456-DaHall 1-PDU-06-30-45 | 6-DaHall 1-PDU-05-30-45 | 6-DaHall 1-PDU-06-30-45 | 6-DaHall 1-PDU-05 | [branch#045] [A] W | 6-DaHall 1-PDU-06 | [branch#045] [A] W | 2.145 | 7-DaHall 1-A-2-50-227-DaHall 1-B-2-50-22 | 7-DaHall 1-A-2-50-22 | 7-DaHall 1-B-2-50-22 | 7-DaHall 1-A-2-50 | [branch#022] [A] W | 7-DaHall 1-B-2-50 | [branch#022] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-05-30-476-DaHall 1-PDU-06-30-47 | 6-DaHall 1-PDU-05-30-47 | 6-DaHall 1-PDU-06-30-47 | 6-DaHall 1-PDU-05 | [branch#047] [A] W | 6-DaHall 1-PDU-06 | [branch#047] [A] W | 2.245 | 7-DaHall 1-PDU-01-30-147-DaHall 1-PDU-02-30-14 | 7-DaHall 1-PDU-01-30-14 | 7-DaHall 1-PDU-02-30-14 | 7-DaHall 1-PDU-01 | [branch#014] [A] W | 7-DaHall 1-PDU-02 | [branch#014] [A] W | 1.483
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-05-30-516-DaHall 1-PDU-06-30-51 | 6-DaHall 1-PDU-05-30-51 | 6-DaHall 1-PDU-06-30-51 | 6-DaHall 1-PDU-05 | [branch#051] [A] W | 6-DaHall 1-PDU-06 | [branch#051] [A] W | 2.333 | 7-DaHall 1-PDU-01-30-167-DaHall 1-PDU-02-30-16 | 7-DaHall 1-PDU-01-30-16 | 7-DaHall 1-PDU-02-30-16 | 7-DaHall 1-PDU-01 | [branch#016] [A] W | 7-DaHall 1-PDU-02 | [branch#016] [A] W | 1.079
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-05-30-536-DaHall 1-PDU-06-30-53 | 6-DaHall 1-PDU-05-30-53 | 6-DaHall 1-PDU-06-30-53 | 6-DaHall 1-PDU-05 | [branch#053] [A] W | 6-DaHall 1-PDU-06 | [branch#053] [A] W | 1.662 | [7 empty] | 0
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-05-30-496-DaHall 1-PDU-06-30-49 | 6-DaHall 1-PDU-05-30-49 | 6-DaHall 1-PDU-06-30-49 | 6-DaHall 1-PDU-05 | [branch#049] [A] W | 6-DaHall 1-PDU-06 | [branch#049] [A] W | 2.167 | [7 empty] | 0
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-03-30-16-DaHall 1-PDU-04-30-1 | 6-DaHall 1-PDU-03-30-1 | 6-DaHall 1-PDU-04-30-1 | 6-DaHall 1-PDU-03 | [branch#001] [A] W | 6-DaHall 1-PDU-04 | [branch#001] [A] W | 3.147 | [7 empty] | 0
4-DaHall 1-PDU-06-100-44-DaHall 1-PDU-05-100-4 | 4-DaHall 1-PDU-06-100-4 | 4-DaHall 1-PDU-05-100-4 | 4-DaHall 1-PDU-06 | [branch#004] [A] W | 4-DaHall 1-PDU-05 | [branch#004] [A] W | 3.038 | [7 empty] | 0 | 6-DaHall 1-PDU-03-30-36-DaHall 1-PDU-04-30-3 | 6-DaHall 1-PDU-03-30-3 | 6-DaHall 1-PDU-04-30-3 | 6-DaHall 1-PDU-03 | [branch#003] [A] W | 6-DaHall 1-PDU-04 | [branch#003] [A] W | 3.154 | [7 empty] | 0
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-03-30-56-DaHall 1-PDU-04-30-5 | 6-DaHall 1-PDU-03-30-5 | 6-DaHall 1-PDU-04-30-5 | 6-DaHall 1-PDU-03 | [branch#005] [A] W | 6-DaHall 1-PDU-04 | [branch#005] [A] W | 0.518 | 7-DaHall 1-A-2-50-127-DaHall 1-B-2-50-12 | 7-DaHall 1-A-2-50-12 | 7-DaHall 1-B-2-50-12 | 7-DaHall 1-A-2-50 | [branch#012] [A] W | 7-DaHall 1-B-2-50 | [branch#012] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-03-30-76-DaHall 1-PDU-04-30-7 | 6-DaHall 1-PDU-03-30-7 | 6-DaHall 1-PDU-04-30-7 | 6-DaHall 1-PDU-03 | [branch#007] [A] W | 6-DaHall 1-PDU-04 | [branch#007] [A] W | 1.828 | 7-DaHall 1-A-2-50-667-DaHall 1-B-2-50-66 | 7-DaHall 1-A-2-50-66 | 7-DaHall 1-B-2-50-66 | 7-DaHall 1-A-2-50 | [branch#066] [A] W | 7-DaHall 1-B-2-50 | [branch#066] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-03-30-96-DaHall 1-PDU-04-30-9 | 6-DaHall 1-PDU-03-30-9 | 6-DaHall 1-PDU-04-30-9 | 6-DaHall 1-PDU-03 | [branch#009] [A] W | 6-DaHall 1-PDU-04 | [branch#009] [A] W | 1.649 | 7-DaHall 1-A-2-50-677-DaHall 1-B-2-50-67 | 7-DaHall 1-A-2-50-67 | 7-DaHall 1-B-2-50-67 | 7-DaHall 1-A-2-50 | [branch#067] [A] W | 7-DaHall 1-B-2-50 | [branch#067] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-03-30-116-DaHall 1-PDU-04-30-11 | 6-DaHall 1-PDU-03-30-11 | 6-DaHall 1-PDU-04-30-11 | 6-DaHall 1-PDU-03 | [branch#011] [A] W | 6-DaHall 1-PDU-04 | [branch#011] [A] W | 2.038 | 7-DaHall 1-A-2-35-657-DaHall 1-B-2-35-65 | 7-DaHall 1-A-2-35-65 | 7-DaHall 1-B-2-35-65 | 7-DaHall 1-A-2-35 | [branch#065] [A] W | 7-DaHall 1-B-2-35 | [branch#065] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-03-30-136-DaHall 1-PDU-04-30-13 | 6-DaHall 1-PDU-03-30-13 | 6-DaHall 1-PDU-04-30-13 | 6-DaHall 1-PDU-03 | [branch#013] [A] W | 6-DaHall 1-PDU-04 | [branch#013] [A] W | 2.686 | 7-DaHall 1-A-2-50-647-DaHall 1-B-2-50-64 | 7-DaHall 1-A-2-50-64 | 7-DaHall 1-B-2-50-64 | 7-DaHall 1-A-2-50 | [branch#064] [A] W | 7-DaHall 1-B-2-50 | [branch#064] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-03-30-156-DaHall 1-PDU-04-30-15 | 6-DaHall 1-PDU-03-30-15 | 6-DaHall 1-PDU-04-30-15 | 6-DaHall 1-PDU-03 | [branch#015] [A] W | 6-DaHall 1-PDU-04 | [branch#015] [A] W | 1.684 | 7-DaHall 1-A-2-35-607-DaHall 1-B-2-35-60 | 7-DaHall 1-A-2-35-60 | 7-DaHall 1-B-2-35-60 | 7-DaHall 1-A-2-35 | [branch#060] [A] W | 7-DaHall 1-B-2-35 | [branch#060] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-03-30-176-DaHall 1-PDU-04-30-17 | 6-DaHall 1-PDU-03-30-17 | 6-DaHall 1-PDU-04-30-17 | 6-DaHall 1-PDU-03 | [branch#017] [A] W | 6-DaHall 1-PDU-04 | [branch#017] [A] W | 0.806 | 7-DaHall 1-A-2-35-617-DaHall 1-B-2-35-61 | 7-DaHall 1-A-2-35-61 | 7-DaHall 1-B-2-35-61 | 7-DaHall 1-A-2-35 | [branch#061] [A] W | 7-DaHall 1-B-2-35 | [branch#061] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | [7 empty] | 0 | 7-DaHall 1-A-2-35-597-DaHall 1-B-2-35-59 | 7-DaHall 1-A-2-35-59 | 7-DaHall 1-B-2-35-59 | 7-DaHall 1-A-2-35 | [branch#059] [A] W | 7-DaHall 1-B-2-35 | [branch#059] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-05-30-206-DaHall 1-PDU-06-30-20 | 6-DaHall 1-PDU-05-30-20 | 6-DaHall 1-PDU-06-30-20 | 6-DaHall 1-PDU-05 | [branch#020] [A] W | 6-DaHall 1-PDU-06 | [branch#020] [A] W | 0 | 7-DaHall 1-A-2-35-567-DaHall 1-B-2-35-56 | 7-DaHall 1-A-2-35-56 | 7-DaHall 1-B-2-35-56 | 7-DaHall 1-A-2-35 | [branch#056] [A] W | 7-DaHall 1-B-2-35 | [branch#056] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-05-30-226-DaHall 1-PDU-06-30-22 | 6-DaHall 1-PDU-05-30-22 | 6-DaHall 1-PDU-06-30-22 | 6-DaHall 1-PDU-05 | [branch#022] [A] W | 6-DaHall 1-PDU-06 | [branch#022] [A] W | 0 | 7-DaHall 1-A-2-35-557-DaHall 1-B-2-35-55 | 7-DaHall 1-A-2-35-55 | 7-DaHall 1-B-2-35-55 | 7-DaHall 1-A-2-35 | [branch#055] [A] W | 7-DaHall 1-B-2-35 | [branch#055] [A] W | #N/A
4-DaHall 1-PDU-06-100-34-DaHall 1-PDU-05-100-3 | 4-DaHall 1-PDU-06-100-3 | 4-DaHall 1-PDU-05-100-3 | 4-DaHall 1-PDU-06 | [branch#003] [A] W | 4-DaHall 1-PDU-05 | [branch#003] [A] W | 3.484 | 5-DaHall 1-PDU-05-30-15-DaHall 1-PDU-06-30-1 | 5-DaHall 1-PDU-05-30-1 | 5-DaHall 1-PDU-06-30-1 | 5-DaHall 1-PDU-05 | [branch#001] [A] W | 5-DaHall 1-PDU-06 | [branch#001] [A] W | 0 | 6-DaHall 1-PDU-05-30-246-DaHall 1-PDU-06-30-24 | 6-DaHall 1-PDU-05-30-24 | 6-DaHall 1-PDU-06-30-24 | 6-DaHall 1-PDU-05 | [branch#024] [A] W | 6-DaHall 1-PDU-06 | [branch#024] [A] W | 0 | 7-DaHall 1-A-2-35-547-DaHall 1-B-2-35-54 | 7-DaHall 1-A-2-35-54 | 7-DaHall 1-B-2-35-54 | 7-DaHall 1-A-2-35 | [branch#054] [A] W | 7-DaHall 1-B-2-35 | [branch#054] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-35-DaHall 1-PDU-06-30-3 | 5-DaHall 1-PDU-05-30-3 | 5-DaHall 1-PDU-06-30-3 | 5-DaHall 1-PDU-05 | [branch#003] [A] W | 5-DaHall 1-PDU-06 | [branch#003] [A] W | 0 | 6-DaHall 1-PDU-05-30-266-DaHall 1-PDU-06-30-26 | 6-DaHall 1-PDU-05-30-26 | 6-DaHall 1-PDU-06-30-26 | 6-DaHall 1-PDU-05 | [branch#026] [A] W | 6-DaHall 1-PDU-06 | [branch#026] [A] W | 0 | 7-DaHall 1-A-2-35-577-DaHall 1-B-2-35-57 | 7-DaHall 1-A-2-35-57 | 7-DaHall 1-B-2-35-57 | 7-DaHall 1-A-2-35 | [branch#057] [A] W | 7-DaHall 1-B-2-35 | [branch#057] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-55-DaHall 1-PDU-06-30-5 | 5-DaHall 1-PDU-05-30-5 | 5-DaHall 1-PDU-06-30-5 | 5-DaHall 1-PDU-05 | [branch#005] [A] W | 5-DaHall 1-PDU-06 | [branch#005] [A] W | 0 | 6-DaHall 1-PDU-05-30-286-DaHall 1-PDU-06-30-28 | 6-DaHall 1-PDU-05-30-28 | 6-DaHall 1-PDU-06-30-28 | 6-DaHall 1-PDU-05 | [branch#028] [A] W | 6-DaHall 1-PDU-06 | [branch#028] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-95-DaHall 1-PDU-06-30-7 | 5-DaHall 1-PDU-05-30-9 | 5-DaHall 1-PDU-06-30-7 | 5-DaHall 1-PDU-05 | [branch#009] [A] W | 5-DaHall 1-PDU-06 | [branch#007] [A] W | 0 | 6-DaHall 1-PDU-05-30-306-DaHall 1-PDU-06-30-30 | 6-DaHall 1-PDU-05-30-30 | 6-DaHall 1-PDU-06-30-30 | 6-DaHall 1-PDU-05 | [branch#030] [A] W | 6-DaHall 1-PDU-06 | [branch#030] [A] W | 0 | 7-DaHall 1-A-1-50-207-DaHall 1-B-1-50-20 | 7-DaHall 1-A-1-50-20 | 7-DaHall 1-B-1-50-20 | 7-DaHall 1-A-1-50 | [branch#020] [A] W | 7-DaHall 1-B-1-50 | [branch#020] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-115-DaHall 1-PDU-06-30-9 | 5-DaHall 1-PDU-05-30-11 | 5-DaHall 1-PDU-06-30-9 | 5-DaHall 1-PDU-05 | [branch#011] [A] W | 5-DaHall 1-PDU-06 | [branch#009] [A] W | 0 | 6-DaHall 1-PDU-05-30-326-DaHall 1-PDU-06-30-32 | 6-DaHall 1-PDU-05-30-32 | 6-DaHall 1-PDU-06-30-32 | 6-DaHall 1-PDU-05 | [branch#032] [A] W | 6-DaHall 1-PDU-06 | [branch#032] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-135-DaHall 1-PDU-06-30-11 | 5-DaHall 1-PDU-05-30-13 | 5-DaHall 1-PDU-06-30-11 | 5-DaHall 1-PDU-05 | [branch#013] [A] W | 5-DaHall 1-PDU-06 | [branch#011] [A] W | 0 | 6-DaHall 1-PDU-05-30-346-DaHall 1-PDU-06-30-34 | 6-DaHall 1-PDU-05-30-34 | 6-DaHall 1-PDU-06-30-34 | 6-DaHall 1-PDU-05 | [branch#034] [A] W | 6-DaHall 1-PDU-06 | [branch#034] [A] W | 0 | 7-DaHall 1-A-1-35-11(1)7-DaHall 1-B-1-35-14(1) | 7-DaHall 1-A-1-35-11(1) | 7-DaHall 1-B-1-35-14(1) | 7-DaHall 1-A-1-35 | [branch#011(1)] [A] W | 7-DaHall 1-B-1-35 | [branch#014(1)] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-155-DaHall 1-PDU-06-30-15 | 5-DaHall 1-PDU-05-30-15 | 5-DaHall 1-PDU-06-30-15 | 5-DaHall 1-PDU-05 | [branch#015] [A] W | 5-DaHall 1-PDU-06 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-05-30-366-DaHall 1-PDU-06-30-36 | 6-DaHall 1-PDU-05-30-36 | 6-DaHall 1-PDU-06-30-36 | 6-DaHall 1-PDU-05 | [branch#036] [A] W | 6-DaHall 1-PDU-06 | [branch#036] [A] W | 0 | 7-DaHall 1-A-1-35-15(2)7-DaHall 1-B-1-35-15(2) | 7-DaHall 1-A-1-35-15(2) | 7-DaHall 1-B-1-35-15(2) | 7-DaHall 1-A-1-35 | [branch#015(2)] [A] W | 7-DaHall 1-B-1-35 | [branch#015(2)] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-175-DaHall 1-PDU-06-30-17 | 5-DaHall 1-PDU-05-30-17 | 5-DaHall 1-PDU-06-30-17 | 5-DaHall 1-PDU-05 | [branch#017] [A] W | 5-DaHall 1-PDU-06 | [branch#017] [A] W | 0 | [7 empty] | 0 | [7 empty] | 0
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-05-30-546-DaHall 1-PDU-06-30-54 | 6-DaHall 1-PDU-05-30-54 | 6-DaHall 1-PDU-06-30-54 | 6-DaHall 1-PDU-05 | [branch#054] [A] W | 6-DaHall 1-PDU-06 | [branch#054] [A] W | 1.426 | 7-DaHall 1-B-1-35-167-DaHall 1-A-1-35-16 | 7-DaHall 1-B-1-35-16 | 7-DaHall 1-A-1-35-16 | 7-DaHall 1-B-1-35 | [branch#016] [A] W | 7-DaHall 1-A-1-35 | [branch#016] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-05-30-26-DaHall 1-PDU-06-30-2 | 6-DaHall 1-PDU-05-30-2 | 6-DaHall 1-PDU-06-30-2 | 6-DaHall 1-PDU-05 | [branch#002] [A] W | 6-DaHall 1-PDU-06 | [branch#002] [A] W | 5.421 | 7-DaHall 1-A-1-50-177-DaHall 1-B-1-50-17 | 7-DaHall 1-A-1-50-17 | 7-DaHall 1-B-1-50-17 | 7-DaHall 1-A-1-50 | [branch#017] [A] W | 7-DaHall 1-B-1-50 | [branch#017] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-195-DaHall 1-PDU-06-30-19 | 5-DaHall 1-PDU-05-30-19 | 5-DaHall 1-PDU-06-30-19 | 5-DaHall 1-PDU-05 | [branch#019] [A] W | 5-DaHall 1-PDU-06 | [branch#019] [A] W | 0 | 6-DaHall 1-PDU-05-30-46-DaHall 1-PDU-06-30-4 | 6-DaHall 1-PDU-05-30-4 | 6-DaHall 1-PDU-06-30-4 | 6-DaHall 1-PDU-05 | [branch#004] [A] W | 6-DaHall 1-PDU-06 | [branch#004] [A] W | 2.094 | 7-DaHall 1-A-1-50-567-DaHall 1-B-1-50-56 | 7-DaHall 1-A-1-50-56 | 7-DaHall 1-B-1-50-56 | 7-DaHall 1-A-1-50 | [branch#056] [A] W | 7-DaHall 1-B-1-50 | [branch#056] [A] W | #N/A
4-DaHall 1-PDU-06-100-24-DaHall 1-PDU-05-100-2 | 4-DaHall 1-PDU-06-100-2 | 4-DaHall 1-PDU-05-100-2 | 4-DaHall 1-PDU-06 | [branch#002] [A] W | 4-DaHall 1-PDU-05 | [branch#002] [A] W | 0 | 5-DaHall 1-PDU-05-30-215-DaHall 1-PDU-06-30-21 | 5-DaHall 1-PDU-05-30-21 | 5-DaHall 1-PDU-06-30-21 | 5-DaHall 1-PDU-05 | [branch#021] [A] W | 5-DaHall 1-PDU-06 | [branch#021] [A] W | 0 | 6-DaHall 1-PDU-05-30-66-DaHall 1-PDU-06-30-6 | 6-DaHall 1-PDU-05-30-6 | 6-DaHall 1-PDU-06-30-6 | 6-DaHall 1-PDU-05 | [branch#006] [A] W | 6-DaHall 1-PDU-06 | [branch#006] [A] W | 0.28 | 7-DaHall 1-A-1-100-197-DaHall 1-B-1-100-19 | 7-DaHall 1-A-1-100-19 | 7-DaHall 1-B-1-100-19 | 7-DaHall 1-A-1-10 | [branch#019] [A] W | 7-DaHall 1-B-1-10 | [branch#019] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-235-DaHall 1-PDU-06-30-23 | 5-DaHall 1-PDU-05-30-23 | 5-DaHall 1-PDU-06-30-23 | 5-DaHall 1-PDU-05 | [branch#023] [A] W | 5-DaHall 1-PDU-06 | [branch#023] [A] W | 0 | 6-DaHall 1-PDU-05-30-86-DaHall 1-PDU-06-30-8 | 6-DaHall 1-PDU-05-30-8 | 6-DaHall 1-PDU-06-30-8 | 6-DaHall 1-PDU-05 | [branch#008] [A] W | 6-DaHall 1-PDU-06 | [branch#008] [A] W | 1.699 | 7-DaHall 1-RPP-01-30-327-DaHall 1-RPP-02-30-26 | 7-DaHall 1-RPP-01-30-32 | 7-DaHall 1-RPP-02-30-26 | 7-DaHall 1-RPP-01 | [branch#032] [A] W | 7-DaHall 1-RPP-02 | [branch#026] [A] W | 0.05
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-275-DaHall 1-PDU-06-30-25 | 5-DaHall 1-PDU-05-30-27 | 5-DaHall 1-PDU-06-30-25 | 5-DaHall 1-PDU-05 | [branch#027] [A] W | 5-DaHall 1-PDU-06 | [branch#025] [A] W | 0 | 6-DaHall 1-PDU-05-30-106-DaHall 1-PDU-06-30-10 | 6-DaHall 1-PDU-05-30-10 | 6-DaHall 1-PDU-06-30-10 | 6-DaHall 1-PDU-05 | [branch#010] [A] W | 6-DaHall 1-PDU-06 | [branch#010] [A] W | 0.302 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-295-DaHall 1-PDU-06-30-27 | 5-DaHall 1-PDU-05-30-29 | 5-DaHall 1-PDU-06-30-27 | 5-DaHall 1-PDU-05 | [branch#029] [A] W | 5-DaHall 1-PDU-06 | [branch#027] [A] W | 0 | 6-DaHall 1-PDU-05-30-126-DaHall 1-PDU-06-30-12 | 6-DaHall 1-PDU-05-30-12 | 6-DaHall 1-PDU-06-30-12 | 6-DaHall 1-PDU-05 | [branch#012] [A] W | 6-DaHall 1-PDU-06 | [branch#012] [A] W | 0.302 | 7-DaHall 1-RPP-01-30-127-DaHall 1-RPP-02-20-17 | 7-DaHall 1-RPP-01-30-12 | 7-DaHall 1-RPP-02-20-17 | 7-DaHall 1-RPP-01 | [branch#012] [A] W | 7-DaHall 1-RPP-02 | [branch#017] [A] W | 1.981
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-315-DaHall 1-PDU-06-30-29 | 5-DaHall 1-PDU-05-30-31 | 5-DaHall 1-PDU-06-30-29 | 5-DaHall 1-PDU-05 | [branch#031] [A] W | 5-DaHall 1-PDU-06 | [branch#029] [A] W | 0 | 6-DaHall 1-PDU-05-30-146-DaHall 1-PDU-06-30-14 | 6-DaHall 1-PDU-05-30-14 | 6-DaHall 1-PDU-06-30-14 | 6-DaHall 1-PDU-05 | [branch#014] [A] W | 6-DaHall 1-PDU-06 | [branch#014] [A] W | 1.857 | 7-DaHall 1-A-1-35-447-DaHall 1-B-1-35-6 | 7-DaHall 1-A-1-35-44 | 7-DaHall 1-B-1-35-6 | 7-DaHall 1-A-1-35 | [branch#044] [A] W | 7-DaHall 1-B-1-35 | [branch#006] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-335-DaHall 1-PDU-06-30-33 | 5-DaHall 1-PDU-05-30-33 | 5-DaHall 1-PDU-06-30-33 | 5-DaHall 1-PDU-05 | [branch#033] [A] W | 5-DaHall 1-PDU-06 | [branch#033] [A] W | 0 | 6-DaHall 1-PDU-05-30-166-DaHall 1-PDU-06-30-16 | 6-DaHall 1-PDU-05-30-16 | 6-DaHall 1-PDU-06-30-16 | 6-DaHall 1-PDU-05 | [branch#016] [A] W | 6-DaHall 1-PDU-06 | [branch#016] [A] W | 1.671 | 7-DaHall 1-RPP-01-30-107-DaHall 1-RPP-02-20-15 | 7-DaHall 1-RPP-01-30-10 | 7-DaHall 1-RPP-02-20-15 | 7-DaHall 1-RPP-01 | [branch#010] [A] W | 7-DaHall 1-RPP-02 | [branch#015] [A] W | 0.712
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-355-DaHall 1-PDU-06-30-35 | 5-DaHall 1-PDU-05-30-35 | 5-DaHall 1-PDU-06-30-35 | 5-DaHall 1-PDU-05 | [branch#035] [A] W | 5-DaHall 1-PDU-06 | [branch#035] [A] W | 0 | 6-DaHall 1-PDU-01-30-436-DaHall 1-PDU-02-30-43 | 6-DaHall 1-PDU-01-30-43 | 6-DaHall 1-PDU-02-30-43 | 6-DaHall 1-PDU-01 | [branch#043] [A] W | 6-DaHall 1-PDU-02 | [branch#043] [A] W | 2.527 | 7-DaHall 1-A-1-35-437-DaHall 1-B-1-35-5 | 7-DaHall 1-A-1-35-43 | 7-DaHall 1-B-1-35-5 | 7-DaHall 1-A-1-35 | [branch#043] [A] W | 7-DaHall 1-B-1-35 | [branch#005] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-01-30-426-DaHall 1-PDU-02-30-42 | 6-DaHall 1-PDU-01-30-42 | 6-DaHall 1-PDU-02-30-42 | 6-DaHall 1-PDU-01 | [branch#042] [A] W | 6-DaHall 1-PDU-02 | [branch#042] [A] W | 1.922 | 7-DaHall 1-RPP-01-30-87-DaHall 1-RPP-02-20-13 | 7-DaHall 1-RPP-01-30-8 | 7-DaHall 1-RPP-02-20-13 | 7-DaHall 1-RPP-01 | [branch#008] [A] W | 7-DaHall 1-RPP-02 | [branch#013] [A] W | 1.022
[7 empty] | 0 | [7 empty] | 0 | [7 empty] | 0 | 7-DaHall 1-PDU-01-30-87-DaHall 1-RPP-02-20-9 | 7-DaHall 1-PDU-01-30-8 | 7-DaHall 1-RPP-02-20-9 | 7-DaHall 1-PDU-01 | [branch#008] [A] W | 7-DaHall 1-RPP-02 | [branch#009] [A] W | 0.82
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-375-DaHall 1-PDU-06-30-37 | 5-DaHall 1-PDU-05-30-37 | 5-DaHall 1-PDU-06-30-37 | 5-DaHall 1-PDU-05 | [branch#037] [A] W | 5-DaHall 1-PDU-06 | [branch#037] [A] W | 0 | 6-DaHall 1-PDU-05-30-386-DaHall 1-PDU-06-30-38 | 6-DaHall 1-PDU-05-30-38 | 6-DaHall 1-PDU-06-30-38 | 6-DaHall 1-PDU-05 | [branch#038] [A] W | 6-DaHall 1-PDU-06 | [branch#038] [A] W | 0 | [7 empty] | 0
4-DaHall 1-PDU-06-100-14-DaHall 1-PDU-05-100-1 | 4-DaHall 1-PDU-06-100-1 | 4-DaHall 1-PDU-05-100-1 | 4-DaHall 1-PDU-06 | [branch#001] [A] W | 4-DaHall 1-PDU-05 | [branch#001] [A] W | 4.537 | 5-DaHall 1-PDU-05-30-395-DaHall 1-PDU-06-30-39 | 5-DaHall 1-PDU-05-30-39 | 5-DaHall 1-PDU-06-30-39 | 5-DaHall 1-PDU-05 | [branch#039] [A] W | 5-DaHall 1-PDU-06 | [branch#039] [A] W | 0 | 6-DaHall 1-PDU-05-30-406-DaHall 1-PDU-06-30-40 | 6-DaHall 1-PDU-05-30-40 | 6-DaHall 1-PDU-06-30-40 | 6-DaHall 1-PDU-05 | [branch#040] [A] W | 6-DaHall 1-PDU-06 | [branch#040] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-415-DaHall 1-PDU-06-30-41 | 5-DaHall 1-PDU-05-30-41 | 5-DaHall 1-PDU-06-30-41 | 5-DaHall 1-PDU-05 | [branch#041] [A] W | 5-DaHall 1-PDU-06 | [branch#041] [A] W | 0 | 6-DaHall 1-PDU-05-30-426-DaHall 1-PDU-06-30-42 | 6-DaHall 1-PDU-05-30-42 | 6-DaHall 1-PDU-06-30-42 | 6-DaHall 1-PDU-05 | [branch#042] [A] W | 6-DaHall 1-PDU-06 | [branch#042] [A] W | 0 | 7-DaHall 1-A-1-100-247-DaHall 1-B-1-100-24 | 7-DaHall 1-A-1-100-24 | 7-DaHall 1-B-1-100-24 | 7-DaHall 1-A-1-10 | [branch#024] [A] W | 7-DaHall 1-B-1-10 | [branch#024] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-455-DaHall 1-PDU-06-30-43 | 5-DaHall 1-PDU-05-30-45 | 5-DaHall 1-PDU-06-30-43 | 5-DaHall 1-PDU-05 | [branch#045] [A] W | 5-DaHall 1-PDU-06 | [branch#043] [A] W | 0 | 6-DaHall 1-PDU-05-30-446-DaHall 1-PDU-06-30-44 | 6-DaHall 1-PDU-05-30-44 | 6-DaHall 1-PDU-06-30-44 | 6-DaHall 1-PDU-05 | [branch#044] [A] W | 6-DaHall 1-PDU-06 | [branch#044] [A] W | 0 | 7-DaHall 1-A-1-100-77-DaHall 1-B-1-100-7 | 7-DaHall 1-A-1-100-7 | 7-DaHall 1-B-1-100-7 | 7-DaHall 1-A-1-10 | [branch#007] [A] W | 7-DaHall 1-B-1-10 | [branch#007] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-475-DaHall 1-PDU-06-30-45 | 5-DaHall 1-PDU-05-30-47 | 5-DaHall 1-PDU-06-30-45 | 5-DaHall 1-PDU-05 | [branch#047] [A] W | 5-DaHall 1-PDU-06 | [branch#045] [A] W | 0 | 6-DaHall 1-PDU-05-30-466-DaHall 1-PDU-06-30-46 | 6-DaHall 1-PDU-05-30-46 | 6-DaHall 1-PDU-06-30-46 | 6-DaHall 1-PDU-05 | [branch#046] [A] W | 6-DaHall 1-PDU-06 | [branch#046] [A] W | 0 | 7-DaHall 1-A-1-50-577-DaHall 1-B-1-50-57 | 7-DaHall 1-A-1-50-57 | 7-DaHall 1-B-1-50-57 | 7-DaHall 1-A-1-50 | [branch#057] [A] W | 7-DaHall 1-B-1-50 | [branch#057] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-495-DaHall 1-PDU-06-30-47 | 5-DaHall 1-PDU-05-30-49 | 5-DaHall 1-PDU-06-30-47 | 5-DaHall 1-PDU-05 | [branch#049] [A] W | 5-DaHall 1-PDU-06 | [branch#047] [A] W | 0 | 6-DaHall 1-PDU-13-30-16-DaHall 1-PDU-14-30-1 | 6-DaHall 1-PDU-13-30-1 | 6-DaHall 1-PDU-14-30-1 | 6-DaHall 1-PDU-13 | [branch#001] [A] W | 6-DaHall 1-PDU-14 | [branch#001] [A] W | 0 | 7-DaHall 1-A-1-50-217-DaHall 1-B-1-50-21 | 7-DaHall 1-A-1-50-21 | 7-DaHall 1-B-1-50-21 | 7-DaHall 1-A-1-50 | [branch#021] [A] W | 7-DaHall 1-B-1-50 | [branch#021] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-515-DaHall 1-PDU-06-30-51 | 5-DaHall 1-PDU-05-30-51 | 5-DaHall 1-PDU-06-30-51 | 5-DaHall 1-PDU-05 | [branch#051] [A] W | 5-DaHall 1-PDU-06 | [branch#051] [A] W | 0 | 6-DaHall 1-PDU-13-30-36-DaHall 1-PDU-14-30-3 | 6-DaHall 1-PDU-13-30-3 | 6-DaHall 1-PDU-14-30-3 | 6-DaHall 1-PDU-13 | [branch#003] [A] W | 6-DaHall 1-PDU-14 | [branch#003] [A] W | 0 | 7-DaHall 1-A-1-100-187-DaHall 1-B-1-100-18 | 7-DaHall 1-A-1-100-18 | 7-DaHall 1-B-1-100-18 | 7-DaHall 1-A-1-10 | [branch#018] [A] W | 7-DaHall 1-B-1-10 | [branch#018] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-535-DaHall 1-PDU-06-30-53 | 5-DaHall 1-PDU-05-30-53 | 5-DaHall 1-PDU-06-30-53 | 5-DaHall 1-PDU-05 | [branch#053] [A] W | 5-DaHall 1-PDU-06 | [branch#053] [A] W | 0 | 6-DaHall 1-PDU-13-30-56-DaHall 1-PDU-14-30-5 | 6-DaHall 1-PDU-13-30-5 | 6-DaHall 1-PDU-14-30-5 | 6-DaHall 1-PDU-13 | [branch#005] [A] W | 6-DaHall 1-PDU-14 | [branch#005] [A] W | 0 | 7-DaHall 1-A-1-100-237-DaHall 1-B-1-100-23 | 7-DaHall 1-A-1-100-23 | 7-DaHall 1-B-1-100-23 | 7-DaHall 1-A-1-10 | [branch#023] [A] W | 7-DaHall 1-B-1-10 | [branch#023] [A] W | #N/A
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-13-30-76-DaHall 1-PDU-14-30-7 | 6-DaHall 1-PDU-13-30-7 | 6-DaHall 1-PDU-14-30-7 | 6-DaHall 1-PDU-13 | [branch#007] [A] W | 6-DaHall 1-PDU-14 | [branch#007] [A] W | 0 | 7-DaHall 1-PDU-01-30-307-DaHall 1-PDU-02-30-30 | 7-DaHall 1-PDU-01-30-30 | 7-DaHall 1-PDU-02-30-30 | 7-DaHall 1-PDU-01 | [branch#030] [A] W | 7-DaHall 1-PDU-02 | [branch#030] [A] W | 0.157
[7 empty] | 0 | [7 empty] | 0 | [7 empty] | 0 | 7-DaHall 1-PDU-01-30-137-DaHall 1-PDU-02-30-13 | 7-DaHall 1-PDU-01-30-13 | 7-DaHall 1-PDU-02-30-13 | 7-DaHall 1-PDU-01 | [branch#013] [A] W | 7-DaHall 1-PDU-02 | [branch#013] [A] W | 2.536
[7 empty] | 0 | 5-DaHall 1-PDU-19-50-225-DaHall 1-PDU-20-50-22 | 5-DaHall 1-PDU-19-50-22 | 5-DaHall 1-PDU-20-50-22 | 5-DaHall 1-PDU-19 | [branch#022] [A] W | 5-DaHall 1-PDU-20 | 3095 [branch#22] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-PDU-01-30-117-DaHall 1-PDU-02-30-11 | 7-DaHall 1-PDU-01-30-11 | 7-DaHall 1-PDU-02-30-11 | 7-DaHall 1-PDU-01 | [branch#011] [A] W | 7-DaHall 1-PDU-02 | [branch#011] [A] W | 2.499
4-DaHall 1-PDU-02-100-64-DaHall 1-PDU-01-100-6 | 4-DaHall 1-PDU-02-100-6 | 4-DaHall 1-PDU-01-100-6 | 4-DaHall 1-PDU-02 | [branch#006] [A] W | 4-DaHall 1-PDU-01 | [branch#006] [A] W | 7.685 | 5-DaHall 1-PDU-21-50-225-DaHall 1-PDU-22-50-22 | 5-DaHall 1-PDU-21-50-22 | 5-DaHall 1-PDU-22-50-22 | 5-DaHall 1-PDU-21 | [branch#022] [A] W | 5-DaHall 1-PDU-22 | 3095 [branch#22] [A] W | #N/A | 6-DaHall 1-PDU-13-30-526-DaHall 1-PDU-14-30-52 | 6-DaHall 1-PDU-13-30-52 | 6-DaHall 1-PDU-14-30-52 | 6-DaHall 1-PDU-13 | [branch#052] [A] W | 6-DaHall 1-PDU-14 | [branch#052] [A] W | 0 | 7-DaHall 1-PDU-01-30-177-DaHall 1-PDU-02-30-17 | 7-DaHall 1-PDU-01-30-17 | 7-DaHall 1-PDU-02-30-17 | 7-DaHall 1-PDU-01 | [branch#017] [A] W | 7-DaHall 1-PDU-02 | [branch#017] [A] W | 1.484
[7 empty] | 0 | 5-DaHall 1-PDU-19-50-205-DaHall 1-PDU-20-50-20 | 5-DaHall 1-PDU-19-50-20 | 5-DaHall 1-PDU-20-50-20 | 5-DaHall 1-PDU-19 | [branch#020] [A] W | 5-DaHall 1-PDU-20 | 2815 [branch#20] [A] W | #N/A | 6-DaHall 1-PDU-11-30-36-DaHall 1-PDU-12-30-3 | 6-DaHall 1-PDU-11-30-3 | 6-DaHall 1-PDU-12-30-3 | 6-DaHall 1-PDU-11 | [branch#003] [A] W | 6-DaHall 1-PDU-12 | [branch#003] [A] W | 0 | 7-DaHall 1-PDU-01-30-277-DaHall 1-PDU-02-30-27 | 7-DaHall 1-PDU-01-30-27 | 7-DaHall 1-PDU-02-30-27 | 7-DaHall 1-PDU-01 | [branch#027] [A] W | 7-DaHall 1-PDU-02 | [branch#027] [A] W | 1.67
[7 empty] | 0 | 5-DaHall 1-PDU-21-50-205-DaHall 1-PDU-22-50-20 | 5-DaHall 1-PDU-21-50-20 | 5-DaHall 1-PDU-22-50-20 | 5-DaHall 1-PDU-21 | [branch#020] [A] W | 5-DaHall 1-PDU-22 | 2815 [branch#20] [A] W | #N/A | 6-DaHall 1-PDU-11-30-56-DaHall 1-PDU-12-30-5 | 6-DaHall 1-PDU-11-30-5 | 6-DaHall 1-PDU-12-30-5 | 6-DaHall 1-PDU-11 | [branch#005] [A] W | 6-DaHall 1-PDU-12 | [branch#005] [A] W | 0 | 7-DaHall 1-PDU-01-30-197-DaHall 1-PDU-02-30-19 | 7-DaHall 1-PDU-01-30-19 | 7-DaHall 1-PDU-02-30-19 | 7-DaHall 1-PDU-01 | [branch#019] [A] W | 7-DaHall 1-PDU-02 | [branch#019] [A] W | 2.786
[7 empty] | 0 | 5-DaHall 1-PDU-19-50-185-DaHall 1-PDU-20-50-18 | 5-DaHall 1-PDU-19-50-18 | 5-DaHall 1-PDU-20-50-18 | 5-DaHall 1-PDU-19 | [branch#018] [A] W | 5-DaHall 1-PDU-20 | 2535 [branch#18] [A] W | #N/A | 6-DaHall 1-PDU-11-30-76-DaHall 1-PDU-12-30-7 | 6-DaHall 1-PDU-11-30-7 | 6-DaHall 1-PDU-12-30-7 | 6-DaHall 1-PDU-11 | [branch#007] [A] W | 6-DaHall 1-PDU-12 | [branch#007] [A] W | 0 | 7-DaHall 1-PDU-01-30-217-DaHall 1-PDU-02-30-21 | 7-DaHall 1-PDU-01-30-21 | 7-DaHall 1-PDU-02-30-21 | 7-DaHall 1-PDU-01 | [branch#021] [A] W | 7-DaHall 1-PDU-02 | [branch#021] [A] W | 1.791
[7 empty] | 0 | 5-DaHall 1-PDU-21-50-185-DaHall 1-PDU-22-50-18 | 5-DaHall 1-PDU-21-50-18 | 5-DaHall 1-PDU-22-50-18 | 5-DaHall 1-PDU-21 | [branch#018] [A] W | 5-DaHall 1-PDU-22 | 2535 [branch#18] [A] W | #N/A | 6-DaHall 1-PDU-11-30-96-DaHall 1-PDU-12-30-9 | 6-DaHall 1-PDU-11-30-9 | 6-DaHall 1-PDU-12-30-9 | 6-DaHall 1-PDU-11 | [branch#009] [A] W | 6-DaHall 1-PDU-12 | [branch#009] [A] W | 0 | 7-DaHall 1-PDU-01-30-237-DaHall 1-PDU-02-30-23 | 7-DaHall 1-PDU-01-30-23 | 7-DaHall 1-PDU-02-30-23 | 7-DaHall 1-PDU-01 | [branch#023] [A] W | 7-DaHall 1-PDU-02 | [branch#023] [A] W | 1.021
[7 empty] | 0 | 5-DaHall 1-PDU-19-50-165-DaHall 1-PDU-20-50-16 | 5-DaHall 1-PDU-19-50-16 | 5-DaHall 1-PDU-20-50-16 | 5-DaHall 1-PDU-19 | [branch#016] [A] W | 5-DaHall 1-PDU-20 | 2255 [branch#16] [A] W | #N/A | 6-DaHall 1-PDU-11-30-116-DaHall 1-PDU-12-30-11 | 6-DaHall 1-PDU-11-30-11 | 6-DaHall 1-PDU-12-30-11 | 6-DaHall 1-PDU-11 | [branch#011] [A] W | 6-DaHall 1-PDU-12 | [branch#011] [A] W | 0 | 7-DaHall 1-PDU-01-30-257-DaHall 1-PDU-02-30-25 | 7-DaHall 1-PDU-01-30-25 | 7-DaHall 1-PDU-02-30-25 | 7-DaHall 1-PDU-01 | [branch#025] [A] W | 7-DaHall 1-PDU-02 | [branch#025] [A] W | 0.734
[7 empty] | 0 | 5-DaHall 1-PDU-21-50-165-DaHall 1-PDU-22-50-16 | 5-DaHall 1-PDU-21-50-16 | 5-DaHall 1-PDU-22-50-16 | 5-DaHall 1-PDU-21 | [branch#016] [A] W | 5-DaHall 1-PDU-22 | 2255 [branch#16] [A] W | #N/A | 6-DaHall 1-PDU-11-30-136-DaHall 1-PDU-09-30-31 | 6-DaHall 1-PDU-11-30-13 | 6-DaHall 1-PDU-09-30-31 | 6-DaHall 1-PDU-11 | [branch#013] [A] W | 6-DaHall 1-PDU-09 | [branch#031] [A] W | 0 | 7-DaHall 1-PDU-01-30-327-DaHall 1-PDU-02-30-32 | 7-DaHall 1-PDU-01-30-32 | 7-DaHall 1-PDU-02-30-32 | 7-DaHall 1-PDU-01 | [branch#032] [A] W | 7-DaHall 1-PDU-02 | [branch#032] [A] W | 0.762
[7 empty] | 0 | 5-DaHall 1-PDU-19-50-215-DaHall 1-PDU-20-50-21 | 5-DaHall 1-PDU-19-50-21 | 5-DaHall 1-PDU-20-50-21 | 5-DaHall 1-PDU-19 | [branch#021] [A] W | 5-DaHall 1-PDU-20 | 2955 [branch#21] [A] W | #N/A | 6-DaHall 1-PDU-11-30-156-DaHall 1-PDU-12-30-15 | 6-DaHall 1-PDU-11-30-15 | 6-DaHall 1-PDU-12-30-15 | 6-DaHall 1-PDU-11 | [branch#015] [A] W | 6-DaHall 1-PDU-12 | [branch#015] [A] W | 0 | 7-DaHall 1-PDU-01-30-417-DaHall 1-PDU-02-30-41 | 7-DaHall 1-PDU-01-30-41 | 7-DaHall 1-PDU-02-30-41 | 7-DaHall 1-PDU-01 | [branch#041] [A] W | 7-DaHall 1-PDU-02 | [branch#041] [A] W | 0.18
[7 empty] | 0 | 5-DaHall 1-PDU-21-50-215-DaHall 1-PDU-22-50-21 | 5-DaHall 1-PDU-21-50-21 | 5-DaHall 1-PDU-22-50-21 | 5-DaHall 1-PDU-21 | [branch#021] [A] W | 5-DaHall 1-PDU-22 | 2955 [branch#21] [A] W | #N/A | 6-DaHall 1-PDU-11-30-176-DaHall 1-PDU-12-30-17 | 6-DaHall 1-PDU-11-30-17 | 6-DaHall 1-PDU-12-30-17 | 6-DaHall 1-PDU-11 | [branch#017] [A] W | 6-DaHall 1-PDU-12 | [branch#017] [A] W | 0 | 7-DaHall 1-RPP-01-20-197-DaHall 1-RPP-02-30-10 | 7-DaHall 1-RPP-01-20-19 | 7-DaHall 1-RPP-02-30-10 | 7-DaHall 1-RPP-01 | [branch#019] [A] W | 7-DaHall 1-RPP-02 | [branch#010] [A] W | 0.28
[7 empty] | 0 | 5-DaHall 1-PDU-19-30-195-DaHall 1-PDU-20-30-19 | 5-DaHall 1-PDU-19-30-19 | 5-DaHall 1-PDU-20-30-19 | 5-DaHall 1-PDU-19 | [branch#019] [A] W | 5-DaHall 1-PDU-20 | 2675 [branch#19] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-PDU-01-30-447-DaHall 1-PDU-02-30-44 | 7-DaHall 1-PDU-01-30-44 | 7-DaHall 1-PDU-02-30-44 | 7-DaHall 1-PDU-01 | [branch#044] [A] W | 7-DaHall 1-PDU-02 | [branch#044] [A] W | 2.434
4-DaHall 1-PDU-02-100-74-DaHall 1-PDU-01-100-7 | 4-DaHall 1-PDU-02-100-7 | 4-DaHall 1-PDU-01-100-7 | 4-DaHall 1-PDU-02 | [branch#007] [A] W | 4-DaHall 1-PDU-01 | [branch#007] [A] W | 8.855 | 5-DaHall 1-PDU-21-30-195-DaHall 1-PDU-22-30-19 | 5-DaHall 1-PDU-21-30-19 | 5-DaHall 1-PDU-22-30-19 | 5-DaHall 1-PDU-21 | [branch#019] [A] W | 5-DaHall 1-PDU-22 | 2675 [branch#19] [A] W | #N/A | 6-DaHall 1-PDU-11-30-26-DaHall 1-PDU-12-30-2 | 6-DaHall 1-PDU-11-30-2 | 6-DaHall 1-PDU-12-30-2 | 6-DaHall 1-PDU-11 | [branch#002] [A] W | 6-DaHall 1-PDU-12 | [branch#002] [A] W | 0 | 7-DaHall 1-PDU-01-30-27-DaHall 1-PDU-02-30-2 | 7-DaHall 1-PDU-01-30-2 | 7-DaHall 1-PDU-02-30-2 | 7-DaHall 1-PDU-01 | [branch#002] [A] W | 7-DaHall 1-PDU-02 | [branch#002] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-19-30-175-DaHall 1-PDU-20-30-17 | 5-DaHall 1-PDU-19-30-17 | 5-DaHall 1-PDU-20-30-17 | 5-DaHall 1-PDU-19 | [branch#017] [A] W | 5-DaHall 1-PDU-20 | 2395 [branch#17] [A] W | #N/A | 6-DaHall 1-PDU-11-30-46-DaHall 1-PDU-12-30-4 | 6-DaHall 1-PDU-11-30-4 | 6-DaHall 1-PDU-12-30-4 | 6-DaHall 1-PDU-11 | [branch#004] [A] W | 6-DaHall 1-PDU-12 | [branch#004] [A] W | 0 | 7-DaHall 1-A-1-35-507-DaHall 1-B-1-50-47 | 7-DaHall 1-A-1-35-50 | 7-DaHall 1-B-1-50-47 | 7-DaHall 1-A-1-35 | [branch#050] [A] W | 7-DaHall 1-B-1-50 | [branch#047] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-21-30-175-DaHall 1-PDU-22-30-17 | 5-DaHall 1-PDU-21-30-17 | 5-DaHall 1-PDU-22-30-17 | 5-DaHall 1-PDU-21 | [branch#017] [A] W | 5-DaHall 1-PDU-22 | 2395 [branch#17] [A] W | #N/A | 6-DaHall 1-PDU-11-30-66-DaHall 1-PDU-12-30-6 | 6-DaHall 1-PDU-11-30-6 | 6-DaHall 1-PDU-12-30-6 | 6-DaHall 1-PDU-11 | [branch#006] [A] W | 6-DaHall 1-PDU-12 | [branch#006] [A] W | 0 | 7-DaHall 1-PDU-01-30-467-DaHall 1-PDU-02-30-46 | 7-DaHall 1-PDU-01-30-46 | 7-DaHall 1-PDU-02-30-46 | 7-DaHall 1-PDU-01 | [branch#046] [A] W | 7-DaHall 1-PDU-02 | [branch#046] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-19-30-155-DaHall 1-PDU-20-30-15 | 5-DaHall 1-PDU-19-30-15 | 5-DaHall 1-PDU-20-30-15 | 5-DaHall 1-PDU-19 | [branch#015] [A] W | 5-DaHall 1-PDU-20 | 2115 [branch#15] [A] W | #N/A | 6-DaHall 1-PDU-11-30-86-DaHall 1-PDU-12-30-8 | 6-DaHall 1-PDU-11-30-8 | 6-DaHall 1-PDU-12-30-8 | 6-DaHall 1-PDU-11 | [branch#008] [A] W | 6-DaHall 1-PDU-12 | [branch#008] [A] W | 0 | 7-DaHall 1-RPP-01-30-247-DaHall 1-RPP-02-30-18 | 7-DaHall 1-RPP-01-30-24 | 7-DaHall 1-RPP-02-30-18 | 7-DaHall 1-RPP-01 | [branch#024] [A] W | 7-DaHall 1-RPP-02 | [branch#018] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-21-30-155-DaHall 1-PDU-22-30-15 | 5-DaHall 1-PDU-21-30-15 | 5-DaHall 1-PDU-22-30-15 | 5-DaHall 1-PDU-21 | [branch#015] [A] W | 5-DaHall 1-PDU-22 | 2115 [branch#15] [A] W | #N/A | 6-DaHall 1-PDU-11-30-106-DaHall 1-PDU-12-30-10 | 6-DaHall 1-PDU-11-30-10 | 6-DaHall 1-PDU-12-30-10 | 6-DaHall 1-PDU-11 | [branch#010] [A] W | 6-DaHall 1-PDU-12 | [branch#010] [A] W | 0 | 7-DaHall 1-RPP-01-20-337-DaHall 1-RPP-02-20-29 | 7-DaHall 1-RPP-01-20-33 | 7-DaHall 1-RPP-02-20-29 | 7-DaHall 1-RPP-01 | [branch#033] [A] W | 7-DaHall 1-RPP-02 | [branch#029] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-19-30-145-DaHall 1-PDU-20-30-14 | 5-DaHall 1-PDU-19-30-14 | 5-DaHall 1-PDU-20-30-14 | 5-DaHall 1-PDU-19 | [branch#014] [A] W | 5-DaHall 1-PDU-20 | 1975 [branch#14] [A] W | #N/A | 6-DaHall 1-PDU-11-30-126-DaHall 1-PDU-12-30-12 | 6-DaHall 1-PDU-11-30-12 | 6-DaHall 1-PDU-12-30-12 | 6-DaHall 1-PDU-11 | [branch#012] [A] W | 6-DaHall 1-PDU-12 | [branch#012] [A] W | 0 | 7-DaHall 1-RPP-01-30-227-DaHall 1-RPP-02-30-16 | 7-DaHall 1-RPP-01-30-22 | 7-DaHall 1-RPP-02-30-16 | 7-DaHall 1-RPP-01 | [branch#022] [A] W | 7-DaHall 1-RPP-02 | [branch#016] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-21-30-145-DaHall 1-PDU-22-30-14 | 5-DaHall 1-PDU-21-30-14 | 5-DaHall 1-PDU-22-30-14 | 5-DaHall 1-PDU-21 | [branch#014] [A] W | 5-DaHall 1-PDU-22 | 1975 [branch#14] [A] W | #N/A | 6-DaHall 1-PDU-11-30-146-DaHall 1-PDU-10-30-21 | 6-DaHall 1-PDU-11-30-14 | 6-DaHall 1-PDU-10-30-21 | 6-DaHall 1-PDU-11 | [branch#014] [A] W | 6-DaHall 1-PDU-10 | [branch#021] [A] W | 0 | 7-DaHall 1-PDU-01-30-17-DaHall 1-PDU-02-30-1 | 7-DaHall 1-PDU-01-30-1 | 7-DaHall 1-PDU-02-30-1 | 7-DaHall 1-PDU-01 | [branch#001] [A] W | 7-DaHall 1-PDU-02 | [branch#001] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-19-30-125-DaHall 1-PDU-20-30-12 | 5-DaHall 1-PDU-19-30-12 | 5-DaHall 1-PDU-20-30-12 | 5-DaHall 1-PDU-19 | [branch#012] [A] W | 5-DaHall 1-PDU-20 | 1695 [branch#12] [A] W | #N/A | 6-DaHall 1-PDU-11-30-166-DaHall 1-PDU-12-30-16 | 6-DaHall 1-PDU-11-30-16 | 6-DaHall 1-PDU-12-30-16 | 6-DaHall 1-PDU-11 | [branch#016] [A] W | 6-DaHall 1-PDU-12 | [branch#016] [A] W | 0 | 7-DaHall 1-PDU-01-30-127-DaHall 1-PDU-02-30-12 | 7-DaHall 1-PDU-01-30-12 | 7-DaHall 1-PDU-02-30-12 | 7-DaHall 1-PDU-01 | [branch#012] [A] W | 7-DaHall 1-PDU-02 | [branch#012] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-21-30-125-DaHall 1-PDU-22-30-12 | 5-DaHall 1-PDU-21-30-12 | 5-DaHall 1-PDU-22-30-12 | 5-DaHall 1-PDU-21 | [branch#012] [A] W | 5-DaHall 1-PDU-22 | 1695 [branch#12] [A] W | #N/A | 6-DaHall 1-PDU-11-30-186-DaHall 1-PDU-12-30-18 | 6-DaHall 1-PDU-11-30-18 | 6-DaHall 1-PDU-12-30-18 | 6-DaHall 1-PDU-11 | [branch#018] [A] W | 6-DaHall 1-PDU-12 | [branch#018] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-19-50-105-DaHall 1-PDU-20-50-10 | 5-DaHall 1-PDU-19-50-10 | 5-DaHall 1-PDU-20-50-10 | 5-DaHall 1-PDU-19 | [branch#010] [A] W | 5-DaHall 1-PDU-20 | 1415 [branch#10] [A] W | #N/A | [7 empty] | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-21-50-105-DaHall 1-PDU-22-50-10 | 5-DaHall 1-PDU-21-50-10 | 5-DaHall 1-PDU-22-50-10 | 5-DaHall 1-PDU-21 | [branch#010] [A] W | 5-DaHall 1-PDU-22 | 1415 [branch#10] [A] W | #N/A | 6-DaHall 1-PDU-09-30-16-DaHall 1-PDU-10-30-1 | 6-DaHall 1-PDU-09-30-1 | 6-DaHall 1-PDU-10-30-1 | 6-DaHall 1-PDU-09 | [branch#001] [A] W | 6-DaHall 1-PDU-10 | [branch#001] [A] W | 0 | [7 empty] | 0
4-DaHall 1-PDU-04-100-84-DaHall 1-PDU-03-100-8 | 4-DaHall 1-PDU-04-100-8 | 4-DaHall 1-PDU-03-100-8 | 4-DaHall 1-PDU-04 | [branch#008] [A] W | 4-DaHall 1-PDU-03 | [branch#008] [A] W | 8.69 | 5-DaHall 1-PDU-19-50-85-DaHall 1-PDU-20-50-8 | 5-DaHall 1-PDU-19-50-8 | 5-DaHall 1-PDU-20-50-8 | 5-DaHall 1-PDU-19 | [branch#008] [A] W | 5-DaHall 1-PDU-20 | 1135 [branch#08] [A] W | #N/A | 6-DaHall 1-PDU-09-30-36-DaHall 1-PDU-10-30-3 | 6-DaHall 1-PDU-09-30-3 | 6-DaHall 1-PDU-10-30-3 | 6-DaHall 1-PDU-09 | [branch#003] [A] W | 6-DaHall 1-PDU-10 | [branch#003] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-21-50-85-DaHall 1-PDU-22-50-8 | 5-DaHall 1-PDU-21-50-8 | 5-DaHall 1-PDU-22-50-8 | 5-DaHall 1-PDU-21 | [branch#008] [A] W | 5-DaHall 1-PDU-22 | 1135 [branch#08] [A] W | #N/A | 6-DaHall 1-PDU-09-30-56-DaHall 1-PDU-10-30-5 | 6-DaHall 1-PDU-09-30-5 | 6-DaHall 1-PDU-10-30-5 | 6-DaHall 1-PDU-09 | [branch#005] [A] W | 6-DaHall 1-PDU-10 | [branch#005] [A] W | 0 | 7-DaHall 1-RPP-01-20-397-DaHall 1-RPP-02-30-40 | 7-DaHall 1-RPP-01-20-39 | 7-DaHall 1-RPP-02-30-40 | 7-DaHall 1-RPP-01 | [branch#039] [A] W | 7-DaHall 1-RPP-02 | [branch#040] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-19-50-245-DaHall 1-PDU-20-50-24 | 5-DaHall 1-PDU-19-50-24 | 5-DaHall 1-PDU-20-50-24 | 5-DaHall 1-PDU-19 | [branch#024] [A] W | 5-DaHall 1-PDU-20 | 3375 [branch#24] [A] W | #N/A | 6-DaHall 1-PDU-13-30-326-DaHall 1-PDU-14-30-34 | 6-DaHall 1-PDU-13-30-32 | 6-DaHall 1-PDU-14-30-34 | 6-DaHall 1-PDU-13 | [branch#032] [A] W | 6-DaHall 1-PDU-14 | [branch#034] [A] W | 0 | 7-DaHall 1-B-5-35-407-DaHall 1-A-5-35-41 | 7-DaHall 1-B-5-35-40 | 7-DaHall 1-A-5-35-41 | 7-DaHall 1-B-5-35 | [branch#040] [A] W | 7-DaHall 1-A-5-35 | [branch#041] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-21-50-245-DaHall 1-PDU-22-50-24 | 5-DaHall 1-PDU-21-50-24 | 5-DaHall 1-PDU-22-50-24 | 5-DaHall 1-PDU-21 | [branch#024] [A] W | 5-DaHall 1-PDU-22 | 3375 [branch#24] [A] W | #N/A | 6-DaHall 1-PDU-13-30-306-DaHall 1-PDU-14-30-30 | 6-DaHall 1-PDU-13-30-30 | 6-DaHall 1-PDU-14-30-30 | 6-DaHall 1-PDU-13 | [branch#030] [A] W | 6-DaHall 1-PDU-14 | [branch#030] [A] W | 0 | 7-DaHall 1-RPP-01-20-357-DaHall 1-RPP-02-30-34 | 7-DaHall 1-RPP-01-20-35 | 7-DaHall 1-RPP-02-30-34 | 7-DaHall 1-RPP-01 | [branch#035] [A] W | 7-DaHall 1-RPP-02 | [branch#034] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-19-30-65-DaHall 1-PDU-20-30-6 | 5-DaHall 1-PDU-19-30-6 | 5-DaHall 1-PDU-20-30-6 | 5-DaHall 1-PDU-19 | [branch#006] [A] W | 5-DaHall 1-PDU-20 | 0855 [branch#06] [A] W | #N/A | 6-DaHall 1-PDU-09-30-76-DaHall 1-PDU-10-30-7 | 6-DaHall 1-PDU-09-30-7 | 6-DaHall 1-PDU-10-30-7 | 6-DaHall 1-PDU-09 | [branch#007] [A] W | 6-DaHall 1-PDU-10 | [branch#007] [A] W | 0 | 7-DaHall 1-RPP-01-30-187-DaHall 1-PDU-02-30-29 | 7-DaHall 1-RPP-01-30-18 | 7-DaHall 1-PDU-02-30-29 | 7-DaHall 1-RPP-01 | [branch#018] [A] W | 7-DaHall 1-PDU-02 | [branch#029] [A] W | 0.95
[7 empty] | 0 | 5-DaHall 1-PDU-21-30-65-DaHall 1-PDU-22-30-6 | 5-DaHall 1-PDU-21-30-6 | 5-DaHall 1-PDU-22-30-6 | 5-DaHall 1-PDU-21 | [branch#006] [A] W | 5-DaHall 1-PDU-22 | 0855 [branch#06] [A] W | #N/A | 6-DaHall 1-PDU-13-30-346-DaHall 1-PDU-14-30-32 | 6-DaHall 1-PDU-13-30-34 | 6-DaHall 1-PDU-14-30-32 | 6-DaHall 1-PDU-13 | [branch#034] [A] W | 6-DaHall 1-PDU-14 | [branch#032] [A] W | 0 | 7-DaHall 1-RPP-02-30-36 |  | 7-DaHall 1-RPP-02-30-36 |  |  | 7-DaHall 1-RPP-02 | [branch#036] [A] W | 1.693
[7 empty] | 0 | 5-DaHall 1-PDU-19-50-45-DaHall 1-PDU-20-50-4 | 5-DaHall 1-PDU-19-50-4 | 5-DaHall 1-PDU-20-50-4 | 5-DaHall 1-PDU-19 | [branch#004] [A] W | 5-DaHall 1-PDU-20 | 0575 [branch#04] [A] W | #N/A | 6-DaHall 1-PDU-13-30-286-DaHall 1-PDU-14-30-28 | 6-DaHall 1-PDU-13-30-28 | 6-DaHall 1-PDU-14-30-28 | 6-DaHall 1-PDU-13 | [branch#028] [A] W | 6-DaHall 1-PDU-14 | [branch#028] [A] W | 0 | 7-DaHall 1-PDU-01-30-37-DaHall 1-RPP-01-30-16 | 7-DaHall 1-PDU-01-30-3 | 7-DaHall 1-RPP-01-30-16 | 7-DaHall 1-PDU-01 | [branch#003] [A] W | 7-DaHall 1-RPP-01 | [branch#016] [A] W | 0.929
[7 empty] | 0 | 5-DaHall 1-PDU-21-50-45-DaHall 1-PDU-22-50-4 | 5-DaHall 1-PDU-21-50-4 | 5-DaHall 1-PDU-22-50-4 | 5-DaHall 1-PDU-21 | [branch#004] [A] W | 5-DaHall 1-PDU-22 | 0575 [branch#04] [A] W | #N/A | 6-DaHall 1-PDU-09-30-96-DaHall 1-PDU-10-30-9 | 6-DaHall 1-PDU-09-30-9 | 6-DaHall 1-PDU-10-30-9 | 6-DaHall 1-PDU-09 | [branch#009] [A] W | 6-DaHall 1-PDU-10 | [branch#009] [A] W | 0 | 7-DaHall 1-RPP-01-30-267-DaHall 1-RPP-02-30-20 | 7-DaHall 1-RPP-01-30-26 | 7-DaHall 1-RPP-02-30-20 | 7-DaHall 1-RPP-01 | [branch#026] [A] W | 7-DaHall 1-RPP-02 | [branch#020] [A] W | 1.253
[7 empty] | 0 | 5-DaHall 1-PDU-19-50-25-DaHall 1-PDU-20-50-2 | 5-DaHall 1-PDU-19-50-2 | 5-DaHall 1-PDU-20-50-2 | 5-DaHall 1-PDU-19 | [branch#002] [A] W | 5-DaHall 1-PDU-20 | 0295 [branch#02] [A] W | #N/A | 6-DaHall 1-PDU-09-30-116-DaHall 1-PDU-10-30-11 | 6-DaHall 1-PDU-09-30-11 | 6-DaHall 1-PDU-10-30-11 | 6-DaHall 1-PDU-09 | [branch#011] [A] W | 6-DaHall 1-PDU-10 | [branch#011] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-21-50-25-DaHall 1-PDU-22-50-2 | 5-DaHall 1-PDU-21-50-2 | 5-DaHall 1-PDU-22-50-2 | 5-DaHall 1-PDU-21 | [branch#002] [A] W | 5-DaHall 1-PDU-22 | 0295 [branch#02] [A] W | #N/A | 6-DaHall 1-PDU-09-30-136-DaHall 1-PDU-10-30-13 | 6-DaHall 1-PDU-09-30-13 | 6-DaHall 1-PDU-10-30-13 | 6-DaHall 1-PDU-09 | [branch#013] [A] W | 6-DaHall 1-PDU-10 | [branch#013] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-19-50-135-DaHall 1-PDU-20-50-13 | 5-DaHall 1-PDU-19-50-13 | 5-DaHall 1-PDU-20-50-13 | 5-DaHall 1-PDU-19 | [branch#013] [A] W | 5-DaHall 1-PDU-20 | 1835 [branch#13] [A] W | #N/A | 6-DaHall 1-PDU-09-30-156-DaHall 1-PDU-10-30-15 | 6-DaHall 1-PDU-09-30-15 | 6-DaHall 1-PDU-10-30-15 | 6-DaHall 1-PDU-09 | [branch#015] [A] W | 6-DaHall 1-PDU-10 | [branch#015] [A] W | 0 | 7-DaHall 1-A-1-35-517-DaHall 1-B-1-35-51 | 7-DaHall 1-A-1-35-51 | 7-DaHall 1-B-1-35-51 | 7-DaHall 1-A-1-35 | [branch#051] [A] W | 7-DaHall 1-B-1-35 | [branch#051] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-21-50-135-DaHall 1-PDU-22-50-13 | 5-DaHall 1-PDU-21-50-13 | 5-DaHall 1-PDU-22-50-13 | 5-DaHall 1-PDU-21 | [branch#013] [A] W | 5-DaHall 1-PDU-22 | 1835 [branch#13] [A] W | #N/A | 6-DaHall 1-PDU-09-30-176-DaHall 1-PDU-10-30-17 | 6-DaHall 1-PDU-09-30-17 | 6-DaHall 1-PDU-10-30-17 | 6-DaHall 1-PDU-09 | [branch#017] [A] W | 6-DaHall 1-PDU-10 | [branch#017] [A] W | 0 | [7 empty] | 0
4-DaHall 1-PDU-04-100-74-DaHall 1-PDU-03-100-7 | 4-DaHall 1-PDU-04-100-7 | 4-DaHall 1-PDU-03-100-7 | 4-DaHall 1-PDU-04 | [branch#007] [A] W | 4-DaHall 1-PDU-03 | [branch#007] [A] W | 10.939 | 5-DaHall 1-PDU-19-50-115-DaHall 1-PDU-20-50-11 | 5-DaHall 1-PDU-19-50-11 | 5-DaHall 1-PDU-20-50-11 | 5-DaHall 1-PDU-19 | [branch#011] [A] W | 5-DaHall 1-PDU-20 | 1555 [branch#11] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-RPP-01--367-DaHall 1-RPP-02-30-30 | 7-DaHall 1-RPP-01--36 | 7-DaHall 1-RPP-02-30-30 | 7-DaHall 1-RPP-01 | [branch#036] [A] W | 7-DaHall 1-RPP-02 | [branch#030] [A] W | 1.31
[7 empty] | 0 | 5-DaHall 1-PDU-21-50-115-DaHall 1-PDU-22-50-11 | 5-DaHall 1-PDU-21-50-11 | 5-DaHall 1-PDU-22-50-11 | 5-DaHall 1-PDU-21 | [branch#011] [A] W | 5-DaHall 1-PDU-22 | 1555 [branch#11] [A] W | #N/A | 6-DaHall 1-PDU-09-30-26-DaHall 1-PDU-10-30-2 | 6-DaHall 1-PDU-09-30-2 | 6-DaHall 1-PDU-10-30-2 | 6-DaHall 1-PDU-09 | [branch#002] [A] W | 6-DaHall 1-PDU-10 | [branch#002] [A] W | 0 | 7-DaHall 1-RPP-01-30-147-DaHall 1-RPP-02-20-27 | 7-DaHall 1-RPP-01-30-14 | 7-DaHall 1-RPP-02-20-27 | 7-DaHall 1-RPP-01 | [branch#014] [A] W | 7-DaHall 1-RPP-02 | [branch#027] [A] W | 2.816
[7 empty] | 0 | 5-DaHall 1-PDU-19-50-95-DaHall 1-PDU-20-50-9 | 5-DaHall 1-PDU-19-50-9 | 5-DaHall 1-PDU-20-50-9 | 5-DaHall 1-PDU-19 | [branch#009] [A] W | 5-DaHall 1-PDU-20 | 1275 [branch#09] [A] W | #N/A | 6-DaHall 1-PDU-09-30-46-DaHall 1-PDU-10-30-4 | 6-DaHall 1-PDU-09-30-4 | 6-DaHall 1-PDU-10-30-4 | 6-DaHall 1-PDU-09 | [branch#004] [A] W | 6-DaHall 1-PDU-10 | [branch#004] [A] W | 0 | 7-DaHall 1-RPP-02-20-25 |  | 7-DaHall 1-RPP-02-20-25 |  |  | 7-DaHall 1-RPP-02 | [branch#025] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-21-50-95-DaHall 1-PDU-22-50-9 | 5-DaHall 1-PDU-21-50-9 | 5-DaHall 1-PDU-22-50-9 | 5-DaHall 1-PDU-21 | [branch#009] [A] W | 5-DaHall 1-PDU-22 | 1275 [branch#09] [A] W | #N/A | 6-DaHall 1-PDU-09-30-66-DaHall 1-PDU-10-30-6 | 6-DaHall 1-PDU-09-30-6 | 6-DaHall 1-PDU-10-30-6 | 6-DaHall 1-PDU-09 | [branch#006] [A] W | 6-DaHall 1-PDU-10 | [branch#006] [A] W | 0 | 7-DaHall 1-RPP-02-20-23 |  | 7-DaHall 1-RPP-02-20-23 |  |  | 7-DaHall 1-RPP-02 | [branch#023] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-19-50-75-DaHall 1-PDU-20-50-7 | 5-DaHall 1-PDU-19-50-7 | 5-DaHall 1-PDU-20-50-7 | 5-DaHall 1-PDU-19 | [branch#007] [A] W | 5-DaHall 1-PDU-20 | 0995 [branch#07] [A] W | #N/A | 6-DaHall 1-PDU-09-30-86-DaHall 1-PDU-10-30-8 | 6-DaHall 1-PDU-09-30-8 | 6-DaHall 1-PDU-10-30-8 | 6-DaHall 1-PDU-09 | [branch#008] [A] W | 6-DaHall 1-PDU-10 | [branch#008] [A] W | 0 | 7-DaHall 1-RPP-02-20-21 |  | 7-DaHall 1-RPP-02-20-21 |  |  | 7-DaHall 1-RPP-02 | [branch#021] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-21-50-75-DaHall 1-PDU-22-50-7 | 5-DaHall 1-PDU-21-50-7 | 5-DaHall 1-PDU-22-50-7 | 5-DaHall 1-PDU-21 | [branch#007] [A] W | 5-DaHall 1-PDU-22 | 0995 [branch#07] [A] W | #N/A | 6-DaHall 1-PDU-09-30-106-DaHall 1-PDU-10-30-10 | 6-DaHall 1-PDU-09-30-10 | 6-DaHall 1-PDU-10-30-10 | 6-DaHall 1-PDU-09 | [branch#010] [A] W | 6-DaHall 1-PDU-10 | [branch#010] [A] W | 0 | 7-DaHall 1-RPP-01-30-4 | 7-DaHall 1-RPP-01-30-4 |  | 7-DaHall 1-RPP-01 | [branch#004] [A] W |  |  | 0
[7 empty] | 0 | 5-DaHall 1-PDU-19-50-235-DaHall 1-PDU-20-50-23 | 5-DaHall 1-PDU-19-50-23 | 5-DaHall 1-PDU-20-50-23 | 5-DaHall 1-PDU-19 | [branch#023] [A] W | 5-DaHall 1-PDU-20 | 3235 [branch#23] [A] W | #N/A | 6-DaHall 1-PDU-09-30-126-DaHall 1-PDU-10-30-12 | 6-DaHall 1-PDU-09-30-12 | 6-DaHall 1-PDU-10-30-12 | 6-DaHall 1-PDU-09 | [branch#012] [A] W | 6-DaHall 1-PDU-10 | [branch#012] [A] W | 0 | 7-DaHall 1-RPP-01-30-6 | 7-DaHall 1-RPP-01-30-6 |  | 7-DaHall 1-RPP-01 | [branch#006] [A] W |  |  | 0
[7 empty] | 0 | 5-DaHall 1-PDU-21-50-235-DaHall 1-PDU-22-50-23 | 5-DaHall 1-PDU-21-50-23 | 5-DaHall 1-PDU-22-50-23 | 5-DaHall 1-PDU-21 | [branch#023] [A] W | 5-DaHall 1-PDU-22 | 3235 [branch#23] [A] W | #N/A | 6-DaHall 1-PDU-09-30-146-DaHall 1-PDU-10-30-14 | 6-DaHall 1-PDU-09-30-14 | 6-DaHall 1-PDU-10-30-14 | 6-DaHall 1-PDU-09 | [branch#014] [A] W | 6-DaHall 1-PDU-10 | [branch#014] [A] W | 0 | 7-DaHall 1-RPP-02-20-19 |  | 7-DaHall 1-RPP-02-20-19 |  |  | 7-DaHall 1-RPP-02 | [branch#019] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-19-50-55-DaHall 1-PDU-20-50-5 | 5-DaHall 1-PDU-19-50-5 | 5-DaHall 1-PDU-20-50-5 | 5-DaHall 1-PDU-19 | [branch#005] [A] W | 5-DaHall 1-PDU-20 | 0715 [branch#05] [A] W | #N/A | 6-DaHall 1-PDU-09-30-166-DaHall 1-PDU-10-30-16 | 6-DaHall 1-PDU-09-30-16 | 6-DaHall 1-PDU-10-30-16 | 6-DaHall 1-PDU-09 | [branch#016] [A] W | 6-DaHall 1-PDU-10 | [branch#016] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-21-50-55-DaHall 1-PDU-22-50-5 | 5-DaHall 1-PDU-21-50-5 | 5-DaHall 1-PDU-22-50-5 | 5-DaHall 1-PDU-21 | [branch#005] [A] W | 5-DaHall 1-PDU-22 | 0715 [branch#05] [A] W | #N/A | 6-DaHall 1-PDU-09-30-186-DaHall 1-PDU-10-30-18 | 6-DaHall 1-PDU-09-30-18 | 6-DaHall 1-PDU-10-30-18 | 6-DaHall 1-PDU-09 | [branch#018] [A] W | 6-DaHall 1-PDU-10 | [branch#018] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-19-50-35-DaHall 1-PDU-20-50-3 | 5-DaHall 1-PDU-19-50-3 | 5-DaHall 1-PDU-20-50-3 | 5-DaHall 1-PDU-19 | [branch#003] [A] W | 5-DaHall 1-PDU-20 | 0435 [branch#03] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-RPP-01-20-11 | 7-DaHall 1-RPP-01-20-11 |  | 7-DaHall 1-RPP-01 | [branch#011] [A] W |  |  | 0
[7 empty] | 0 | 5-DaHall 1-PDU-21-50-35-DaHall 1-PDU-22-50-3 | 5-DaHall 1-PDU-21-50-3 | 5-DaHall 1-PDU-22-50-3 | 5-DaHall 1-PDU-21 | [branch#003] [A] W | 5-DaHall 1-PDU-22 | 0435 [branch#03] [A] W | #N/A | 6-DaHall 1-PDU-09-30-206-DaHall 1-PDU-10-30-20 | 6-DaHall 1-PDU-09-30-20 | 6-DaHall 1-PDU-10-30-20 | 6-DaHall 1-PDU-09 | [branch#020] [A] W | 6-DaHall 1-PDU-10 | [branch#020] [A] W | 0 | 7-DaHall 1-RPP-01-30-387-DaHall 1-RPP-02-30-32 | 7-DaHall 1-RPP-01-30-38 | 7-DaHall 1-RPP-02-30-32 | 7-DaHall 1-RPP-01 | [branch#038] [A] W | 7-DaHall 1-RPP-02 | [branch#032] [A] W | 1.231
4-DaHall 1-PDU-04-100-64-DaHall 1-PDU-03-100-6 | 4-DaHall 1-PDU-04-100-6 | 4-DaHall 1-PDU-03-100-6 | 4-DaHall 1-PDU-04 | [branch#006] [A] W | 4-DaHall 1-PDU-03 | [branch#006] [A] W | 5.368 | 5-DaHall 1-PDU-19-50-15-DaHall 1-PDU-20-50-1 | 5-DaHall 1-PDU-19-50-1 | 5-DaHall 1-PDU-20-50-1 | 5-DaHall 1-PDU-19 | [branch#001] [A] W | 5-DaHall 1-PDU-20 | 0155 [branch#01] [A] W | #N/A | 6-DaHall 1-PDU-09-30-226-DaHall 1-PDU-10-30-22 | 6-DaHall 1-PDU-09-30-22 | 6-DaHall 1-PDU-10-30-22 | 6-DaHall 1-PDU-09 | [branch#022] [A] W | 6-DaHall 1-PDU-10 | [branch#022] [A] W | 0 | 7-DaHall 1-RPP-01-30-347-DaHall 1-RPP-02-30-28 | 7-DaHall 1-RPP-01-30-34 | 7-DaHall 1-RPP-02-30-28 | 7-DaHall 1-RPP-01 | [branch#034] [A] W | 7-DaHall 1-RPP-02 | [branch#028] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-21-50-15-DaHall 1-PDU-22-50-1 | 5-DaHall 1-PDU-21-50-1 | 5-DaHall 1-PDU-22-50-1 | 5-DaHall 1-PDU-21 | [branch#001] [A] W | 5-DaHall 1-PDU-22 | 0155 [branch#01] [A] W | #N/A | 6-DaHall 1-PDU-09-30-246-DaHall 1-PDU-10-30-48 | 6-DaHall 1-PDU-09-30-24 | 6-DaHall 1-PDU-10-30-48 | 6-DaHall 1-PDU-09 | [branch#024] [A] W | 6-DaHall 1-PDU-10 | [branch#048] [A] W | 0 | 7-DaHall 1-PDU-01-30-67-DaHall 1-PDU-02-30-6 | 7-DaHall 1-PDU-01-30-6 | 7-DaHall 1-PDU-02-30-6 | 7-DaHall 1-PDU-01 | [branch#006] [A] W | 7-DaHall 1-PDU-02 | [branch#006] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-25-DaHall 1-PDU-06-30-2 | 5-DaHall 1-PDU-05-30-2 | 5-DaHall 1-PDU-06-30-2 | 5-DaHall 1-PDU-05 | [branch#002] [A] W | 5-DaHall 1-PDU-06 | [branch#002] [A] W | 0 | 6-DaHall 1-PDU-09-30-266-DaHall 1-PDU-10-30-26 | 6-DaHall 1-PDU-09-30-26 | 6-DaHall 1-PDU-10-30-26 | 6-DaHall 1-PDU-09 | [branch#026] [A] W | 6-DaHall 1-PDU-10 | [branch#026] [A] W | 0 | 7-DaHall 1-PDU-01-30-547-DaHall 1-PDU-02-30-53 | 7-DaHall 1-PDU-01-30-54 | 7-DaHall 1-PDU-02-30-53 | 7-DaHall 1-PDU-01 | [branch#054] [A] W | 7-DaHall 1-PDU-02 | [branch#053] [A] W | 0.115
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-45-DaHall 1-PDU-06-30-4 | 5-DaHall 1-PDU-05-30-4 | 5-DaHall 1-PDU-06-30-4 | 5-DaHall 1-PDU-05 | [branch#004] [A] W | 5-DaHall 1-PDU-06 | [branch#004] [A] W | 0 | 6-DaHall 1-PDU-09-30-286-DaHall 1-PDU-10-30-28 | 6-DaHall 1-PDU-09-30-28 | 6-DaHall 1-PDU-10-30-28 | 6-DaHall 1-PDU-09 | [branch#028] [A] W | 6-DaHall 1-PDU-10 | [branch#028] [A] W | 0 | 7-DaHall 1-RPP-03-50-27-DaHall 1-RPP-04-50-2 | 7-DaHall 1-RPP-03-50-2 | 7-DaHall 1-RPP-04-50-2 | 7-DaHall 1-RPP-03 | [branch#002] [A] W | 7-DaHall 1-RPP-04 | [branch#002] [A] W | 0.64
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-65-DaHall 1-PDU-06-30-6 | 5-DaHall 1-PDU-05-30-6 | 5-DaHall 1-PDU-06-30-6 | 5-DaHall 1-PDU-05 | [branch#006] [A] W | 5-DaHall 1-PDU-06 | [branch#006] [A] W | 0 | 6-DaHall 1-PDU-09-30-306-DaHall 1-PDU-10-30-30 | 6-DaHall 1-PDU-09-30-30 | 6-DaHall 1-PDU-10-30-30 | 6-DaHall 1-PDU-09 | [branch#030] [A] W | 6-DaHall 1-PDU-10 | [branch#030] [A] W | 0 | 7-DaHall 1-RPP-02-30-14 |  | 7-DaHall 1-RPP-02-30-14 |  |  | 7-DaHall 1-RPP-02 | [branch#014] [A] W | 3.312
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-85-DaHall 1-PDU-06-30-8 | 5-DaHall 1-PDU-05-30-8 | 5-DaHall 1-PDU-06-30-8 | 5-DaHall 1-PDU-05 | [branch#008] [A] W | 5-DaHall 1-PDU-06 | [branch#008] [A] W | 0 | 6-DaHall 1-PDU-09-30-326-DaHall 1-PDU-10-30-32 | 6-DaHall 1-PDU-09-30-32 | 6-DaHall 1-PDU-10-30-32 | 6-DaHall 1-PDU-09 | [branch#032] [A] W | 6-DaHall 1-PDU-10 | [branch#032] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-105-DaHall 1-PDU-06-30-10 | 5-DaHall 1-PDU-05-30-10 | 5-DaHall 1-PDU-06-30-10 | 5-DaHall 1-PDU-05 | [branch#010] [A] W | 5-DaHall 1-PDU-06 | [branch#010] [A] W | 0 | 6-DaHall 1-PDU-09-30-346-DaHall 1-PDU-10-30-34 | 6-DaHall 1-PDU-09-30-34 | 6-DaHall 1-PDU-10-30-34 | 6-DaHall 1-PDU-09 | [branch#034] [A] W | 6-DaHall 1-PDU-10 | [branch#034] [A] W | 0 | 7-DaHall 1-PDU-01-30-47-DaHall 1-PDU-02-30-4 | 7-DaHall 1-PDU-01-30-4 | 7-DaHall 1-PDU-02-30-4 | 7-DaHall 1-PDU-01 | [branch#004] [A] W | 7-DaHall 1-PDU-02 | [branch#004] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-125-DaHall 1-PDU-06-30-12 | 5-DaHall 1-PDU-05-30-12 | 5-DaHall 1-PDU-06-30-12 | 5-DaHall 1-PDU-05 | [branch#012] [A] W | 5-DaHall 1-PDU-06 | [branch#012] [A] W | 0 | 6-DaHall 1-PDU-09-30-366-DaHall 1-PDU-10-30-36 | 6-DaHall 1-PDU-09-30-36 | 6-DaHall 1-PDU-10-30-36 | 6-DaHall 1-PDU-09 | [branch#036] [A] W | 6-DaHall 1-PDU-10 | [branch#036] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-145-DaHall 1-PDU-06-30-16 | 5-DaHall 1-PDU-05-30-14 | 5-DaHall 1-PDU-06-30-16 | 5-DaHall 1-PDU-05 | [branch#014] [A] W | 5-DaHall 1-PDU-06 | [branch#016] [A] W | 0 | 6-DaHall 1-PDU-01-30-176-DaHall 1-PDU-02-30-17 | 6-DaHall 1-PDU-01-30-17 | 6-DaHall 1-PDU-02-30-17 | 6-DaHall 1-PDU-01 | [branch#017] [A] W | 6-DaHall 1-PDU-02 | [branch#017] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-165-DaHall 1-PDU-06-30-18 | 5-DaHall 1-PDU-05-30-16 | 5-DaHall 1-PDU-06-30-18 | 5-DaHall 1-PDU-05 | [branch#016] [A] W | 5-DaHall 1-PDU-06 | [branch#018] [A] W | 0 | 6-DaHall 1-PDU-01-30-156-DaHall 1-PDU-02-30-15 | 6-DaHall 1-PDU-01-30-15 | 6-DaHall 1-PDU-02-30-15 | 6-DaHall 1-PDU-01 | [branch#015] [A] W | 6-DaHall 1-PDU-02 | [branch#015] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-01-30-136-DaHall 1-PDU-02-30-13 | 6-DaHall 1-PDU-01-30-13 | 6-DaHall 1-PDU-02-30-13 | 6-DaHall 1-PDU-01 | [branch#013] [A] W | 6-DaHall 1-PDU-02 | [branch#013] [A] W | 0 | 7-DaHall 1-RPP-01-20-237-DaHall 1-RPP-02-30-12 | 7-DaHall 1-RPP-01-20-23 | 7-DaHall 1-RPP-02-30-12 | 7-DaHall 1-RPP-01 | [branch#023] [A] W | 7-DaHall 1-RPP-02 | [branch#012] [A] W | 1.288
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-01-30-116-DaHall 1-PDU-02-30-11 | 6-DaHall 1-PDU-01-30-11 | 6-DaHall 1-PDU-02-30-11 | 6-DaHall 1-PDU-01 | [branch#011] [A] W | 6-DaHall 1-PDU-02 | [branch#011] [A] W | 0 | 7-DaHall 1-RPP-01-20-377-DaHall 1-RPP-02-30-8 | 7-DaHall 1-RPP-01-20-37 | 7-DaHall 1-RPP-02-30-8 | 7-DaHall 1-RPP-01 | [branch#037] [A] W | 7-DaHall 1-RPP-02 | [branch#008] [A] W | 2.801
4-DaHall 1-PDU-04-100-54-DaHall 1-PDU-03-100-5 | 4-DaHall 1-PDU-04-100-5 | 4-DaHall 1-PDU-03-100-5 | 4-DaHall 1-PDU-04 | [branch#005] [A] W | 4-DaHall 1-PDU-03 | [branch#005] [A] W | 3.509 | 5-DaHall 1-PDU-05-30-185-DaHall 1-PDU-06-30-20 | 5-DaHall 1-PDU-05-30-18 | 5-DaHall 1-PDU-06-30-20 | 5-DaHall 1-PDU-05 | [branch#018] [A] W | 5-DaHall 1-PDU-06 | [branch#020] [A] W | 0 | 6-DaHall 1-PDU-01-30-96-DaHall 1-PDU-02-30-9 | 6-DaHall 1-PDU-01-30-9 | 6-DaHall 1-PDU-02-30-9 | 6-DaHall 1-PDU-01 | [branch#009] [A] W | 6-DaHall 1-PDU-02 | [branch#009] [A] W | 0 | 7-DaHall 1-PDU-01-30-107-DaHall 1-PDU-02-30-10 | 7-DaHall 1-PDU-01-30-10 | 7-DaHall 1-PDU-02-30-10 | 7-DaHall 1-PDU-01 | [branch#010] [A] W | 7-DaHall 1-PDU-02 | [branch#010] [A] W | 1.49
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-205-DaHall 1-PDU-06-30-22 | 5-DaHall 1-PDU-05-30-20 | 5-DaHall 1-PDU-06-30-22 | 5-DaHall 1-PDU-05 | [branch#020] [A] W | 5-DaHall 1-PDU-06 | [branch#022] [A] W | 0 | 6-DaHall 1-PDU-01-30-76-DaHall 1-PDU-02-30-7 | 6-DaHall 1-PDU-01-30-7 | 6-DaHall 1-PDU-02-30-7 | 6-DaHall 1-PDU-01 | [branch#007] [A] W | 6-DaHall 1-PDU-02 | [branch#007] [A] W | 0 | 7-DaHall 1-PDU-01-30-427-DaHall 1-PDU-02-30-42 | 7-DaHall 1-PDU-01-30-42 | 7-DaHall 1-PDU-02-30-42 | 7-DaHall 1-PDU-01 | [branch#042] [A] W | 7-DaHall 1-PDU-02 | [branch#042] [A] W | 1.699
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-225-DaHall 1-PDU-06-30-24 | 5-DaHall 1-PDU-05-30-22 | 5-DaHall 1-PDU-06-30-24 | 5-DaHall 1-PDU-05 | [branch#022] [A] W | 5-DaHall 1-PDU-06 | [branch#024] [A] W | 0 | 6-DaHall 1-PDU--30-6-DaHall 1-PDU--30- | 6-DaHall 1-PDU--30- | 6-DaHall 1-PDU--30- | 6-DaHall 1-PDU--3 |  | 6-DaHall 1-PDU--3 |  | #N/A | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-245-DaHall 1-PDU-06-30-26 | 5-DaHall 1-PDU-05-30-24 | 5-DaHall 1-PDU-06-30-26 | 5-DaHall 1-PDU-05 | [branch#024] [A] W | 5-DaHall 1-PDU-06 | [branch#026] [A] W | 0 | 6-DaHall 1-PDU--30-6-DaHall 1-PDU--30- | 6-DaHall 1-PDU--30- | 6-DaHall 1-PDU--30- | 6-DaHall 1-PDU--3 |  | 6-DaHall 1-PDU--3 |  | #N/A | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-265-DaHall 1-PDU-06-30-28 | 5-DaHall 1-PDU-05-30-26 | 5-DaHall 1-PDU-06-30-28 | 5-DaHall 1-PDU-05 | [branch#026] [A] W | 5-DaHall 1-PDU-06 | [branch#028] [A] W | 0 | 6-DaHall 1-PDU--30-6-DaHall 1-PDU--30- | 6-DaHall 1-PDU--30- | 6-DaHall 1-PDU--30- | 6-DaHall 1-PDU--3 |  | 6-DaHall 1-PDU--3 |  | #N/A | 7-DaHall 1-PDU-01-30-347-DaHall 1-PDU-02-30-34 | 7-DaHall 1-PDU-01-30-34 | 7-DaHall 1-PDU-02-30-34 | 7-DaHall 1-PDU-01 | [branch#034] [A] W | 7-DaHall 1-PDU-02 | [branch#034] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-285-DaHall 1-PDU-06-30-30 | 5-DaHall 1-PDU-05-30-28 | 5-DaHall 1-PDU-06-30-30 | 5-DaHall 1-PDU-05 | [branch#028] [A] W | 5-DaHall 1-PDU-06 | [branch#030] [A] W | 0 | 6-DaHall 1-PDU-01-30-26-DaHall 1-PDU-02-30-2 | 6-DaHall 1-PDU-01-30-2 | 6-DaHall 1-PDU-02-30-2 | 6-DaHall 1-PDU-01 | [branch#002] [A] W | 6-DaHall 1-PDU-02 | [branch#002] [A] W | 0.582 | 7-DaHall 1-B-5-100-487-DaHall 1-B-1-100-41 | 7-DaHall 1-B-5-100-48 | 7-DaHall 1-B-1-100-41 | 7-DaHall 1-B-5-10 | [branch#048] [A] W | 7-DaHall 1-B-1-10 | [branch#041] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-305-DaHall 1-PDU-06-30-34 | 5-DaHall 1-PDU-05-30-30 | 5-DaHall 1-PDU-06-30-34 | 5-DaHall 1-PDU-05 | [branch#030] [A] W | 5-DaHall 1-PDU-06 | [branch#034] [A] W | 0 | 6-DaHall 1-PDU-01-30-366-DaHall 1-PDU-02-30-36 | 6-DaHall 1-PDU-01-30-36 | 6-DaHall 1-PDU-02-30-36 | 6-DaHall 1-PDU-01 | [branch#036] [A] W | 6-DaHall 1-PDU-02 | [branch#036] [A] W | 1.404 | 7-DaHall 1-PDU-01-30-157-DaHall 1-PDU-02-30-15 | 7-DaHall 1-PDU-01-30-15 | 7-DaHall 1-PDU-02-30-15 | 7-DaHall 1-PDU-01 | [branch#015] [A] W | 7-DaHall 1-PDU-02 | [branch#015] [A] W | 0.252
[7 empty] | 0 | 5-DaHall 1-PDU-05-30-325-DaHall 1-PDU-06-30-36 | 5-DaHall 1-PDU-05-30-32 | 5-DaHall 1-PDU-06-30-36 | 5-DaHall 1-PDU-05 | [branch#032] [A] W | 5-DaHall 1-PDU-06 | [branch#036] [A] W | 0 | 6-DaHall 1-PDU-01-30-386-DaHall 1-PDU-02-30-38 | 6-DaHall 1-PDU-01-30-38 | 6-DaHall 1-PDU-02-30-38 | 6-DaHall 1-PDU-01 | [branch#038] [A] W | 6-DaHall 1-PDU-02 | [branch#038] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-01-30-46-DaHall 1-PDU-02-30-4 | 6-DaHall 1-PDU-01-30-4 | 6-DaHall 1-PDU-02-30-4 | 6-DaHall 1-PDU-01 | [branch#004] [A] W | 6-DaHall 1-PDU-02 | [branch#004] [A] W | 3.406 | 7-DaHall 1-PDU-01-30-357-DaHall 1-PDU-02-30-35 | 7-DaHall 1-PDU-01-30-35 | 7-DaHall 1-PDU-02-30-35 | 7-DaHall 1-PDU-01 | [branch#035] [A] W | 7-DaHall 1-PDU-02 | [branch#035] [A] W | 3.003
[7 empty] | 0 | [7 empty] | 0 | 6-DaHall 1-PDU-01-30-66-DaHall 1-PDU-02-30-6 | 6-DaHall 1-PDU-01-30-6 | 6-DaHall 1-PDU-02-30-6 | 6-DaHall 1-PDU-01 | [branch#006] [A] W | 6-DaHall 1-PDU-02 | [branch#006] [A] W | 1.664 | 7-DaHall 1-PDU-01-30-337-DaHall 1-PDU-02-30-33 | 7-DaHall 1-PDU-01-30-33 | 7-DaHall 1-PDU-02-30-33 | 7-DaHall 1-PDU-01 | [branch#033] [A] W | 7-DaHall 1-PDU-02 | [branch#033] [A] W | 3.809
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-15-DaHall 1-PDU-02-30-1 | 5-DaHall 1-PDU-01-30-1 | 5-DaHall 1-PDU-02-30-1 | 5-DaHall 1-PDU-01 | [branch#001] [A] W | 5-DaHall 1-PDU-02 | [branch#001] [A] W | 0 | 6-DaHall 1-PDU-01-30-86-DaHall 1-PDU-02-30-8 | 6-DaHall 1-PDU-01-30-8 | 6-DaHall 1-PDU-02-30-8 | 6-DaHall 1-PDU-01 | [branch#008] [A] W | 6-DaHall 1-PDU-02 | [branch#008] [A] W | 1.662 | 7-DaHall 1-PDU-01-30-317-DaHall 1-PDU-02-30-31 | 7-DaHall 1-PDU-01-30-31 | 7-DaHall 1-PDU-02-30-31 | 7-DaHall 1-PDU-01 | [branch#031] [A] W | 7-DaHall 1-PDU-02 | [branch#031] [A] W | 1.671
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-35-DaHall 1-PDU-02-30-3 | 5-DaHall 1-PDU-01-30-3 | 5-DaHall 1-PDU-02-30-3 | 5-DaHall 1-PDU-01 | [branch#003] [A] W | 5-DaHall 1-PDU-02 | [branch#003] [A] W | 0 | 6-DaHall 1-PDU-01-30-106-DaHall 1-PDU-02-30-10 | 6-DaHall 1-PDU-01-30-10 | 6-DaHall 1-PDU-02-30-10 | 6-DaHall 1-PDU-01 | [branch#010] [A] W | 6-DaHall 1-PDU-02 | [branch#010] [A] W | 3.858 | 7-DaHall 1-PDU-01-30-397-DaHall 1-PDU-02-30-39 | 7-DaHall 1-PDU-01-30-39 | 7-DaHall 1-PDU-02-30-39 | 7-DaHall 1-PDU-01 | [branch#039] [A] W | 7-DaHall 1-PDU-02 | [branch#039] [A] W | 0.568
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-55-DaHall 1-PDU-02-30-5 | 5-DaHall 1-PDU-01-30-5 | 5-DaHall 1-PDU-02-30-5 | 5-DaHall 1-PDU-01 | [branch#005] [A] W | 5-DaHall 1-PDU-02 | [branch#005] [A] W | 0 | 6-DaHall 1-PDU-01-30-126-DaHall 1-PDU-02-30-12 | 6-DaHall 1-PDU-01-30-12 | 6-DaHall 1-PDU-02-30-12 | 6-DaHall 1-PDU-01 | [branch#012] [A] W | 6-DaHall 1-PDU-02 | [branch#012] [A] W | 4.132 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-75-DaHall 1-PDU-02-30-7 | 5-DaHall 1-PDU-01-30-7 | 5-DaHall 1-PDU-02-30-7 | 5-DaHall 1-PDU-01 | [branch#007] [A] W | 5-DaHall 1-PDU-02 | [branch#007] [A] W | 5.682 | 6-DaHall 1-PDU-01-30-146-DaHall 1-PDU-02-30-14 | 6-DaHall 1-PDU-01-30-14 | 6-DaHall 1-PDU-02-30-14 | 6-DaHall 1-PDU-01 | [branch#014] [A] W | 6-DaHall 1-PDU-02 | [branch#014] [A] W | 3.291 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-95-DaHall 1-PDU-02-30-9 | 5-DaHall 1-PDU-01-30-9 | 5-DaHall 1-PDU-02-30-9 | 5-DaHall 1-PDU-01 | [branch#009] [A] W | 5-DaHall 1-PDU-02 | [branch#009] [A] W | 2.874 | 6-DaHall 1-PDU-01-30-166-DaHall 1-PDU-02-30-16 | 6-DaHall 1-PDU-01-30-16 | 6-DaHall 1-PDU-02-30-16 | 6-DaHall 1-PDU-01 | [branch#016] [A] W | 6-DaHall 1-PDU-02 | [branch#016] [A] W | 2.613 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-115-DaHall 1-PDU-02-30-11 | 5-DaHall 1-PDU-01-30-11 | 5-DaHall 1-PDU-02-30-11 | 5-DaHall 1-PDU-01 | [branch#011] [A] W | 5-DaHall 1-PDU-02 | [branch#011] [A] W | 0.18 | 6-DaHall 1-PDU-11-30-196-DaHall 1-PDU-12-30-19 | 6-DaHall 1-PDU-11-30-19 | 6-DaHall 1-PDU-12-30-19 | 6-DaHall 1-PDU-11 | [branch#019] [A] W | 6-DaHall 1-PDU-12 | [branch#019] [A] W | 2.585 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-135-DaHall 1-PDU-02-30-13 | 5-DaHall 1-PDU-01-30-13 | 5-DaHall 1-PDU-02-30-13 | 5-DaHall 1-PDU-01 | [branch#013] [A] W | 5-DaHall 1-PDU-02 | [branch#013] [A] W | 0.604 | 6-DaHall 1-PDU-11-30-446-DaHall 1-PDU-12-30-44 | 6-DaHall 1-PDU-11-30-44 | 6-DaHall 1-PDU-12-30-44 | 6-DaHall 1-PDU-11 | [branch#044] [A] W | 6-DaHall 1-PDU-12 | [branch#044] [A] W | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-155-DaHall 1-PDU-02-30-15 | 5-DaHall 1-PDU-01-30-15 | 5-DaHall 1-PDU-02-30-15 | 5-DaHall 1-PDU-01 | [branch#015] [A] W | 5-DaHall 1-PDU-02 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-13-30-2 | 6-DaHall 1-PDU-13-30-2 |  | 6-DaHall 1-PDU-13 | [branch#002] [A] W |  |  | 0 | 7-DaHall 1-RPP-03-50-87-DaHall 1-RPP-04-50-8 | 7-DaHall 1-RPP-03-50-8 | 7-DaHall 1-RPP-04-50-8 | 7-DaHall 1-RPP-03 | [branch#008] [A] W | 7-DaHall 1-RPP-04 | [branch#008] [A] W | 0.87
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-175-DaHall 1-PDU-02-30-17 | 5-DaHall 1-PDU-01-30-17 | 5-DaHall 1-PDU-02-30-17 | 5-DaHall 1-PDU-01 | [branch#017] [A] W | 5-DaHall 1-PDU-02 | [branch#017] [A] W | 5.481 | 6-DaHall 1-PDU-13-30-4 | 6-DaHall 1-PDU-13-30-4 |  | 6-DaHall 1-PDU-13 | [branch#004] [A] W |  |  | 0 | 7-DaHall 1-RPP-03-50-67-DaHall 1-RPP-04-50-6 | 7-DaHall 1-RPP-03-50-6 | 7-DaHall 1-RPP-04-50-6 | 7-DaHall 1-RPP-03 | [branch#006] [A] W | 7-DaHall 1-RPP-04 | [branch#006] [A] W | 0.633
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-315-DaHall 1-PDU-02-30-31 | 5-DaHall 1-PDU-01-30-31 | 5-DaHall 1-PDU-02-30-31 | 5-DaHall 1-PDU-01 | [branch#031] [A] W | 5-DaHall 1-PDU-02 | [branch#031] [A] W | #N/A | 6-DaHall 1-PDU-14-30-2 |  | 6-DaHall 1-PDU-14-30-2 |  |  | 6-DaHall 1-PDU-14 | [branch#002] [A] W | 0 | 7-DaHall 1-RPP-03-50-107-DaHall 1-RPP-04-50-10 | 7-DaHall 1-RPP-03-50-10 | 7-DaHall 1-RPP-04-50-10 | 7-DaHall 1-RPP-03 | [branch#010] [A] W | 7-DaHall 1-RPP-04 | [branch#010] [A] W | 1.072
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-335-DaHall 1-PDU-02-30-33 | 5-DaHall 1-PDU-01-30-33 | 5-DaHall 1-PDU-02-30-33 | 5-DaHall 1-PDU-01 | [branch#033] [A] W | 5-DaHall 1-PDU-02 | [branch#033] [A] W | #N/A | 6-DaHall 1-PDU-14-30-4 |  | 6-DaHall 1-PDU-14-30-4 |  |  | 6-DaHall 1-PDU-14 | [branch#004] [A] W | 0 | 7-DaHall 1-RPP-03-50-97-DaHall 1-RPP-04-50-9 | 7-DaHall 1-RPP-03-50-9 | 7-DaHall 1-RPP-04-50-9 | 7-DaHall 1-RPP-03 | [branch#009] [A] W | 7-DaHall 1-RPP-04 | [branch#009] [A] W | 0.943
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-355-DaHall 1-PDU-02-30-35 | 5-DaHall 1-PDU-01-30-35 | 5-DaHall 1-PDU-02-30-35 | 5-DaHall 1-PDU-01 | [branch#035] [A] W | 5-DaHall 1-PDU-02 | [branch#035] [A] W | #N/A | 6-DaHall 1-PDU-14-30-20 |  | 6-DaHall 1-PDU-14-30-20 |  |  | 6-DaHall 1-PDU-14 | [branch#020] [A] W | 0 | 7-DaHall 1-B-5-35-427-DaHall 1-A-5-35-42 | 7-DaHall 1-B-5-35-42 | 7-DaHall 1-A-5-35-42 | 7-DaHall 1-B-5-35 | [branch#042] [A] W | 7-DaHall 1-A-5-35 | [branch#042] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-375-DaHall 1-PDU-02-30-37 | 5-DaHall 1-PDU-01-30-37 | 5-DaHall 1-PDU-02-30-37 | 5-DaHall 1-PDU-01 | [branch#037] [A] W | 5-DaHall 1-PDU-02 | [branch#037] [A] W | #N/A | 6-DaHall 1-PDU-13-30-40 | 6-DaHall 1-PDU-13-30-40 |  | 6-DaHall 1-PDU-13 | [branch#040] [A] W |  |  | 0 | 7-DaHall 1-B-5-35-437-DaHall 1-A-5-35-43 | 7-DaHall 1-B-5-35-43 | 7-DaHall 1-A-5-35-43 | 7-DaHall 1-B-5-35 | [branch#043] [A] W | 7-DaHall 1-A-5-35 | [branch#043] [A] W | #N/A
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-395-DaHall 1-PDU-02-30-39 | 5-DaHall 1-PDU-01-30-39 | 5-DaHall 1-PDU-02-30-39 | 5-DaHall 1-PDU-01 | [branch#039] [A] W | 5-DaHall 1-PDU-02 | [branch#039] [A] W | #N/A | 6-DaHall 1-PDU-01-30-50 | 6-DaHall 1-PDU-01-30-50 |  | 6-DaHall 1-PDU-01 | [branch#050] [A] W |  |  | 0 | 7-DaHall 1-RPP-03-50-77-DaHall 1-RPP-04-50-7 | 7-DaHall 1-RPP-03-50-7 | 7-DaHall 1-RPP-04-50-7 | 7-DaHall 1-RPP-03 | [branch#007] [A] W | 7-DaHall 1-RPP-04 | [branch#007] [A] W | 1.447
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-415-DaHall 1-PDU-02-30-41 | 5-DaHall 1-PDU-01-30-41 | 5-DaHall 1-PDU-02-30-41 | 5-DaHall 1-PDU-01 | [branch#041] [A] W | 5-DaHall 1-PDU-02 | [branch#041] [A] W | #N/A | 6-DaHall 1-PDU-01-30-46 | 6-DaHall 1-PDU-01-30-46 |  | 6-DaHall 1-PDU-01 | [branch#046] [A] W |  |  | 0.129 | 7-DaHall 1-RPP-03-50-57-DaHall 1-RPP-04-50-5 | 7-DaHall 1-RPP-03-50-5 | 7-DaHall 1-RPP-04-50-5 | 7-DaHall 1-RPP-03 | [branch#005] [A] W | 7-DaHall 1-RPP-04 | [branch#005] [A] W | 1.649
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-435-DaHall 1-PDU-02-30-43 | 5-DaHall 1-PDU-01-30-43 | 5-DaHall 1-PDU-02-30-43 | 5-DaHall 1-PDU-01 | [branch#043] [A] W | 5-DaHall 1-PDU-02 | [branch#043] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-RPP-03-50-37-DaHall 1-RPP-04-50-3 | 7-DaHall 1-RPP-03-50-3 | 7-DaHall 1-RPP-04-50-3 | 7-DaHall 1-RPP-03 | [branch#003] [A] W | 7-DaHall 1-RPP-04 | [branch#003] [A] W | 1.239
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-455-DaHall 1-PDU-02-30-45 | 5-DaHall 1-PDU-01-30-45 | 5-DaHall 1-PDU-02-30-45 | 5-DaHall 1-PDU-01 | [branch#045] [A] W | 5-DaHall 1-PDU-02 | [branch#045] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-RPP-03-50-17-DaHall 1-RPP-04-50-1 | 7-DaHall 1-RPP-03-50-1 | 7-DaHall 1-RPP-04-50-1 | 7-DaHall 1-RPP-03 | [branch#001] [A] W | 7-DaHall 1-RPP-04 | [branch#001] [A] W | 1.346
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-475-DaHall 1-PDU-02-30-47 | 5-DaHall 1-PDU-01-30-47 | 5-DaHall 1-PDU-02-30-47 | 5-DaHall 1-PDU-01 | [branch#047] [A] W | 5-DaHall 1-PDU-02 | [branch#047] [A] W | #N/A | [7 empty] | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-195-DaHall 1-PDU-02-30-19 | 5-DaHall 1-PDU-01-30-19 | 5-DaHall 1-PDU-02-30-19 | 5-DaHall 1-PDU-01 | [branch#019] [A] W | 5-DaHall 1-PDU-02 | [branch#019] [A] W | 5.171 | [7 empty] | 0 | [7 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-215-DaHall 1-PDU-02-30-21 | 5-DaHall 1-PDU-01-30-21 | 5-DaHall 1-PDU-02-30-21 | 5-DaHall 1-PDU-01 | [branch#021] [A] W | 5-DaHall 1-PDU-02 | [branch#021] [A] W | 4.986 | [7 empty] | 0 | 7-DaHall 1-PDU-02-30-49 |  | 7-DaHall 1-PDU-02-30-49 |  |  | 7-DaHall 1-PDU-02 | [branch#049] [A] W | 0.158
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-235-DaHall 1-PDU-02-30-23 | 5-DaHall 1-PDU-01-30-23 | 5-DaHall 1-PDU-02-30-23 | 5-DaHall 1-PDU-01 | [branch#023] [A] W | 5-DaHall 1-PDU-02 | [branch#023] [A] W | 0 | [7 empty] | 0 | 7-DaHall 1-PDU-02-30-51 |  | 7-DaHall 1-PDU-02-30-51 |  |  | 7-DaHall 1-PDU-02 | [branch#051] [A] W | 0.108
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-255-DaHall 1-PDU-02-30-25 | 5-DaHall 1-PDU-01-30-25 | 5-DaHall 1-PDU-02-30-25 | 5-DaHall 1-PDU-01 | [branch#025] [A] W | 5-DaHall 1-PDU-02 | [branch#025] [A] W | 0 | [7 empty] | 0 | 7-DaHall 1-PDU-03-225-2 | 7-DaHall 1-PDU-03-225-2 |  | 7-DaHall 1-PDU-03 | [branch#002] [A] W |  |  | 3.02
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-42 | 5-DaHall 1-PDU-01-30-42 |  | 5-DaHall 1-PDU-01 | [branch#042] [A] W |  |  | #N/A | [7 empty] | 0 | 7-DaHall 1-RPP-01-20-1 | 7-DaHall 1-RPP-01-20-1 |  | 7-DaHall 1-RPP-01 | [branch#001] [A] W |  |  | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-445-DaHall 1-PDU-02-30-44 | 5-DaHall 1-PDU-01-30-44 | 5-DaHall 1-PDU-02-30-44 | 5-DaHall 1-PDU-01 | [branch#044] [A] W | 5-DaHall 1-PDU-02 | [branch#044] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-RPP-01-30-2 | 7-DaHall 1-RPP-01-30-2 |  | 7-DaHall 1-RPP-01 | [branch#002] [A] W |  |  | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-45-DaHall 1-PDU-02-30-4 | 5-DaHall 1-PDU-01-30-4 | 5-DaHall 1-PDU-02-30-4 | 5-DaHall 1-PDU-01 | [branch#004] [A] W | 5-DaHall 1-PDU-02 | [branch#004] [A] W | 0 | [7 empty] | 0 | 7-DaHall 1-RPP-01-20-3 | 7-DaHall 1-RPP-01-20-3 |  | 7-DaHall 1-RPP-01 | [branch#003] [A] W |  |  | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-65-DaHall 1-PDU-02-30-6 | 5-DaHall 1-PDU-01-30-6 | 5-DaHall 1-PDU-02-30-6 | 5-DaHall 1-PDU-01 | [branch#006] [A] W | 5-DaHall 1-PDU-02 | [branch#006] [A] W | 5.531 | [7 empty] | 0 | 7-DaHall 1-RPP-01-20-5 | 7-DaHall 1-RPP-01-20-5 |  | 7-DaHall 1-RPP-01 | [branch#005] [A] W |  |  | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-10 | 5-DaHall 1-PDU-01-30-10 |  | 5-DaHall 1-PDU-01 | [branch#010] [A] W |  |  | 0 | [7 empty] | 0 | 7-DaHall 1-RPP-01-20-9 | 7-DaHall 1-RPP-01-20-9 |  | 7-DaHall 1-RPP-01 | [branch#009] [A] W |  |  | 0
[7 empty] | 0 | 5-DaHall 1-PDU-02-30-10 |  | 5-DaHall 1-PDU-02-30-10 |  |  | 5-DaHall 1-PDU-02 | [branch#010] [A] W | 1.347 | [7 empty] | 0 | 7-DaHall 1-RPP-01-20-13 | 7-DaHall 1-RPP-01-20-13 |  | 7-DaHall 1-RPP-01 | [branch#013] [A] W |  |  | 0
[7 empty] | 0 | [7 empty] | 0 | [7 empty] | 0 | 7-DaHall 1-RPP-01-20-15 | 7-DaHall 1-RPP-01-20-15 |  | 7-DaHall 1-RPP-01 | [branch#015] [A] W |  |  | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-505-DaHall 1-PDU-02-30-50 | 5-DaHall 1-PDU-01-30-50 | 5-DaHall 1-PDU-02-30-50 | 5-DaHall 1-PDU-01 | [branch#050] [A] W | 5-DaHall 1-PDU-02 | [branch#050] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-RPP-01-20-17 | 7-DaHall 1-RPP-01-20-17 |  | 7-DaHall 1-RPP-01 | [branch#017] [A] W |  |  | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-60-25-DaHall 1-PDU-02-60-2 | 5-DaHall 1-PDU-01-60-2 | 5-DaHall 1-PDU-02-60-2 | 5-DaHall 1-PDU-01 | [branch#002] [A] W | 5-DaHall 1-PDU-02 | [branch#002] [A] W | 0 | [7 empty] | 0 | 7-DaHall 1-RPP-01-20-27 | 7-DaHall 1-RPP-01-20-27 |  | 7-DaHall 1-RPP-01 | [branch#027] [A] W |  |  | 0.619
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-485-DaHall 1-PDU-02-30-48 | 5-DaHall 1-PDU-01-30-48 | 5-DaHall 1-PDU-02-30-48 | 5-DaHall 1-PDU-01 | [branch#048] [A] W | 5-DaHall 1-PDU-02 | [branch#048] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-RPP-01-30-28 | 7-DaHall 1-RPP-01-30-28 |  | 7-DaHall 1-RPP-01 | [branch#028] [A] W |  |  | 0.554
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-215-DaHall 1-PDU-04-30-21 | 5-DaHall 1-PDU-03-30-21 | 5-DaHall 1-PDU-04-30-21 | 5-DaHall 1-PDU-03 | [branch#021] [A] W | 5-DaHall 1-PDU-04 | [branch#021] [A] W | 0.748 | [7 empty] | 0 | 7-DaHall 1-RPP-01-20-29 | 7-DaHall 1-RPP-01-20-29 |  | 7-DaHall 1-RPP-01 | [branch#029] [A] W |  |  | 0.713
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-235-DaHall 1-PDU-04-30-23 | 5-DaHall 1-PDU-03-30-23 | 5-DaHall 1-PDU-04-30-23 | 5-DaHall 1-PDU-03 | [branch#023] [A] W | 5-DaHall 1-PDU-04 | [branch#023] [A] W | 1.418 | [7 empty] | 0 | 7-DaHall 1-RPP-01-30-30 | 7-DaHall 1-RPP-01-30-30 |  | 7-DaHall 1-RPP-01 | [branch#030] [A] W |  |  | 0.972
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-255-DaHall 1-PDU-04-30-25 | 5-DaHall 1-PDU-03-30-25 | 5-DaHall 1-PDU-04-30-25 | 5-DaHall 1-PDU-03 | [branch#025] [A] W | 5-DaHall 1-PDU-04 | [branch#025] [A] W | 1.945 | [7 empty] | 0 | 7-DaHall 1-RPP-01-20-31 | 7-DaHall 1-RPP-01-20-31 |  | 7-DaHall 1-RPP-01 | [branch#031] [A] W |  |  | 0.929
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-275-DaHall 1-PDU-04-30-27 | 5-DaHall 1-PDU-03-30-27 | 5-DaHall 1-PDU-04-30-27 | 5-DaHall 1-PDU-03 | [branch#027] [A] W | 5-DaHall 1-PDU-04 | [branch#027] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-PDU-02-30-50 |  | 7-DaHall 1-PDU-02-30-50 |  |  | 7-DaHall 1-PDU-02 | [branch#050] [A] W | 0.532
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-295-DaHall 1-PDU-04-30-29 | 5-DaHall 1-PDU-03-30-29 | 5-DaHall 1-PDU-04-30-29 | 5-DaHall 1-PDU-03 | [branch#029] [A] W | 5-DaHall 1-PDU-04 | [branch#029] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-PDU-02-30-52 |  | 7-DaHall 1-PDU-02-30-52 |  |  | 7-DaHall 1-PDU-02 | [branch#052] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-315-DaHall 1-PDU-04-30-31 | 5-DaHall 1-PDU-03-30-31 | 5-DaHall 1-PDU-04-30-31 | 5-DaHall 1-PDU-03 | [branch#031] [A] W | 5-DaHall 1-PDU-04 | [branch#031] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-PDU-02-30-54 |  | 7-DaHall 1-PDU-02-30-54 |  |  | 7-DaHall 1-PDU-02 | [branch#054] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-335-DaHall 1-PDU-04-30-33 | 5-DaHall 1-PDU-03-30-33 | 5-DaHall 1-PDU-04-30-33 | 5-DaHall 1-PDU-03 | [branch#033] [A] W | 5-DaHall 1-PDU-04 | [branch#033] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-PDU-01-30-52 | 7-DaHall 1-PDU-01-30-52 |  | 7-DaHall 1-PDU-01 | [branch#052] [A] W |  |  | 0
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-15-DaHall 1-PDU-04-30-1 | 5-DaHall 1-PDU-03-30-1 | 5-DaHall 1-PDU-04-30-1 | 5-DaHall 1-PDU-03 | [branch#001] [A] W | 5-DaHall 1-PDU-04 | [branch#001] [A] W | 0 | [7 empty] | 0 | 7-DaHall 1-RPP-02-20-1 |  | 7-DaHall 1-RPP-02-20-1 |  |  | 7-DaHall 1-RPP-02 | [branch#001] [A] W | 0.216
[7 empty] | 0 | 5-DaHall 1-PDU-03-30-35-DaHall 1-PDU-04-30-3 | 5-DaHall 1-PDU-03-30-3 | 5-DaHall 1-PDU-04-30-3 | 5-DaHall 1-PDU-03 | [branch#003] [A] W | 5-DaHall 1-PDU-04 | [branch#003] [A] W | 0 | [7 empty] | 0 | 7-DaHall 1-RPP-02-30-2 |  | 7-DaHall 1-RPP-02-30-2 |  |  | 7-DaHall 1-RPP-02 | [branch#002] [A] W | 3.573
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-125-DaHall 1-PDU-02-30-12 | 5-DaHall 1-PDU-01-30-12 | 5-DaHall 1-PDU-02-30-12 | 5-DaHall 1-PDU-01 | [branch#012] [A] W | 5-DaHall 1-PDU-02 | [branch#012] [A] W | 0.604 | [7 empty] | 0 | 7-DaHall 1-RPP-02-20-3 |  | 7-DaHall 1-RPP-02-20-3 |  |  | 7-DaHall 1-RPP-02 | [branch#003] [A] W | 0.129
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-145-DaHall 1-PDU-02-30-14 | 5-DaHall 1-PDU-01-30-14 | 5-DaHall 1-PDU-02-30-14 | 5-DaHall 1-PDU-01 | [branch#014] [A] W | 5-DaHall 1-PDU-02 | [branch#014] [A] W | 0 | [7 empty] | 0 | 7-DaHall 1-RPP-02-30-6 |  | 7-DaHall 1-RPP-02-30-6 |  |  | 7-DaHall 1-RPP-02 | [branch#006] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-165-DaHall 1-PDU-02-30-16 | 5-DaHall 1-PDU-01-30-16 | 5-DaHall 1-PDU-02-30-16 | 5-DaHall 1-PDU-01 | [branch#016] [A] W | 5-DaHall 1-PDU-02 | [branch#016] [A] W | 0 | [7 empty] | 0 | 7-DaHall 1-RPP-02-20-7 |  | 7-DaHall 1-RPP-02-20-7 |  |  | 7-DaHall 1-RPP-02 | [branch#007] [A] W | 0.223
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-185-DaHall 1-PDU-02-30-18 | 5-DaHall 1-PDU-01-30-18 | 5-DaHall 1-PDU-02-30-18 | 5-DaHall 1-PDU-01 | [branch#018] [A] W | 5-DaHall 1-PDU-02 | [branch#018] [A] W | 5.186 | [7 empty] | 0 | 7-DaHall 1-RPP-02-20-11 |  | 7-DaHall 1-RPP-02-20-11 |  |  | 7-DaHall 1-RPP-02 | [branch#011] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-205-DaHall 1-PDU-02-30-20 | 5-DaHall 1-PDU-01-30-20 | 5-DaHall 1-PDU-02-30-20 | 5-DaHall 1-PDU-01 | [branch#020] [A] W | 5-DaHall 1-PDU-02 | [branch#020] [A] W | 5.076 | [7 empty] | 0 | 7-DaHall 1-RPP-02-30-22 |  | 7-DaHall 1-RPP-02-30-22 |  |  | 7-DaHall 1-RPP-02 | [branch#022] [A] W | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-225-DaHall 1-PDU-02-30-22 | 5-DaHall 1-PDU-01-30-22 | 5-DaHall 1-PDU-02-30-22 | 5-DaHall 1-PDU-01 | [branch#022] [A] W | 5-DaHall 1-PDU-02 | [branch#022] [A] W | 0 | [7 empty] | 0 | 7-DaHall 1-RPP-02-30-24 |  | 7-DaHall 1-RPP-02-30-24 |  |  | 7-DaHall 1-RPP-02 | [branch#024] [A] W | 0.626
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-245-DaHall 1-PDU-02-30-24 | 5-DaHall 1-PDU-01-30-24 | 5-DaHall 1-PDU-02-30-24 | 5-DaHall 1-PDU-01 | [branch#024] [A] W | 5-DaHall 1-PDU-02 | [branch#024] [A] W | 0 | [7 empty] | 0 | 7-DaHall 1-RPP-02-20-35 |  | 7-DaHall 1-RPP-02-20-35 |  |  | 7-DaHall 1-RPP-02 | [branch#035] [A] W | 0.468
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-265-DaHall 1-PDU-02-30-26 | 5-DaHall 1-PDU-01-30-26 | 5-DaHall 1-PDU-02-30-26 | 5-DaHall 1-PDU-01 | [branch#026] [A] W | 5-DaHall 1-PDU-02 | [branch#026] [A] W | 0 | [7 empty] | 0 | 7-DaHall 1-RPP-02-20-37 |  | 7-DaHall 1-RPP-02-20-37 |  |  | 7-DaHall 1-RPP-02 | [branch#037] [A] W | 1.015
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-285-DaHall 1-PDU-02-30-28 | 5-DaHall 1-PDU-01-30-28 | 5-DaHall 1-PDU-02-30-28 | 5-DaHall 1-PDU-01 | [branch#028] [A] W | 5-DaHall 1-PDU-02 | [branch#028] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-RPP-02-20-38 |  | 7-DaHall 1-RPP-02-20-38 |  |  | 7-DaHall 1-RPP-02 | [branch#038] [A] W | 1.087
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-305-DaHall 1-PDU-02-30-30 | 5-DaHall 1-PDU-01-30-30 | 5-DaHall 1-PDU-02-30-30 | 5-DaHall 1-PDU-01 | [branch#030] [A] W | 5-DaHall 1-PDU-02 | [branch#030] [A] W | #N/A | [7 empty] | 0 | 7-DaHall 1-RPP-02-20-39 |  | 7-DaHall 1-RPP-02-20-39 |  |  | 7-DaHall 1-RPP-02 | [branch#039] [A] W | 3.033
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-325-DaHall 1-PDU-02-30-32 | 5-DaHall 1-PDU-01-30-32 | 5-DaHall 1-PDU-02-30-32 | 5-DaHall 1-PDU-01 | [branch#032] [A] W | 5-DaHall 1-PDU-02 | [branch#032] [A] W | #N/A | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-345-DaHall 1-PDU-02-30-34 | 5-DaHall 1-PDU-01-30-34 | 5-DaHall 1-PDU-02-30-34 | 5-DaHall 1-PDU-01 | [branch#034] [A] W | 5-DaHall 1-PDU-02 | [branch#034] [A] W | #N/A | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-365-DaHall 1-PDU-02-30-36 | 5-DaHall 1-PDU-01-30-36 | 5-DaHall 1-PDU-02-30-36 | 5-DaHall 1-PDU-01 | [branch#036] [A] W | 5-DaHall 1-PDU-02 | [branch#036] [A] W | #N/A | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-385-DaHall 1-PDU-02-30-38 | 5-DaHall 1-PDU-01-30-38 | 5-DaHall 1-PDU-02-30-38 | 5-DaHall 1-PDU-01 | [branch#038] [A] W | 5-DaHall 1-PDU-02 | [branch#038] [A] W | #N/A | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-02-30-40 |  | 5-DaHall 1-PDU-02-30-40 |  |  | 5-DaHall 1-PDU-02 | [branch#040] [A] W | #N/A | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-495-DaHall 1-PDU-02-30-49 | 5-DaHall 1-PDU-01-30-49 | 5-DaHall 1-PDU-02-30-49 | 5-DaHall 1-PDU-01 | [branch#049] [A] W | 5-DaHall 1-PDU-02 | [branch#049] [A] W | #N/A | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-25-DaHall 1-PDU-02-30-2 | 5-DaHall 1-PDU-01-30-2 | 5-DaHall 1-PDU-02-30-2 | 5-DaHall 1-PDU-01 | [branch#002] [A] W | 5-DaHall 1-PDU-02 | [branch#002] [A] W | 0 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-85-DaHall 1-PDU-02-30-8 | 5-DaHall 1-PDU-01-30-8 | 5-DaHall 1-PDU-02-30-8 | 5-DaHall 1-PDU-01 | [branch#008] [A] W | 5-DaHall 1-PDU-02 | [branch#008] [A] W | 5.87 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-275-DaHall 1-PDU-02-30-27 | 5-DaHall 1-PDU-01-30-27 | 5-DaHall 1-PDU-02-30-27 | 5-DaHall 1-PDU-01 | [branch#027] [A] W | 5-DaHall 1-PDU-02 | [branch#027] [A] W | #N/A | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-01-30-295-DaHall 1-PDU-02-30-29 | 5-DaHall 1-PDU-01-30-29 | 5-DaHall 1-PDU-02-30-29 | 5-DaHall 1-PDU-01 | [branch#029] [A] W | 5-DaHall 1-PDU-02 | [branch#029] [A] W | #N/A | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-14-20-32 |  | 5-DaHall 1-PDU-14-20-32 |  |  | 5-DaHall 1-PDU-14 | [branch#032] [A] W | 0 | [15 empty] | 0
[7 empty] | 0 | [7 empty] | 0 | [15 empty] | 0
[7 empty] | 0 | [7 empty] | 0 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-15-30-135-DaHall 1-PDU-16-30-13 | 5-DaHall 1-PDU-15-30-13 | 5-DaHall 1-PDU-16-30-13 | 5-DaHall 1-PDU-15 | [branch#013] [A] W | 5-DaHall 1-PDU-16 | [branch#013] [A] W | 0.503 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-15-20-23 | 5-DaHall 1-PDU-15-20-23 |  | 5-DaHall 1-PDU-15 | [branch#023] [A] W |  |  | 0.497 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-15-20-29 | 5-DaHall 1-PDU-15-20-29 |  | 5-DaHall 1-PDU-15 | [branch#029] [A] W |  |  | 0.036 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-16-20-15 |  | 5-DaHall 1-PDU-16-20-15 |  |  | 5-DaHall 1-PDU-16 | [branch#015] [A] W | 0.734 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-16-20-17 |  | 5-DaHall 1-PDU-16-20-17 |  |  | 5-DaHall 1-PDU-16 | [branch#017] [A] W | 0.741 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-16-20-19 |  | 5-DaHall 1-PDU-16-20-19 |  |  | 5-DaHall 1-PDU-16 | [branch#019] [A] W | 0 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-16-20-23 |  | 5-DaHall 1-PDU-16-20-23 |  |  | 5-DaHall 1-PDU-16 | [branch#023] [A] W | 0 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-16-20-25 |  | 5-DaHall 1-PDU-16-20-25 |  |  | 5-DaHall 1-PDU-16 | [branch#025] [A] W | 0.093 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-16-20-27 |  | 5-DaHall 1-PDU-16-20-27 |  |  | 5-DaHall 1-PDU-16 | [branch#027] [A] W | 0.324 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-16-20-29 |  | 5-DaHall 1-PDU-16-20-29 |  |  | 5-DaHall 1-PDU-16 | [branch#029] [A] W | 0.482 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-16-20-24 |  | 5-DaHall 1-PDU-16-20-24 |  |  | 5-DaHall 1-PDU-16 | [branch#024] [A] W | 0.439 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-16-20-30 |  | 5-DaHall 1-PDU-16-20-30 |  |  | 5-DaHall 1-PDU-16 | [branch#030] [A] W | 0.064 | [15 empty] | 0
[7 empty] | 0 | [7 empty] | 0 | [15 empty] | 0
[7 empty] | 0 | [7 empty] | 0 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-15-50-1 | 5-DaHall 1-PDU-15-50-1 |  | 5-DaHall 1-PDU-15 | [branch#001] [A] W |  |  | 3.012 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-15-50-2 | 5-DaHall 1-PDU-15-50-2 |  | 5-DaHall 1-PDU-15 | [branch#002] [A] W |  |  | 1.779 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-16-50-1 |  | 5-DaHall 1-PDU-16-50-1 |  |  | 5-DaHall 1-PDU-16 | [branch#001] [A] W | 2.273 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-16-50-2 |  | 5-DaHall 1-PDU-16-50-2 |  |  | 5-DaHall 1-PDU-16 | [branch#002] [A] W | 1.751 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-16-20-21 |  | 5-DaHall 1-PDU-16-20-21 |  |  | 5-DaHall 1-PDU-16 | [branch#021] [A] W | 0.064 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-16-50-20 |  | 5-DaHall 1-PDU-16-50-20 |  |  | 5-DaHall 1-PDU-16 | [branch#020] [A] W | 0.122 | [15 empty] | 0
[7 empty] | 0 | 5-DaHall 1-PDU-16-50-22 |  | 5-DaHall 1-PDU-16-50-22 |  |  | 5-DaHall 1-PDU-16 | [branch#022] [A] W | 0.115 | [15 empty] | 0

## 7층~4층_고객 총사용량(삭제X)
SEL1층별 고객사 랙 전력데이터 현황 | [5 empty] | 고객사명 입력↓ | 총 계약용량 | 총 시간당 전력량 | 피크값 | 평균값 | 총 남은 전력량 | 전력초과여부
[6 empty] | 미디어꾼 | 0 | 0 | 0 | 0 | 0 | 미사용 랙
층수 : | 4 |  |  |  |  | ↑ 위 셀에 고객사명을 입력하면 4~7층 고객사랙의 총 전력값이 나옵니다.
위치 | 계약용량 | 시간당 전력량 | 남은 전력량 | 전력초과여부 | 피크값 | 평균값
7층 | 0 | 0 | 0 | 미사용 랙 | 0
6층 | 0 | 0 | 0 | 미사용 랙 | 0
5층 | 0 | 0 | 0 | 미사용 랙 | 0
4층 | 0 | 0 | 0 | 미사용 랙 | 0
Entry1
Entry2
Entry3
Entry4
Entry5
Entry6
Entry7
Entry8
Entry9
Entry10

## Power_Summary
Customer | Description | Power |  | Sample | Customer | Description | Power
Total PowerUsage for Customer: 미디어꾼 | PowerUsage Total | 0 | 총사용량 |  | Total Power Usage for Customer XXYY | Power Usage Total | 70.32 kW
| Subscribed Power | 0 | 계약용량 |  |  | Subscribed Power | 81.00 KVA
| Average Power | 0 | 평균전력 |  |  | Remaining Power | 10.68 kW | 남은용량 | (고객사한테 보여줄필요 X)
| Peak Power | 0 | 최대전력 |  | Attachments
Attachments: PowerReport

## 각층분기별_유효전력최대(전월)
Date : 2024-01-01 ~ 2024-01-31 | [11 empty] | =INDEX('각층분기별_유효전력최대(전월)'!C4:C2020,MATCH(1,("4-DaHall 1-PDU-04"='각층분기별_유효전력최대(전월)'!A4:A2020)*("[branch#006] [A] W"='각층분기별_유효전력최대(전월)'!B4:B2020),0))+INDEX('각층분기별_유효전력최대(전월)'!C4:C2020,MATCH(1,("4-DaHall 1-PDU-03"='각층분기별_유효전력최대(전월)'!A4:A2020)*("[branch#006] [A] W"='각층분기별_유효전력최대(전월)'!B4:B2020),0))
4F | 포인트명 | kW(전월최대유효전력) | 5F | 포인트명 | kW(전월최대유효전력) | 6F | 포인트명 | kW(전월최대유효전력) | 7F | 포인트명 | kW(전월최대유효전력)
4-CRACRm-CEP-01 | 0155 [branch#01] [A] W | -0.017 | 5-CRACRm-CEP-01 | 0155 [branch#01] [A] W | 0 | 6-DaHall 1-CEP-05 | [branch#001] [A] W | 36.262 | 7-DaHall 1-PDU-01 | [branch#001] [A] W | 0
4-CRACRm-CEP-01 | 0295 [branch#02] [A] W | 34.645 | 5-CRACRm-CEP-01 | 0295 [branch#02] [A] W | 34.084 | 6-DaHall 1-CEP-05 | [branch#002] [A] W | 13.043 | 7-DaHall 1-PDU-01 | [branch#002] [A] W | 0
4-CRACRm-CEP-01 | 0435 [branch#03] [A] W | 0 | 5-CRACRm-CEP-01 | 0435 [branch#03] [A] W | 0 | 6-DaHall 1-CEP-05 | [branch#003] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#003] [A] W | 0.605
4-CRACRm-CEP-01 | 0575 [branch#04] [A] W | 34.248 | 5-CRACRm-CEP-01 | 0575 [branch#04] [A] W | 34.087 | 6-DaHall 1-CEP-05 | [branch#004] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#004] [A] W | 0
4-CRACRm-CEP-02 | 0155 [branch#01] [A] W | 35.582 | 5-CRACRm-CEP-02 | 0155 [branch#01] [A] W | 34.246 | 6-DaHall 1-CEP-05 | [branch#005] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#005] [A] W | 1.044
4-CRACRm-CEP-02 | 0295 [branch#02] [A] W | 0 | 5-CRACRm-CEP-02 | 0295 [branch#02] [A] W | 0 | 6-DaHall 1-CEP-05 | [branch#006] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#006] [A] W | 0
4-CRACRm-CEP-02 | 0435 [branch#03] [A] W | 35.393 | 5-CRACRm-CEP-02 | 0435 [branch#03] [A] W | 40.545 | 6-DaHall 1-CEP-05 | [branch#007] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#007] [A] W | 1.333
4-CRACRm-CEP-02 | 0575 [branch#04] [A] W | -0.089 | 5-CRACRm-CEP-02 | 0575 [branch#04] [A] W | 0 | 6-DaHall 1-CEP-05 | [branch#008] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#008] [A] W | 0.475
4-DaHall 1-CEP-05 | 0155 [branch#01] [A] W | 0 | 5-DaHall 1-CEP-05 | [branch#001] [A] W | 7.682 | 6-DaHall 1-CEP-05 | [branch#009] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#009] [A] W | 1.613
4-DaHall 1-CEP-05 | 0295 [branch#02] [A] W | 0 | 5-DaHall 1-CEP-05 | [branch#002] [A] W | 7.581 | 6-DaHall 1-CEP-05 | [branch#010] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#010] [A] W | 0.561
4-DaHall 1-CEP-05 | 0435 [branch#03] [A] W | 0 | 5-DaHall 1-CEP-05 | [branch#003] [A] W | 12.812 | 6-DaHall 1-CEP-05 | [branch#011] [A] W | 33.868 | 7-DaHall 1-PDU-01 | [branch#011] [A] W | 1.39
4-DaHall 1-CEP-05 | 0575 [branch#04] [A] W | 0 | 5-DaHall 1-CEP-05 | [branch#004] [A] W | 13.153 | 6-DaHall 1-CEP-05 | [branch#012] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#012] [A] W | 0
4-DaHall 1-CEP-05 | 0715 [branch#05] [A] W | 0 | 5-DaHall 1-CEP-05 | [branch#005] [A] W | 13.564 | 6-DaHall 1-CEP-05 | [branch#013] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#013] [A] W | 1.427
4-DaHall 1-CEP-05 | 0855 [branch#06] [A] W | 0 | 5-DaHall 1-CEP-05 | [branch#006] [A] W | 13.4 | 6-DaHall 1-CEP-05 | [branch#014] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#014] [A] W | 0.965
4-DaHall 1-CEP-05 | 0995 [branch#07] [A] W | 0 | 5-DaHall 1-CEP-05 | [branch#007] [A] W | 13.603 | 6-DaHall 1-CEP-05 | [branch#015] [A] W | 2.852 | 7-DaHall 1-PDU-01 | [branch#015] [A] W | 0.108
4-DaHall 1-CEP-05 | 1135 [branch#08] [A] W | 0 | 5-DaHall 1-CEP-05 | [branch#008] [A] W | 13.54 | 6-DaHall 1-CEP-05 | [branch#016] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#016] [A] W | 0.489
4-DaHall 1-CEP-05 | 1275 [branch#09] [A] W | 0 | 5-DaHall 1-CEP-05 | [branch#009] [A] W | 13.632 | 6-DaHall 1-CEP-05 | [branch#017] [A] W | 3.673 | 7-DaHall 1-PDU-01 | [branch#017] [A] W | 0.67
4-DaHall 1-CEP-05 | 1415 [branch#10] [A] W | 0 | 5-DaHall 1-CEP-05 | [branch#010] [A] W | 12.296 | 6-DaHall 1-PDU-01 | [branch#001] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#018] [A] W | 0.453
4-DaHall 1-CEP-05 | 1555 [branch#11] [A] W | 0 | 5-DaHall 1-CEP-05 | [branch#011] [A] W | 14.761 | 6-DaHall 1-PDU-01 | [branch#002] [A] W | 0.338 | 7-DaHall 1-PDU-01 | [branch#019] [A] W | 0.871
4-DaHall 1-CEP-05 | 1695 [branch#12] [A] W | 0 | 5-DaHall 1-CEP-05 | [branch#012] [A] W | 13.848 | 6-DaHall 1-PDU-01 | [branch#003] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#020] [A] W | 0.403
4-DaHall 1-PDU-01 | [branch#001] [A] W | 0.696 | 5-DaHall 1-CEP-05 | [branch#013] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#004] [A] W | 1.944 | 7-DaHall 1-PDU-01 | [branch#021] [A] W | 0.863
4-DaHall 1-PDU-01 | [branch#002] [A] W | 8.036 | 5-DaHall 1-CEP-05 | [branch#014] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#005] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#022] [A] W | 0.374
4-DaHall 1-PDU-01 | [branch#003] [A] W | 7.358 | 5-DaHall 1-CEP-05 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#006] [A] W | 0.605 | 7-DaHall 1-PDU-01 | [branch#023] [A] W | 0.431
4-DaHall 1-PDU-01 | [branch#004] [A] W | 7.79 | 5-DaHall 1-CEP-05 | [branch#016] [A] W | 3.248 | 6-DaHall 1-PDU-01 | [branch#007] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#024] [A] W | 0.669
4-DaHall 1-PDU-01 | [branch#005] [A] W | 9.268 | 5-DaHall 1-CEP-05 | [branch#017] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#008] [A] W | 1.029 | 7-DaHall 1-PDU-01 | [branch#025] [A] W | 0.36
4-DaHall 1-PDU-01 | [branch#006] [A] W | 5.131 | 5-DaHall 1-CEP-05 | [branch#018] [A] W | 3.161 | 6-DaHall 1-PDU-01 | [branch#009] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#026] [A] W | 0.713
4-DaHall 1-PDU-01 | [branch#007] [A] W | 2.577 | 5-DaHall 1-CEP-06 | 0155 [branch#01] [A] W | 12.269 | 6-DaHall 1-PDU-01 | [branch#010] [A] W | 1.951 | 7-DaHall 1-PDU-01 | [branch#027] [A] W | 0.77
4-DaHall 1-PDU-01 | [branch#008] [A] W | 0 | 5-DaHall 1-CEP-06 | 0295 [branch#02] [A] W | 12.545 | 6-DaHall 1-PDU-01 | [branch#011] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#028] [A] W | 1.153
4-DaHall 1-PDU-01 | [branch#009] [A] W | 0 | 5-DaHall 1-CEP-06 | 0435 [branch#03] [A] W | 12.121 | 6-DaHall 1-PDU-01 | [branch#012] [A] W | 1.828 | 7-DaHall 1-PDU-01 | [branch#029] [A] W | 0.079
4-DaHall 1-PDU-02 | [branch#001] [A] W | 0.391 | 5-DaHall 1-CEP-06 | 0575 [branch#04] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#013] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#030] [A] W | 0.064
4-DaHall 1-PDU-02 | [branch#002] [A] W | 7.453 | 5-DaHall 1-PDU-01 | [branch#001] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#014] [A] W | 1.426 | 7-DaHall 1-PDU-01 | [branch#031] [A] W | 0.944
4-DaHall 1-PDU-02 | [branch#003] [A] W | 6.959 | 5-DaHall 1-PDU-01 | [branch#055] [A] W | 0.057 | 6-DaHall 1-PDU-01 | [branch#015] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#032] [A] W | 0.417
4-DaHall 1-PDU-02 | [branch#004] [A] W | 7.489 | 5-DaHall 1-PDU-01 | [branch#002] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#016] [A] W | 1.454 | 7-DaHall 1-PDU-01 | [branch#033] [A] W | 1.936
4-DaHall 1-PDU-02 | [branch#005] [A] W | 9.201 | 5-DaHall 1-PDU-01 | [branch#056] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#017] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#034] [A] W | 0
4-DaHall 1-PDU-02 | [branch#006] [A] W | 2.554 | 5-DaHall 1-PDU-01 | [branch#003] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#018] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#035] [A] W | 1.541
4-DaHall 1-PDU-02 | [branch#007] [A] W | 6.278 | 5-DaHall 1-PDU-01 | [branch#057] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#019] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#036] [A] W | 0
4-DaHall 1-PDU-02 | [branch#008] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#004] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#020] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#037] [A] W | 0
4-DaHall 1-PDU-02 | [branch#009] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#058] [A] W | 0.453 | 6-DaHall 1-PDU-01 | [branch#021] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#038] [A] W | 0.59
4-DaHall 1-PDU-03 | [branch#001] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#005] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#022] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#039] [A] W | 0.201
4-DaHall 1-PDU-03 | [branch#002] [A] W | 7.223 | 5-DaHall 1-PDU-01 | [branch#059] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#023] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#040] [A] W | 0.727
4-DaHall 1-PDU-03 | [branch#003] [A] W | 6.125 | 5-DaHall 1-PDU-01 | [branch#006] [A] W | 3.011 | 6-DaHall 1-PDU-01 | [branch#024] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#041] [A] W | 0.18
4-DaHall 1-PDU-03 | [branch#004] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#060] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#025] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#042] [A] W | 0.698
4-DaHall 1-PDU-03 | [branch#005] [A] W | 1.414 | 5-DaHall 1-PDU-01 | [branch#007] [A] W | 2.643 | 6-DaHall 1-PDU-01 | [branch#026] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#043] [A] W | 0
4-DaHall 1-PDU-03 | [branch#006] [A] W | 2.149 | 5-DaHall 1-PDU-01 | [branch#061] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#027] [A] W | 0.425 | 7-DaHall 1-PDU-01 | [branch#044] [A] W | 1.743
4-DaHall 1-PDU-03 | [branch#007] [A] W | 6.423 | 5-DaHall 1-PDU-01 | [branch#008] [A] W | 3.219 | 6-DaHall 1-PDU-01 | [branch#028] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#045] [A] W | 0
4-DaHall 1-PDU-03 | [branch#008] [A] W | 3.94 | 5-DaHall 1-PDU-01 | [branch#062] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#029] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#046] [A] W | 0
4-DaHall 1-PDU-03 | [branch#009] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#009] [A] W | 1.419 | 6-DaHall 1-PDU-01 | [branch#030] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#047] [A] W | 0
4-DaHall 1-PDU-04 | [branch#001] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#063] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#031] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#048] [A] W | 0.641
4-DaHall 1-PDU-04 | [branch#002] [A] W | 9.013 | 5-DaHall 1-PDU-01 | [branch#010] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#032] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#049] [A] W | 0
4-DaHall 1-PDU-04 | [branch#003] [A] W | 6.397 | 5-DaHall 1-PDU-01 | [branch#064] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#033] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#050] [A] W | 0
4-DaHall 1-PDU-04 | [branch#004] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#011] [A] W | 0.18 | 6-DaHall 1-PDU-01 | [branch#034] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#051] [A] W | 0
4-DaHall 1-PDU-04 | [branch#005] [A] W | 2.095 | 5-DaHall 1-PDU-01 | [branch#065] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#035] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#052] [A] W | 0
4-DaHall 1-PDU-04 | [branch#006] [A] W | 3.219 | 5-DaHall 1-PDU-01 | [branch#012] [A] W | 0.28 | 6-DaHall 1-PDU-01 | [branch#036] [A] W | 0.633 | 7-DaHall 1-PDU-01 | [branch#053] [A] W | 0
4-DaHall 1-PDU-04 | [branch#007] [A] W | 4.516 | 5-DaHall 1-PDU-01 | [branch#066] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#037] [A] W | 0 | 7-DaHall 1-PDU-01 | [branch#054] [A] W | 0.072
4-DaHall 1-PDU-04 | [branch#008] [A] W | 4.75 | 5-DaHall 1-PDU-01 | [branch#013] [A] W | 0.324 | 6-DaHall 1-PDU-01 | [branch#038] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#001] [A] W | 0
4-DaHall 1-PDU-04 | [branch#009] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#067] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#039] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#002] [A] W | 0
4-DaHall 1-PDU-05 | [branch#001] [A] W | 2.064 | 5-DaHall 1-PDU-01 | [branch#014] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#040] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#003] [A] W | 0.943
4-DaHall 1-PDU-05 | [branch#002] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#068] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#041] [A] W | 0.208 | 7-DaHall 1-PDU-02 | [branch#004] [A] W | 0
4-DaHall 1-PDU-05 | [branch#003] [A] W | 1.556 | 5-DaHall 1-PDU-01 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#042] [A] W | 0.957 | 7-DaHall 1-PDU-02 | [branch#005] [A] W | 0
4-DaHall 1-PDU-05 | [branch#004] [A] W | 1.506 | 5-DaHall 1-PDU-01 | [branch#069] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#043] [A] W | 1.188 | 7-DaHall 1-PDU-02 | [branch#006] [A] W | 0
4-DaHall 1-PDU-05 | [branch#005] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#016] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#044] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#007] [A] W | 1.361
4-DaHall 1-PDU-05 | [branch#006] [A] W | 2.57 | 5-DaHall 1-PDU-01 | [branch#070] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#045] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#008] [A] W | 0
4-DaHall 1-PDU-05 | [branch#007] [A] W | 1.546 | 5-DaHall 1-PDU-01 | [branch#017] [A] W | 2.6 | 6-DaHall 1-PDU-01 | [branch#046] [A] W | 0.129 | 7-DaHall 1-PDU-02 | [branch#009] [A] W | 1.318
4-DaHall 1-PDU-05 | [branch#008] [A] W | 2.818 | 5-DaHall 1-PDU-01 | [branch#071] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#047] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#010] [A] W | 0.929
4-DaHall 1-PDU-05 | [branch#009] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#018] [A] W | 2.384 | 6-DaHall 1-PDU-01 | [branch#048] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#011] [A] W | 1.109
4-DaHall 1-PDU-05 | [branch#010] [A] W | 6.843 | 5-DaHall 1-PDU-01 | [branch#072] [A] W | 0 | 6-DaHall 1-PDU-01 | [branch#049] [A] W | 2.196 | 7-DaHall 1-PDU-02 | [branch#012] [A] W | 0
4-DaHall 1-PDU-05 | [branch#011] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#019] [A] W | 2.823 | 6-DaHall 1-PDU-01 | [branch#050] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#013] [A] W | 1.109
4-DaHall 1-PDU-05 | [branch#012] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#073] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#001] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#014] [A] W | 0.518
4-DaHall 1-PDU-06 | [branch#001] [A] W | 2.473 | 5-DaHall 1-PDU-01 | [branch#020] [A] W | 2.305 | 6-DaHall 1-PDU-02 | [branch#002] [A] W | 0.244 | 7-DaHall 1-PDU-02 | [branch#015] [A] W | 0.144
4-DaHall 1-PDU-06 | [branch#002] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#074] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#003] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#016] [A] W | 0.59
4-DaHall 1-PDU-06 | [branch#003] [A] W | 1.928 | 5-DaHall 1-PDU-01 | [branch#021] [A] W | 2.77 | 6-DaHall 1-PDU-02 | [branch#004] [A] W | 1.462 | 7-DaHall 1-PDU-02 | [branch#017] [A] W | 0.814
4-DaHall 1-PDU-06 | [branch#004] [A] W | 1.532 | 5-DaHall 1-PDU-01 | [branch#075] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#005] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#018] [A] W | 0.446
4-DaHall 1-PDU-06 | [branch#005] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#022] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#006] [A] W | 1.059 | 7-DaHall 1-PDU-02 | [branch#019] [A] W | 1.915
4-DaHall 1-PDU-06 | [branch#006] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#076] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#007] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#020] [A] W | 0.662
4-DaHall 1-PDU-06 | [branch#007] [A] W | 1.901 | 5-DaHall 1-PDU-01 | [branch#023] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#008] [A] W | 0.633 | 7-DaHall 1-PDU-02 | [branch#021] [A] W | 0.928
4-DaHall 1-PDU-06 | [branch#008] [A] W | 3.037 | 5-DaHall 1-PDU-01 | [branch#077] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#009] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#022] [A] W | 0.425
4-DaHall 1-PDU-06 | [branch#009] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#024] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#010] [A] W | 1.907 | 7-DaHall 1-PDU-02 | [branch#023] [A] W | 0.59
4-DaHall 1-PDU-06 | [branch#010] [A] W | 8.305 | 5-DaHall 1-PDU-01 | [branch#078] [A] W | 0.122 | 6-DaHall 1-PDU-02 | [branch#011] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#024] [A] W | 0.554
4-DaHall 1-PDU-06 | [branch#011] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#025] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#012] [A] W | 2.304 | 7-DaHall 1-PDU-02 | [branch#025] [A] W | 0.374
4-DaHall 1-PDU-06 | [branch#012] [A] W | 0 | 5-DaHall 1-PDU-01 | [branch#079] [A] W | 0.389 | 6-DaHall 1-PDU-02 | [branch#013] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#026] [A] W | 0.763
4-DaHall 1-PDU-07 | [branch#001] [A] W | 4.625 | 5-DaHall 1-PDU-01 | [branch#026] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#014] [A] W | 1.865 | 7-DaHall 1-PDU-02 | [branch#027] [A] W | 0.9
4-DaHall 1-PDU-07 | [branch#002] [A] W | 7.579 | 5-DaHall 1-PDU-01 | [branch#080] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#015] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#028] [A] W | 1.203
4-DaHall 1-PDU-07 | [branch#003] [A] W | 1.132 | 5-DaHall 1-PDU-02 | [branch#001] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#016] [A] W | 1.159 | 7-DaHall 1-PDU-02 | [branch#029] [A] W | 0.54
4-DaHall 1-PDU-07 | [branch#004] [A] W | 2.212 | 5-DaHall 1-PDU-02 | [branch#055] [A] W | 0.057 | 6-DaHall 1-PDU-02 | [branch#017] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#030] [A] W | 0.093
4-DaHall 1-PDU-07 | [branch#005] [A] W | 1.312 | 5-DaHall 1-PDU-02 | [branch#002] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#018] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#031] [A] W | 0.727
4-DaHall 1-PDU-07 | [branch#006] [A] W | 3.439 | 5-DaHall 1-PDU-02 | [branch#056] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#019] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#032] [A] W | 0.345
4-DaHall 1-PDU-07 | [branch#007] [A] W | 2.599 | 5-DaHall 1-PDU-02 | [branch#003] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#020] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#033] [A] W | 1.873
4-DaHall 1-PDU-07 | [branch#008] [A] W | 7.875 | 5-DaHall 1-PDU-02 | [branch#057] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#021] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#034] [A] W | 0
4-DaHall 1-PDU-07 | [branch#009] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#004] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#022] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#035] [A] W | 1.462
4-DaHall 1-PDU-07 | [branch#010] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#058] [A] W | 0.403 | 6-DaHall 1-PDU-02 | [branch#023] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#036] [A] W | 0
4-DaHall 1-PDU-07 | [branch#011] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#005] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#024] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#037] [A] W | 0.093
4-DaHall 1-PDU-07 | [branch#012] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#059] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#025] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#038] [A] W | 0.792
4-DaHall 1-PDU-08 | [branch#001] [A] W | 5.223 | 5-DaHall 1-PDU-02 | [branch#006] [A] W | 2.52 | 6-DaHall 1-PDU-02 | [branch#026] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#039] [A] W | 0.367
4-DaHall 1-PDU-08 | [branch#002] [A] W | 7.495 | 5-DaHall 1-PDU-02 | [branch#060] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#027] [A] W | 0.259 | 7-DaHall 1-PDU-02 | [branch#040] [A] W | 0.677
4-DaHall 1-PDU-08 | [branch#003] [A] W | 1.166 | 5-DaHall 1-PDU-02 | [branch#007] [A] W | 3.039 | 6-DaHall 1-PDU-02 | [branch#028] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#041] [A] W | 0
4-DaHall 1-PDU-08 | [branch#004] [A] W | 2.105 | 5-DaHall 1-PDU-02 | [branch#061] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#029] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#042] [A] W | 1.001
4-DaHall 1-PDU-08 | [branch#005] [A] W | 1.634 | 5-DaHall 1-PDU-02 | [branch#008] [A] W | 2.651 | 6-DaHall 1-PDU-02 | [branch#030] [A] W | 2.196 | 7-DaHall 1-PDU-02 | [branch#043] [A] W | 0
4-DaHall 1-PDU-08 | [branch#006] [A] W | 2.733 | 5-DaHall 1-PDU-02 | [branch#062] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#031] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#044] [A] W | 0.691
4-DaHall 1-PDU-08 | [branch#007] [A] W | 2.451 | 5-DaHall 1-PDU-02 | [branch#009] [A] W | 1.455 | 6-DaHall 1-PDU-02 | [branch#032] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#045] [A] W | 0
4-DaHall 1-PDU-08 | [branch#008] [A] W | 6.924 | 5-DaHall 1-PDU-02 | [branch#063] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#033] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#046] [A] W | 0
4-DaHall 1-PDU-08 | [branch#009] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#010] [A] W | 1.347 | 6-DaHall 1-PDU-02 | [branch#034] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#047] [A] W | 0
4-DaHall 1-PDU-08 | [branch#010] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#064] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#035] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#048] [A] W | 0.842
4-DaHall 1-PDU-08 | [branch#011] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#011] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#036] [A] W | 0.771 | 7-DaHall 1-PDU-02 | [branch#049] [A] W | 0.158
4-DaHall 1-PDU-08 | [branch#012] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#065] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#037] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#050] [A] W | 0.532
4-DaHall 1-PDU-09 | [branch#001] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#012] [A] W | 0.324 | 6-DaHall 1-PDU-02 | [branch#038] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#051] [A] W | 0.108
4-DaHall 1-PDU-09 | [branch#002] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#066] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#039] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#052] [A] W | 0
4-DaHall 1-PDU-09 | [branch#003] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#013] [A] W | 0.28 | 6-DaHall 1-PDU-02 | [branch#040] [A] W | 0 | 7-DaHall 1-PDU-02 | [branch#053] [A] W | 0.043
4-DaHall 1-PDU-10 | [branch#001] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#067] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#041] [A] W | 0.158 | 7-DaHall 1-PDU-02 | [branch#054] [A] W | 0
4-DaHall 1-PDU-10 | [branch#002] [A] W | 19.682 | 5-DaHall 1-PDU-02 | [branch#014] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#042] [A] W | 0.965 | 7-DaHall 1-PDU-03 | [branch#001] [A] W | 12.504
4-DaHall 1-PDU-10 | [branch#003] [A] W | 17.48 | 5-DaHall 1-PDU-02 | [branch#068] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#043] [A] W | 1.339 | 7-DaHall 1-PDU-03 | [branch#002] [A] W | 3.02
4-DaHall 1-PDU-11 | [branch#001] [A] W | 0.201 | 5-DaHall 1-PDU-02 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#044] [A] W | 0 | 7-DaHall 1-PDU-03 | [branch#003] [A] W | 4.01
4-DaHall 1-PDU-11 | [branch#002] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#069] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#045] [A] W | 0 | 7-DaHall 1-PDU-03 | [branch#004] [A] W | 0
4-DaHall 1-PDU-11 | [branch#003] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#016] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#046] [A] W | 0 | 7-DaHall 1-PDU-03 | [branch#005] [A] W | 0
4-DaHall 1-PDU-11 | [branch#004] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#070] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#047] [A] W | 0 | 7-DaHall 1-PDU-03 | [branch#006] [A] W | 32.356
4-DaHall 1-PDU-11 | [branch#005] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#017] [A] W | 2.881 | 6-DaHall 1-PDU-02 | [branch#048] [A] W | 0 | 7-DaHall 1-PDU-03 | [branch#007] [A] W | 0
4-DaHall 1-PDU-11 | [branch#006] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#071] [A] W | 0 | 6-DaHall 1-PDU-02 | [branch#049] [A] W | 0 | 7-DaHall 1-PDU-03 | [branch#008] [A] W | 0
4-DaHall 1-PDU-11 | [branch#007] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#018] [A] W | 2.802 | 6-DaHall 1-PDU-02 | [branch#050] [A] W | 0 | 7-DaHall 1-PDU-03 | [branch#009] [A] W | 0
4-DaHall 1-PDU-11 | [branch#008] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#072] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#001] [A] W | 1.692 | 7-DaHall 1-PDU-03 | [branch#010] [A] W | 0
4-DaHall 1-PDU-11 | [branch#009] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#019] [A] W | 2.348 | 6-DaHall 1-PDU-03 | [branch#002] [A] W | 0 | 7-DaHall 1-PDU-04 | [branch#001] [A] W | 28.323
4-DaHall 1-PDU-11 | [branch#010] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#073] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#003] [A] W | 1.491 | 7-DaHall 1-PDU-04 | [branch#002] [A] W | 17.931
4-DaHall 1-PDU-11 | [branch#011] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#020] [A] W | 2.771 | 6-DaHall 1-PDU-03 | [branch#004] [A] W | 0 | 7-DaHall 1-PDU-04 | [branch#003] [A] W | 0
4-DaHall 1-PDU-11 | [branch#012] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#074] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#005] [A] W | 0.194 | 7-DaHall 1-PDU-04 | [branch#004] [A] W | 4.577
4-DaHall 1-PDU-11 | [branch#013] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#021] [A] W | 2.216 | 6-DaHall 1-PDU-03 | [branch#006] [A] W | 0 | 7-DaHall 1-PDU-04 | [branch#005] [A] W | 0
4-DaHall 1-PDU-11 | [branch#014] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#075] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#007] [A] W | 0.892 | 7-DaHall 1-PDU-04 | [branch#006] [A] W | 0
4-DaHall 1-PDU-11 | [branch#015] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#022] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#008] [A] W | 0 | 7-DaHall 1-PDU-04 | [branch#007] [A] W | 0
4-DaHall 1-PDU-11 | [branch#016] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#076] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#009] [A] W | 0.763 | 7-DaHall 1-PDU-04 | [branch#008] [A] W | 0
4-DaHall 1-PDU-11 | [branch#017] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#023] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#010] [A] W | 0 | 7-DaHall 1-PDU-04 | [branch#009] [A] W | 0
4-DaHall 1-PDU-11 | [branch#018] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#077] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#011] [A] W | 0.951 | 7-DaHall 1-PDU-04 | [branch#010] [A] W | 0
4-DaHall 1-PDU-11 | [branch#019] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#078] [A] W | 0.129 | 6-DaHall 1-PDU-03 | [branch#012] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#001] [A] W | 0
4-DaHall 1-PDU-11 | [branch#020] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#024] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#013] [A] W | 1.505 | 7-DaHall 1-RPP-01 | [branch#002] [A] W | 0
4-DaHall 1-PDU-11 | [branch#021] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#079] [A] W | 0.266 | 6-DaHall 1-PDU-03 | [branch#014] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#003] [A] W | 0
4-DaHall 1-PDU-11 | [branch#022] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#025] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#015] [A] W | 0.878 | 7-DaHall 1-RPP-01 | [branch#004] [A] W | 0
4-DaHall 1-PDU-11 | [branch#023] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#080] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#016] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#005] [A] W | 0
4-DaHall 1-PDU-11 | [branch#024] [A] W | 0 | 5-DaHall 1-PDU-02 | [branch#026] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#017] [A] W | 0.425 | 7-DaHall 1-RPP-01 | [branch#006] [A] W | 0
4-DaHall 1-PDU-11 | [branch#025] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#001] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#018] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#007] [A] W | 0
4-DaHall 1-PDU-11 | [branch#026] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#055] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#019] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#008] [A] W | 0.475
4-DaHall 1-PDU-11 | [branch#027] [A] W | 0.028 | 5-DaHall 1-PDU-03 | [branch#002] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#020] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#009] [A] W | 0
4-DaHall 1-PDU-11 | [branch#028] [A] W | 0.028 | 5-DaHall 1-PDU-03 | [branch#056] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#021] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#010] [A] W | 0.338
4-DaHall 1-PDU-11 | [branch#029] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#003] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#022] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#011] [A] W | 0
4-DaHall 1-PDU-11 | [branch#030] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#057] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#023] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#012] [A] W | 1.102
4-DaHall 1-PDU-11 | [branch#031] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#004] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#024] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#013] [A] W | 0
4-DaHall 1-PDU-11 | [branch#032] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#058] [A] W | 0.144 | 6-DaHall 1-PDU-03 | [branch#025] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#014] [A] W | 1.505
4-DaHall 1-PDU-11 | [branch#033] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#005] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#026] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#015] [A] W | 0
4-DaHall 1-PDU-11 | [branch#034] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#059] [A] W | 0.374 | 6-DaHall 1-PDU-03 | [branch#027] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#016] [A] W | 0.324
4-DaHall 1-PDU-11 | [branch#035] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#006] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#028] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#017] [A] W | 0
4-DaHall 1-PDU-11 | [branch#036] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#060] [A] W | 0.972 | 6-DaHall 1-PDU-03 | [branch#029] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#018] [A] W | 0.41
4-DaHall 1-PDU-11 | [branch#037] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#007] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#030] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#019] [A] W | 0.165
4-DaHall 1-PDU-11 | [branch#038] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#061] [A] W | 0.425 | 6-DaHall 1-PDU-03 | [branch#031] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#020] [A] W | 0.324
4-DaHall 1-PDU-11 | [branch#039] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#008] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#032] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#021] [A] W | 0
4-DaHall 1-PDU-11 | [branch#040] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#062] [A] W | 0.079 | 6-DaHall 1-PDU-03 | [branch#033] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#022] [A] W | 0
4-DaHall 1-PDU-11 | [branch#041] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#009] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#034] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#023] [A] W | 0.367
4-DaHall 1-PDU-11 | [branch#042] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#063] [A] W | 0.965 | 6-DaHall 1-PDU-03 | [branch#035] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#024] [A] W | 0
4-DaHall 1-PDU-11 | [branch#043] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#010] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#036] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#025] [A] W | 0.338
4-DaHall 1-PDU-11 | [branch#044] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#064] [A] W | 0.151 | 6-DaHall 1-PDU-03 | [branch#037] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#026] [A] W | 1.001
4-DaHall 1-PDU-11 | [branch#045] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#011] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#038] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#027] [A] W | 0.619
4-DaHall 1-PDU-11 | [branch#046] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#065] [A] W | 0.597 | 6-DaHall 1-PDU-03 | [branch#039] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#028] [A] W | 0.554
4-DaHall 1-PDU-11 | [branch#047] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#012] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#040] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#029] [A] W | 0.713
4-DaHall 1-PDU-11 | [branch#048] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#066] [A] W | 0.59 | 6-DaHall 1-PDU-03 | [branch#041] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#030] [A] W | 0.972
4-DaHall 1-PDU-11 | [branch#049] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#013] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#042] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#031] [A] W | 0.929
4-DaHall 1-PDU-11 | [branch#050] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#067] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#043] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#032] [A] W | 0
4-DaHall 1-PDU-12 | [branch#001] [A] W | 0.122 | 5-DaHall 1-PDU-03 | [branch#014] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#044] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#033] [A] W | 0
4-DaHall 1-PDU-12 | [branch#002] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#068] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#045] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#034] [A] W | 0
4-DaHall 1-PDU-12 | [branch#003] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#046] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#035] [A] W | 0
4-DaHall 1-PDU-12 | [branch#004] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#069] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#047] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#036] [A] W | 0.828
4-DaHall 1-PDU-12 | [branch#005] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#016] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#048] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#037] [A] W | 1.448
4-DaHall 1-PDU-12 | [branch#006] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#070] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#049] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#038] [A] W | 0.446
4-DaHall 1-PDU-12 | [branch#007] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#017] [A] W | 0 | 6-DaHall 1-PDU-03 | [branch#050] [A] W | 0 | 7-DaHall 1-RPP-01 | [branch#039] [A] W | 0
4-DaHall 1-PDU-12 | [branch#008] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#071] [A] W | 0.36 | 6-DaHall 1-PDU-04 | [branch#001] [A] W | 1.455 | 7-DaHall 1-RPP-01 | [branch#040] [A] W | 1.065
4-DaHall 1-PDU-12 | [branch#009] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#018] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#002] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#001] [A] W | 0.216
4-DaHall 1-PDU-12 | [branch#010] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#072] [A] W | 0.352 | 6-DaHall 1-PDU-04 | [branch#003] [A] W | 1.663 | 7-DaHall 1-RPP-02 | [branch#002] [A] W | 3.573
4-DaHall 1-PDU-12 | [branch#011] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#019] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#004] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#003] [A] W | 0.129
4-DaHall 1-PDU-12 | [branch#012] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#073] [A] W | 0.331 | 6-DaHall 1-PDU-04 | [branch#005] [A] W | 0.324 | 7-DaHall 1-RPP-02 | [branch#004] [A] W | 0
4-DaHall 1-PDU-12 | [branch#013] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#020] [A] W | 0.906 | 6-DaHall 1-PDU-04 | [branch#006] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#005] [A] W | 0
4-DaHall 1-PDU-12 | [branch#014] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#074] [A] W | 0.367 | 6-DaHall 1-PDU-04 | [branch#007] [A] W | 0.936 | 7-DaHall 1-RPP-02 | [branch#006] [A] W | 0
4-DaHall 1-PDU-12 | [branch#015] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#021] [A] W | 0.453 | 6-DaHall 1-PDU-04 | [branch#008] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#007] [A] W | 0.223
4-DaHall 1-PDU-12 | [branch#016] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#075] [A] W | 0.245 | 6-DaHall 1-PDU-04 | [branch#009] [A] W | 0.886 | 7-DaHall 1-RPP-02 | [branch#008] [A] W | 1.353
4-DaHall 1-PDU-12 | [branch#017] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#022] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#010] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#009] [A] W | 0.345
4-DaHall 1-PDU-12 | [branch#018] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#076] [A] W | 0.309 | 6-DaHall 1-PDU-04 | [branch#011] [A] W | 1.087 | 7-DaHall 1-RPP-02 | [branch#010] [A] W | 0.115
4-DaHall 1-PDU-12 | [branch#019] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#023] [A] W | 0.698 | 6-DaHall 1-PDU-04 | [branch#012] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#011] [A] W | 0
4-DaHall 1-PDU-12 | [branch#020] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#077] [A] W | 0.677 | 6-DaHall 1-PDU-04 | [branch#013] [A] W | 1.181 | 7-DaHall 1-RPP-02 | [branch#012] [A] W | 0.921
4-DaHall 1-PDU-12 | [branch#021] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#024] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#014] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#013] [A] W | 0.547
4-DaHall 1-PDU-12 | [branch#022] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#078] [A] W | 0.655 | 6-DaHall 1-PDU-04 | [branch#015] [A] W | 0.806 | 7-DaHall 1-RPP-02 | [branch#014] [A] W | 3.312
4-DaHall 1-PDU-12 | [branch#023] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#025] [A] W | 0.944 | 6-DaHall 1-PDU-04 | [branch#016] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#015] [A] W | 0.374
4-DaHall 1-PDU-12 | [branch#024] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#079] [A] W | 0.857 | 6-DaHall 1-PDU-04 | [branch#017] [A] W | 0.381 | 7-DaHall 1-RPP-02 | [branch#016] [A] W | 0
4-DaHall 1-PDU-12 | [branch#025] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#026] [A] W | 1.39 | 6-DaHall 1-PDU-04 | [branch#018] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#017] [A] W | 0.879
4-DaHall 1-PDU-12 | [branch#026] [A] W | 0 | 5-DaHall 1-PDU-03 | [branch#080] [A] W | 1.009 | 6-DaHall 1-PDU-04 | [branch#019] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#018] [A] W | 0
4-DaHall 1-PDU-12 | [branch#027] [A] W | 0.389 | 5-DaHall 1-PDU-04 | [branch#001] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#020] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#019] [A] W | 0
4-DaHall 1-PDU-12 | [branch#028] [A] W | 0.187 | 5-DaHall 1-PDU-04 | [branch#055] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#021] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#020] [A] W | 0.252
4-DaHall 1-PDU-12 | [branch#029] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#002] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#022] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#021] [A] W | 0
4-DaHall 1-PDU-12 | [branch#030] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#056] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#023] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#022] [A] W | 0
4-DaHall 1-PDU-12 | [branch#031] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#003] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#024] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#023] [A] W | 0
4-DaHall 1-PDU-12 | [branch#032] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#057] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#025] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#024] [A] W | 0.626
4-DaHall 1-PDU-12 | [branch#033] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#004] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#026] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#025] [A] W | 0
4-DaHall 1-PDU-12 | [branch#034] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#058] [A] W | 0.144 | 6-DaHall 1-PDU-04 | [branch#027] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#026] [A] W | 0.05
4-DaHall 1-PDU-12 | [branch#035] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#005] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#028] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#027] [A] W | 1.311
4-DaHall 1-PDU-12 | [branch#036] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#059] [A] W | 0.439 | 6-DaHall 1-PDU-04 | [branch#029] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#028] [A] W | 0
4-DaHall 1-PDU-12 | [branch#037] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#006] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#030] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#029] [A] W | 0
4-DaHall 1-PDU-12 | [branch#038] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#060] [A] W | 0.958 | 6-DaHall 1-PDU-04 | [branch#031] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#030] [A] W | 0.482
4-DaHall 1-PDU-12 | [branch#039] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#007] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#032] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#031] [A] W | 0
4-DaHall 1-PDU-12 | [branch#040] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#061] [A] W | 0.439 | 6-DaHall 1-PDU-04 | [branch#033] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#032] [A] W | 0.785
4-DaHall 1-PDU-12 | [branch#041] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#008] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#034] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#033] [A] W | 0
4-DaHall 1-PDU-12 | [branch#042] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#062] [A] W | 0.237 | 6-DaHall 1-PDU-04 | [branch#035] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#034] [A] W | 0
4-DaHall 1-PDU-12 | [branch#043] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#009] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#036] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#035] [A] W | 0.468
4-DaHall 1-PDU-12 | [branch#044] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#063] [A] W | 0.935 | 6-DaHall 1-PDU-04 | [branch#037] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#036] [A] W | 1.693
4-DaHall 1-PDU-12 | [branch#045] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#010] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#038] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#037] [A] W | 1.015
4-DaHall 1-PDU-12 | [branch#046] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#064] [A] W | 0.165 | 6-DaHall 1-PDU-04 | [branch#039] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#038] [A] W | 1.087
4-DaHall 1-PDU-12 | [branch#047] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#011] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#040] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#039] [A] W | 3.033
4-DaHall 1-PDU-12 | [branch#048] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#065] [A] W | 0.381 | 6-DaHall 1-PDU-04 | [branch#041] [A] W | 0 | 7-DaHall 1-RPP-02 | [branch#040] [A] W | 0
4-DaHall 1-PDU-12 | [branch#049] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#012] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#042] [A] W | 0 | 7-DaHall 1-RPP-03 | [branch#001] [A] W | 0.237
4-DaHall 1-PDU-12 | [branch#050] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#066] [A] W | 0.583 | 6-DaHall 1-PDU-04 | [branch#043] [A] W | 0 | 7-DaHall 1-RPP-03 | [branch#002] [A] W | 0.252
4-DaHall 1-PDU-13 | [branch#001] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#013] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#044] [A] W | 0 | 7-DaHall 1-RPP-03 | [branch#003] [A] W | 0.547
4-DaHall 1-PDU-13 | [branch#002] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#067] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#045] [A] W | 0 | 7-DaHall 1-RPP-03 | [branch#004] [A] W | 0
4-DaHall 1-PDU-13 | [branch#003] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#014] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#046] [A] W | 0 | 7-DaHall 1-RPP-03 | [branch#005] [A] W | 0.698
4-DaHall 1-PDU-13 | [branch#004] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#068] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#047] [A] W | 0 | 7-DaHall 1-RPP-03 | [branch#006] [A] W | 0.36
4-DaHall 1-PDU-13 | [branch#005] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#048] [A] W | 0 | 7-DaHall 1-RPP-03 | [branch#007] [A] W | 0.569
4-DaHall 1-PDU-13 | [branch#006] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#069] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#049] [A] W | 0 | 7-DaHall 1-RPP-03 | [branch#008] [A] W | 0.439
4-DaHall 1-PDU-13 | [branch#007] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#016] [A] W | 0 | 6-DaHall 1-PDU-04 | [branch#050] [A] W | 0 | 7-DaHall 1-RPP-03 | [branch#009] [A] W | 0.576
4-DaHall 1-PDU-13 | [branch#008] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#070] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#001] [A] W | 0 | 7-DaHall 1-RPP-03 | [branch#010] [A] W | 0.518
4-DaHall 1-PDU-13 | [branch#009] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#017] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#002] [A] W | 2.823 | 7-DaHall 1-RPP-04 | [branch#001] [A] W | 1.109
4-DaHall 1-PDU-13 | [branch#010] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#071] [A] W | 0.086 | 6-DaHall 1-PDU-05 | [branch#003] [A] W | 0 | 7-DaHall 1-RPP-04 | [branch#002] [A] W | 0.388
4-DaHall 1-PDU-13 | [branch#011] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#018] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#004] [A] W | 1.137 | 7-DaHall 1-RPP-04 | [branch#003] [A] W | 0.692
4-DaHall 1-PDU-13 | [branch#012] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#072] [A] W | 0.036 | 6-DaHall 1-PDU-05 | [branch#005] [A] W | 0 | 7-DaHall 1-RPP-04 | [branch#004] [A] W | 0
4-DaHall 1-PDU-13 | [branch#013] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#073] [A] W | 0.353 | 6-DaHall 1-PDU-05 | [branch#006] [A] W | 0.144 | 7-DaHall 1-RPP-04 | [branch#005] [A] W | 0.951
4-DaHall 1-PDU-13 | [branch#014] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#019] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#007] [A] W | 0 | 7-DaHall 1-RPP-04 | [branch#006] [A] W | 0.273
4-DaHall 1-PDU-13 | [branch#015] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#020] [A] W | 1.044 | 6-DaHall 1-PDU-05 | [branch#008] [A] W | 0.741 | 7-DaHall 1-RPP-04 | [branch#007] [A] W | 0.878
4-DaHall 1-PDU-13 | [branch#016] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#074] [A] W | 0.453 | 6-DaHall 1-PDU-05 | [branch#009] [A] W | 0 | 7-DaHall 1-RPP-04 | [branch#008] [A] W | 0.431
4-DaHall 1-PDU-13 | [branch#017] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#075] [A] W | 0.432 | 6-DaHall 1-PDU-05 | [branch#010] [A] W | 0.194 | 7-DaHall 1-RPP-04 | [branch#009] [A] W | 0.367
4-DaHall 1-PDU-13 | [branch#018] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#021] [A] W | 0.295 | 6-DaHall 1-PDU-05 | [branch#011] [A] W | 0.381 | 7-DaHall 1-RPP-04 | [branch#010] [A] W | 0.554
4-DaHall 1-PDU-13 | [branch#019] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#022] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#012] [A] W | 0.302
4-DaHall 1-PDU-13 | [branch#020] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#076] [A] W | 0.259 | 6-DaHall 1-PDU-05 | [branch#013] [A] W | 0.324
4-DaHall 1-PDU-13 | [branch#021] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#077] [A] W | 0.504 | 6-DaHall 1-PDU-05 | [branch#014] [A] W | 1.188
4-DaHall 1-PDU-13 | [branch#022] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#023] [A] W | 0.72 | 6-DaHall 1-PDU-05 | [branch#015] [A] W | 0.727
4-DaHall 1-PDU-13 | [branch#023] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#024] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#016] [A] W | 0.742
4-DaHall 1-PDU-13 | [branch#024] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#078] [A] W | 0.497 | 6-DaHall 1-PDU-05 | [branch#017] [A] W | 0.208
4-DaHall 1-PDU-13 | [branch#025] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#079] [A] W | 0.791 | 6-DaHall 1-PDU-05 | [branch#018] [A] W | 0
4-DaHall 1-PDU-13 | [branch#026] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#025] [A] W | 1.001 | 6-DaHall 1-PDU-05 | [branch#019] [A] W | 0
4-DaHall 1-PDU-13 | [branch#027] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#026] [A] W | 1.347 | 6-DaHall 1-PDU-05 | [branch#020] [A] W | 0
4-DaHall 1-PDU-13 | [branch#028] [A] W | 0 | 5-DaHall 1-PDU-04 | [branch#080] [A] W | 0.958 | 6-DaHall 1-PDU-05 | [branch#021] [A] W | 0
4-DaHall 1-PDU-13 | [branch#029] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#001] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#022] [A] W | 0
4-DaHall 1-PDU-13 | [branch#030] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#002] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#023] [A] W | 0
4-DaHall 1-PDU-13 | [branch#031] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#003] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#024] [A] W | 0
4-DaHall 1-PDU-13 | [branch#032] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#004] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#025] [A] W | 2.614
4-DaHall 1-PDU-13 | [branch#033] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#005] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#026] [A] W | 0
4-DaHall 1-PDU-13 | [branch#034] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#006] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#027] [A] W | 1.152
4-DaHall 1-PDU-13 | [branch#035] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#007] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#028] [A] W | 0
4-DaHall 1-PDU-13 | [branch#036] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#008] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#029] [A] W | 0
4-DaHall 1-PDU-13 | [branch#037] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#009] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#030] [A] W | 0
4-DaHall 1-PDU-13 | [branch#038] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#010] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#031] [A] W | 0.36
4-DaHall 1-PDU-13 | [branch#039] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#011] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#032] [A] W | 0
4-DaHall 1-PDU-13 | [branch#040] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#012] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#033] [A] W | 0.208
4-DaHall 1-PDU-13 | [branch#041] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#013] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#034] [A] W | 0
4-DaHall 1-PDU-13 | [branch#042] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#014] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#035] [A] W | 0.129
4-DaHall 1-PDU-13 | [branch#043] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#036] [A] W | 0
4-DaHall 1-PDU-13 | [branch#044] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#016] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#037] [A] W | 1.707
4-DaHall 1-PDU-13 | [branch#045] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#017] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#038] [A] W | 0
4-DaHall 1-PDU-13 | [branch#046] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#018] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#039] [A] W | 0.461
4-DaHall 1-PDU-13 | [branch#047] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#019] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#040] [A] W | 0
4-DaHall 1-PDU-13 | [branch#048] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#020] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#041] [A] W | 0.461
4-DaHall 1-PDU-13 | [branch#049] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#021] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#042] [A] W | 0
4-DaHall 1-PDU-13 | [branch#050] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#022] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#043] [A] W | 1.297
4-DaHall 1-PDU-13 | [branch#051] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#023] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#044] [A] W | 0
4-DaHall 1-PDU-13 | [branch#052] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#024] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#045] [A] W | 1.058
4-DaHall 1-PDU-13 | [branch#053] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#025] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#046] [A] W | 0
4-DaHall 1-PDU-13 | [branch#054] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#026] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#047] [A] W | 1.173
4-DaHall 1-PDU-14 | [branch#001] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#027] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#048] [A] W | 0
4-DaHall 1-PDU-14 | [branch#002] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#028] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#049] [A] W | 1.872
4-DaHall 1-PDU-14 | [branch#003] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#029] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#050] [A] W | 0
4-DaHall 1-PDU-14 | [branch#004] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#030] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#051] [A] W | 1.094
4-DaHall 1-PDU-14 | [branch#005] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#031] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#052] [A] W | 0
4-DaHall 1-PDU-14 | [branch#006] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#032] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#053] [A] W | 1.475
4-DaHall 1-PDU-14 | [branch#007] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#033] [A] W | 0 | 6-DaHall 1-PDU-05 | [branch#054] [A] W | 0.886
4-DaHall 1-PDU-14 | [branch#008] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#034] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#001] [A] W | 0
4-DaHall 1-PDU-14 | [branch#009] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#035] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#002] [A] W | 2.598
4-DaHall 1-PDU-14 | [branch#010] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#036] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#003] [A] W | 0
4-DaHall 1-PDU-14 | [branch#011] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#037] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#004] [A] W | 0.957
4-DaHall 1-PDU-14 | [branch#012] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#038] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#005] [A] W | 0
4-DaHall 1-PDU-14 | [branch#013] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#039] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#006] [A] W | 0.136
4-DaHall 1-PDU-14 | [branch#014] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#040] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#007] [A] W | 0
4-DaHall 1-PDU-14 | [branch#015] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#041] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#008] [A] W | 0.958
4-DaHall 1-PDU-14 | [branch#016] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#042] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#009] [A] W | 0
4-DaHall 1-PDU-14 | [branch#017] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#043] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#010] [A] W | 0.108
4-DaHall 1-PDU-14 | [branch#018] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#044] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#011] [A] W | 0.288
4-DaHall 1-PDU-14 | [branch#019] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#045] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#012] [A] W | 0
4-DaHall 1-PDU-14 | [branch#020] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#046] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#013] [A] W | 0.655
4-DaHall 1-PDU-14 | [branch#021] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#047] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#014] [A] W | 0.669
4-DaHall 1-PDU-14 | [branch#022] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#048] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#015] [A] W | 0.655
4-DaHall 1-PDU-14 | [branch#023] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#049] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#016] [A] W | 0.929
4-DaHall 1-PDU-14 | [branch#024] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#050] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#017] [A] W | 0.194
4-DaHall 1-PDU-14 | [branch#025] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#051] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#018] [A] W | 0
4-DaHall 1-PDU-14 | [branch#026] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#052] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#019] [A] W | 0
4-DaHall 1-PDU-14 | [branch#027] [A] W | 0.821 | 5-DaHall 1-PDU-05 | [branch#053] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#020] [A] W | 0
4-DaHall 1-PDU-14 | [branch#028] [A] W | 0 | 5-DaHall 1-PDU-05 | [branch#054] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#021] [A] W | 0
4-DaHall 1-PDU-14 | [branch#029] [A] W | 1.015 | 5-DaHall 1-PDU-06 | [branch#001] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#022] [A] W | 0
4-DaHall 1-PDU-14 | [branch#030] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#002] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#023] [A] W | 0
4-DaHall 1-PDU-14 | [branch#031] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#003] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#024] [A] W | 0
4-DaHall 1-PDU-14 | [branch#032] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#004] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#025] [A] W | 1.75
4-DaHall 1-PDU-14 | [branch#033] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#005] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#026] [A] W | 0
4-DaHall 1-PDU-14 | [branch#034] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#006] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#027] [A] W | 1.519
4-DaHall 1-PDU-14 | [branch#035] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#007] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#028] [A] W | 0
4-DaHall 1-PDU-14 | [branch#036] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#008] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#029] [A] W | 0
4-DaHall 1-PDU-14 | [branch#037] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#009] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#030] [A] W | 0
4-DaHall 1-PDU-14 | [branch#038] [A] W | 1.109 | 5-DaHall 1-PDU-06 | [branch#010] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#031] [A] W | 0.072
4-DaHall 1-PDU-14 | [branch#039] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#011] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#032] [A] W | 0
4-DaHall 1-PDU-14 | [branch#040] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#012] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#033] [A] W | 0.208
4-DaHall 1-PDU-14 | [branch#041] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#013] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#034] [A] W | 0
4-DaHall 1-PDU-14 | [branch#042] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#014] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#035] [A] W | 0.064
4-DaHall 1-PDU-14 | [branch#043] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#036] [A] W | 0
4-DaHall 1-PDU-14 | [branch#044] [A] W | 1.044 | 5-DaHall 1-PDU-06 | [branch#016] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#037] [A] W | 2.296
4-DaHall 1-PDU-14 | [branch#045] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#017] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#038] [A] W | 0
4-DaHall 1-PDU-14 | [branch#046] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#018] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#039] [A] W | 0.446
4-DaHall 1-PDU-14 | [branch#047] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#019] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#040] [A] W | 0
4-DaHall 1-PDU-14 | [branch#048] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#020] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#041] [A] W | 0.237
4-DaHall 1-PDU-14 | [branch#049] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#021] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#042] [A] W | 0
4-DaHall 1-PDU-14 | [branch#050] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#022] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#043] [A] W | 1.16
4-DaHall 1-PDU-14 | [branch#051] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#023] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#044] [A] W | 0
4-DaHall 1-PDU-14 | [branch#052] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#024] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#045] [A] W | 1.087
4-DaHall 1-PDU-14 | [branch#053] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#025] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#046] [A] W | 0
4-DaHall 1-PDU-14 | [branch#054] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#026] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#047] [A] W | 1.072
4-DaHall 1-RPP-01 | [branch#001] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#027] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#048] [A] W | 0
4-DaHall 1-RPP-01 | [branch#002] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#028] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#049] [A] W | 0.295
4-DaHall 1-RPP-01 | [branch#003] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#029] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#050] [A] W | 0
4-DaHall 1-RPP-01 | [branch#004] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#030] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#051] [A] W | 1.239
4-DaHall 1-RPP-01 | [branch#005] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#031] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#052] [A] W | 0
4-DaHall 1-RPP-01 | [branch#006] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#032] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#053] [A] W | 0.187
4-DaHall 1-RPP-01 | [branch#007] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#033] [A] W | 0 | 6-DaHall 1-PDU-06 | [branch#054] [A] W | 0.54
4-DaHall 1-RPP-01 | [branch#008] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#034] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#001] [A] W | 0
4-DaHall 1-RPP-02 | [branch#001] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#035] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#002] [A] W | 0
4-DaHall 1-RPP-02 | [branch#002] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#036] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#003] [A] W | 0
4-DaHall 1-RPP-02 | [branch#003] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#037] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#004] [A] W | 0
4-DaHall 1-RPP-02 | [branch#004] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#038] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#005] [A] W | 0
4-DaHall 1-RPP-02 | [branch#005] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#039] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#006] [A] W | 0
4-DaHall 1-RPP-02 | [branch#006] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#040] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#007] [A] W | 0
4-DaHall 1-RPP-02 | [branch#007] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#041] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#008] [A] W | 0
4-DaHall 1-RPP-02 | [branch#008] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#042] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#009] [A] W | 0
4-EPS-CEP-06 | [branch#001] [A] W | 3.653 | 5-DaHall 1-PDU-06 | [branch#043] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#010] [A] W | 0
4-EPS-CEP-06 | [branch#002] [A] W | 9.028 | 5-DaHall 1-PDU-06 | [branch#044] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#011] [A] W | 0
4-EPS-CEP-06 | [branch#003] [A] W | 3.657 | 5-DaHall 1-PDU-06 | [branch#045] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#012] [A] W | 0
4-EPS-CEP-06 | [branch#004] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#046] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#013] [A] W | 0
4-EPS-CEP-06 | [branch#005] [A] W | 3.811 | 5-DaHall 1-PDU-06 | [branch#047] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#014] [A] W | 0
4-EPS-CEP-06 | [branch#006] [A] W | 0 | 5-DaHall 1-PDU-06 | [branch#048] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#015] [A] W | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#049] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#016] [A] W | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#050] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#017] [A] W | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#051] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#018] [A] W | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#052] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#019] [A] W | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#053] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#020] [A] W | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#054] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#021] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#001] [A] W | 1.711 | 6-DaHall 1-PDU-07 | [branch#022] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#002] [A] W | 0.169 | 6-DaHall 1-PDU-07 | [branch#023] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#003] [A] W | 0.165 | 6-DaHall 1-PDU-07 | [branch#024] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#004] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#025] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#005] [A] W | 0.082 | 6-DaHall 1-PDU-07 | [branch#026] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#006] [A] W | 0.082 | 6-DaHall 1-PDU-07 | [branch#027] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#007] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#028] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#008] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#029] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#009] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#030] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#010] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#031] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#011] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#032] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#012] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#033] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#013] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#034] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#014] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#035] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#036] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#016] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#037] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#017] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#038] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#018] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#039] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#019] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#040] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#020] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#041] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#021] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#042] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#022] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#043] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#023] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#044] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#024] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#045] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#025] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#046] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#026] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#047] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#027] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#048] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#028] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#049] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#029] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#050] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#030] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#051] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#031] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#052] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#032] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#053] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#033] [A] W | 0 | 6-DaHall 1-PDU-07 | [branch#054] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#034] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#001] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#035] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#002] [A] W | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#036] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#003] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#001] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#004] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#002] [A] W | 0.223 | 6-DaHall 1-PDU-08 | [branch#005] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#003] [A] W | 0.176 | 6-DaHall 1-PDU-08 | [branch#006] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#004] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#007] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#005] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#008] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#006] [A] W | 0.255 | 6-DaHall 1-PDU-08 | [branch#009] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#007] [A] W | 1.083 | 6-DaHall 1-PDU-08 | [branch#010] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#008] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#011] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#009] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#012] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#010] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#013] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#011] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#014] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#012] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#015] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#013] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#016] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#014] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#017] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#018] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#016] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#019] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#017] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#020] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#018] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#021] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#019] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#022] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#020] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#023] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#021] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#024] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#022] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#025] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#023] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#026] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#024] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#027] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#025] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#028] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#026] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#029] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#027] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#030] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#028] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#031] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#029] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#032] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#030] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#033] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#031] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#034] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#032] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#035] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#033] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#036] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#034] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#037] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#035] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#038] [A] W | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#036] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#039] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#001] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#040] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#002] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#041] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#003] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#042] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#004] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#043] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#005] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#044] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#006] [A] W | 0.403 | 6-DaHall 1-PDU-08 | [branch#045] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#007] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#046] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#008] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#047] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#009] [A] W | 1.138 | 6-DaHall 1-PDU-08 | [branch#048] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#010] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#049] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#011] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#050] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#012] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#051] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#013] [A] W | 0.431 | 6-DaHall 1-PDU-08 | [branch#052] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#014] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#053] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-08 | [branch#054] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#016] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#001] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#017] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#002] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#018] [A] W | 0.705 | 6-DaHall 1-PDU-09 | [branch#003] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#019] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#004] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#020] [A] W | 0.446 | 6-DaHall 1-PDU-09 | [branch#005] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#021] [A] W | 0.525 | 6-DaHall 1-PDU-09 | [branch#006] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#022] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#007] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#023] [A] W | 1.195 | 6-DaHall 1-PDU-09 | [branch#008] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#024] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#009] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#025] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#010] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#026] [A] W | 1.189 | 6-DaHall 1-PDU-09 | [branch#011] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#027] [A] W | 0.604 | 6-DaHall 1-PDU-09 | [branch#012] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#028] [A] W | 1.217 | 6-DaHall 1-PDU-09 | [branch#013] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#029] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#014] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#030] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#015] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#031] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#016] [A] W | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#032] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#017] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#001] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#018] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#002] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#019] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#003] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#020] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#004] [A] W | 0.352 | 6-DaHall 1-PDU-09 | [branch#021] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#005] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#022] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#006] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#023] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#007] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#024] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#008] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#025] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#009] [A] W | 0.626 | 6-DaHall 1-PDU-09 | [branch#026] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#010] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#027] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#011] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#028] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#012] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#029] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#013] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#030] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#014] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#031] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#032] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#016] [A] W | 1.44 | 6-DaHall 1-PDU-09 | [branch#033] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#017] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#034] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#018] [A] W | 0.699 | 6-DaHall 1-PDU-09 | [branch#035] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#019] [A] W | 0.583 | 6-DaHall 1-PDU-09 | [branch#036] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#020] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#037] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#021] [A] W | 1.123 | 6-DaHall 1-PDU-09 | [branch#038] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#022] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#039] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#023] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#040] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#024] [A] W | 0.778 | 6-DaHall 1-PDU-09 | [branch#041] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#025] [A] W | 0.77 | 6-DaHall 1-PDU-09 | [branch#042] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#026] [A] W | 1.087 | 6-DaHall 1-PDU-09 | [branch#043] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#027] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#044] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#028] [A] W | 1.289 | 6-DaHall 1-PDU-09 | [branch#045] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#029] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#046] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#030] [A] W | 1.419 | 6-DaHall 1-PDU-09 | [branch#047] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#031] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#048] [A] W | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#032] [A] W | 0.676 | 6-DaHall 1-PDU-09 | [branch#049] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#001] [A] W | 0 | 6-DaHall 1-PDU-09 | [branch#050] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#002] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#001] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#003] [A] W | 1.375 | 6-DaHall 1-PDU-10 | [branch#002] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#004] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#003] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#005] [A] W | 1.275 | 6-DaHall 1-PDU-10 | [branch#004] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#006] [A] W | 1.325 | 6-DaHall 1-PDU-10 | [branch#005] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#007] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#006] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#008] [A] W | 0.907 | 6-DaHall 1-PDU-10 | [branch#007] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#009] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#008] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#010] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#009] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#011] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#010] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#012] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#011] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#013] [A] W | 0.108 | 6-DaHall 1-PDU-10 | [branch#012] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#014] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#013] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#014] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#016] [A] W | 0.864 | 6-DaHall 1-PDU-10 | [branch#015] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#017] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#016] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#018] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#017] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#019] [A] W | 1.188 | 6-DaHall 1-PDU-10 | [branch#018] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#020] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#019] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#021] [A] W | 0.72 | 6-DaHall 1-PDU-10 | [branch#020] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#022] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#021] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#023] [A] W | 2.181 | 6-DaHall 1-PDU-10 | [branch#022] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#024] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#023] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#025] [A] W | 0.532 | 6-DaHall 1-PDU-10 | [branch#024] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#026] [A] W | 0.403 | 6-DaHall 1-PDU-10 | [branch#025] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#027] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#026] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#028] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#027] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#029] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#028] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#030] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#029] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#031] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#030] [A] W | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#032] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#031] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#001] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#032] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#002] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#033] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#003] [A] W | 0.662 | 6-DaHall 1-PDU-10 | [branch#034] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#004] [A] W | 1.628 | 6-DaHall 1-PDU-10 | [branch#035] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#005] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#036] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#006] [A] W | 0.633 | 6-DaHall 1-PDU-10 | [branch#037] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#007] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#038] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#008] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#039] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#009] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#040] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#010] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#041] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#011] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#042] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#012] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#043] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#013] [A] W | 0.353 | 6-DaHall 1-PDU-10 | [branch#044] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#014] [A] W | 0.713 | 6-DaHall 1-PDU-10 | [branch#045] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#046] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#016] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#047] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#017] [A] W | 0.194 | 6-DaHall 1-PDU-10 | [branch#048] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#018] [A] W | 0 | 6-DaHall 1-PDU-10 | [branch#049] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#019] [A] W | 0.547 | 6-DaHall 1-PDU-10 | [branch#050] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#020] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#001] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#021] [A] W | 0.806 | 6-DaHall 1-PDU-11 | [branch#002] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#022] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#003] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#023] [A] W | 0.561 | 6-DaHall 1-PDU-11 | [branch#004] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#024] [A] W | 1.138 | 6-DaHall 1-PDU-11 | [branch#005] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#025] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#006] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#026] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#007] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#027] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#008] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#028] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#009] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#029] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#010] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#030] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#011] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#031] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#012] [A] W | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#032] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#013] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#001] [A] W | 3.012 | 6-DaHall 1-PDU-11 | [branch#014] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#002] [A] W | 1.779 | 6-DaHall 1-PDU-11 | [branch#015] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#003] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#016] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#004] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#017] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#005] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#018] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#006] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#019] [A] W | 1.317
|  |  | 5-DaHall 1-PDU-15 | [branch#007] [A] W | 0.799 | 6-DaHall 1-PDU-11 | [branch#020] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#008] [A] W | 0.842 | 6-DaHall 1-PDU-11 | [branch#021] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#009] [A] W | 0.295 | 6-DaHall 1-PDU-11 | [branch#022] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#010] [A] W | 1.52 | 6-DaHall 1-PDU-11 | [branch#023] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#011] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#024] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#012] [A] W | 0.417 | 6-DaHall 1-PDU-11 | [branch#025] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#013] [A] W | 0.122 | 6-DaHall 1-PDU-11 | [branch#026] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#014] [A] W | 0.251 | 6-DaHall 1-PDU-11 | [branch#027] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#015] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#028] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#016] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#029] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#017] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#030] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#018] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#031] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#019] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#032] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#020] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#033] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#021] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#034] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#022] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#035] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#023] [A] W | 0.497 | 6-DaHall 1-PDU-11 | [branch#036] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#024] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#037] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#025] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#038] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#026] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#039] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#027] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#040] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#028] [A] W | 0.115 | 6-DaHall 1-PDU-11 | [branch#041] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#029] [A] W | 0.036 | 6-DaHall 1-PDU-11 | [branch#042] [A] W | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#030] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#043] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#001] [A] W | 2.273 | 6-DaHall 1-PDU-11 | [branch#044] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#002] [A] W | 1.751 | 6-DaHall 1-PDU-11 | [branch#045] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#003] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#046] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#004] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#047] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#005] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#048] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#006] [A] W | 0 | 6-DaHall 1-PDU-11 | [branch#049] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#007] [A] W | 0.85 | 6-DaHall 1-PDU-11 | [branch#050] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#008] [A] W | 0.958 | 6-DaHall 1-PDU-12 | [branch#001] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#009] [A] W | 0.309 | 6-DaHall 1-PDU-12 | [branch#002] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#010] [A] W | 0.05 | 6-DaHall 1-PDU-12 | [branch#003] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#011] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#004] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#012] [A] W | 0.439 | 6-DaHall 1-PDU-12 | [branch#005] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#013] [A] W | 0.381 | 6-DaHall 1-PDU-12 | [branch#006] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#014] [A] W | 0.288 | 6-DaHall 1-PDU-12 | [branch#007] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#015] [A] W | 0.734 | 6-DaHall 1-PDU-12 | [branch#008] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#016] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#009] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#017] [A] W | 0.741 | 6-DaHall 1-PDU-12 | [branch#010] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#018] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#011] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#019] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#012] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#020] [A] W | 0.122 | 6-DaHall 1-PDU-12 | [branch#013] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#021] [A] W | 0.064 | 6-DaHall 1-PDU-12 | [branch#014] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#022] [A] W | 0.115 | 6-DaHall 1-PDU-12 | [branch#015] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#023] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#016] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#024] [A] W | 0.439 | 6-DaHall 1-PDU-12 | [branch#017] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#025] [A] W | 0.093 | 6-DaHall 1-PDU-12 | [branch#018] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#026] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#019] [A] W | 1.268
|  |  | 5-DaHall 1-PDU-16 | [branch#027] [A] W | 0.324 | 6-DaHall 1-PDU-12 | [branch#020] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#028] [A] W | 0.036 | 6-DaHall 1-PDU-12 | [branch#021] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#029] [A] W | 0.482 | 6-DaHall 1-PDU-12 | [branch#022] [A] W | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#030] [A] W | 0.064 | 6-DaHall 1-PDU-12 | [branch#023] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 0155 [branch#01] [A] W | 0.126 | 6-DaHall 1-PDU-12 | [branch#024] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 0295 [branch#02] [A] W | 0.162 | 6-DaHall 1-PDU-12 | [branch#025] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 0435 [branch#03] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#026] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 0575 [branch#04] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#027] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 0715 [branch#05] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#028] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 0855 [branch#06] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#029] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 0995 [branch#07] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#030] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 1135 [branch#08] [A] W | 0.472 | 6-DaHall 1-PDU-12 | [branch#031] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 1275 [branch#09] [A] W | 1.581 | 6-DaHall 1-PDU-12 | [branch#032] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 1415 [branch#10] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#033] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 1555 [branch#11] [A] W | 0.104 | 6-DaHall 1-PDU-12 | [branch#034] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 1695 [branch#12] [A] W | 0.223 | 6-DaHall 1-PDU-12 | [branch#035] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 1835 [branch#13] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#036] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 1975 [branch#14] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#037] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 2115 [branch#15] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#038] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 2255 [branch#16] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#039] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 2395 [branch#17] [A] W | 0.115 | 6-DaHall 1-PDU-12 | [branch#040] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 2535 [branch#18] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#041] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 2675 [branch#19] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#042] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 2815 [branch#20] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#043] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 2955 [branch#21] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#044] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 3095 [branch#22] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#045] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 3235 [branch#23] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#046] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 3375 [branch#24] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#047] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 3515 [branch#25] [A] W | 0.345 | 6-DaHall 1-PDU-12 | [branch#048] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 3655 [branch#26] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#049] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 3795 [branch#27] [A] W | 0 | 6-DaHall 1-PDU-12 | [branch#050] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 3935 [branch#28] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#001] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 4075 [branch#29] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#002] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 4215 [branch#30] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#003] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 4355 [branch#31] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#004] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 4495 [branch#32] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#005] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 4635 [branch#33] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#006] [A] W | 0
|  |  | 5-DaHall 1-PDU-17 | 4775 [branch#34] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#007] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 0155 [branch#01] [A] W | 0.176 | 6-DaHall 1-PDU-13 | [branch#008] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 0295 [branch#02] [A] W | 0.154 | 6-DaHall 1-PDU-13 | [branch#009] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 0435 [branch#03] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#010] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 0575 [branch#04] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#011] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 0715 [branch#05] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#012] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 0855 [branch#06] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#013] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 0995 [branch#07] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#014] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 1135 [branch#08] [A] W | 0.45 | 6-DaHall 1-PDU-13 | [branch#015] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 1275 [branch#09] [A] W | 1.066 | 6-DaHall 1-PDU-13 | [branch#016] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 1415 [branch#10] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#017] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 1555 [branch#11] [A] W | 0.082 | 6-DaHall 1-PDU-13 | [branch#018] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 1695 [branch#12] [A] W | 0.158 | 6-DaHall 1-PDU-13 | [branch#019] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 1835 [branch#13] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#020] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 1975 [branch#14] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#021] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 2115 [branch#15] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#022] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 2255 [branch#16] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#023] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 2395 [branch#17] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#024] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 2535 [branch#18] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#025] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 2675 [branch#19] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#026] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 2815 [branch#20] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#027] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 2955 [branch#21] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#028] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 3095 [branch#22] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#029] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 3235 [branch#23] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#030] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 3375 [branch#24] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#031] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 3515 [branch#25] [A] W | 0.108 | 6-DaHall 1-PDU-13 | [branch#032] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 3655 [branch#26] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#033] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 3795 [branch#27] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#034] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 3935 [branch#28] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#035] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 4075 [branch#29] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#036] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 4215 [branch#30] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#037] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 4355 [branch#31] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#038] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 4495 [branch#32] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#039] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 4635 [branch#33] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#040] [A] W | 0
|  |  | 5-DaHall 1-PDU-18 | 4775 [branch#34] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#041] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 0155 [branch#01] [A] W | 0.885 | 6-DaHall 1-PDU-13 | [branch#042] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 0295 [branch#02] [A] W | 2.577 | 6-DaHall 1-PDU-13 | [branch#043] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 0435 [branch#03] [A] W | 1.742 | 6-DaHall 1-PDU-13 | [branch#044] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 0575 [branch#04] [A] W | 2.301 | 6-DaHall 1-PDU-13 | [branch#045] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 0715 [branch#05] [A] W | 0 | 6-DaHall 1-PDU-13 | [branch#046] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 0855 [branch#06] [A] W | 0.868 | 6-DaHall 1-PDU-13 | [branch#047] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 0995 [branch#07] [A] W | 2.805 | 6-DaHall 1-PDU-13 | [branch#048] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 1135 [branch#08] [A] W | 1.846 | 6-DaHall 1-PDU-13 | [branch#049] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 1275 [branch#09] [A] W | 2.984 | 6-DaHall 1-PDU-13 | [branch#050] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 1415 [branch#10] [A] W | 2.369 | 6-DaHall 1-PDU-13 | [branch#051] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 1555 [branch#11] [A] W | 1.941 | 6-DaHall 1-PDU-13 | [branch#052] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 1695 [branch#12] [A] W | 0.796 | 6-DaHall 1-PDU-13 | [branch#053] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 1835 [branch#13] [A] W | 2.744 | 6-DaHall 1-PDU-13 | [branch#054] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 1975 [branch#14] [A] W | 0.331 | 6-DaHall 1-PDU-14 | [branch#001] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 2115 [branch#15] [A] W | 2.224 | 6-DaHall 1-PDU-14 | [branch#002] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 2255 [branch#16] [A] W | 3.38 | 6-DaHall 1-PDU-14 | [branch#003] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 2395 [branch#17] [A] W | 1.411 | 6-DaHall 1-PDU-14 | [branch#004] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 2535 [branch#18] [A] W | 1.948 | 6-DaHall 1-PDU-14 | [branch#005] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 2675 [branch#19] [A] W | 1.649 | 6-DaHall 1-PDU-14 | [branch#006] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 2815 [branch#20] [A] W | 2.541 | 6-DaHall 1-PDU-14 | [branch#007] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 2955 [branch#21] [A] W | 0 | 6-DaHall 1-PDU-14 | [branch#008] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 3095 [branch#22] [A] W | 2.595 | 6-DaHall 1-PDU-14 | [branch#009] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 3235 [branch#23] [A] W | 1.397 | 6-DaHall 1-PDU-14 | [branch#010] [A] W | 0
|  |  | 5-DaHall 1-PDU-19 | 3375 [branch#24] [A] W | 0 | 6-DaHall 1-PDU-14 | [branch#011] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 0155 [branch#01] [A] W | 1.173 | 6-DaHall 1-PDU-14 | [branch#012] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 0295 [branch#02] [A] W | 2.526 | 6-DaHall 1-PDU-14 | [branch#013] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 0435 [branch#03] [A] W | 1.807 | 6-DaHall 1-PDU-14 | [branch#014] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 0575 [branch#04] [A] W | 2.304 | 6-DaHall 1-PDU-14 | [branch#015] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 0715 [branch#05] [A] W | 0 | 6-DaHall 1-PDU-14 | [branch#016] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 0855 [branch#06] [A] W | 0.785 | 6-DaHall 1-PDU-14 | [branch#017] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 0995 [branch#07] [A] W | 2.701 | 6-DaHall 1-PDU-14 | [branch#018] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 1135 [branch#08] [A] W | 1.915 | 6-DaHall 1-PDU-14 | [branch#019] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 1275 [branch#09] [A] W | 3.054 | 6-DaHall 1-PDU-14 | [branch#020] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 1415 [branch#10] [A] W | 2.412 | 6-DaHall 1-PDU-14 | [branch#021] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 1555 [branch#11] [A] W | 1.772 | 6-DaHall 1-PDU-14 | [branch#022] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 1695 [branch#12] [A] W | 0.771 | 6-DaHall 1-PDU-14 | [branch#023] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 1835 [branch#13] [A] W | 2.657 | 6-DaHall 1-PDU-14 | [branch#024] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 1975 [branch#14] [A] W | 0.309 | 6-DaHall 1-PDU-14 | [branch#025] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 2115 [branch#15] [A] W | 2.44 | 6-DaHall 1-PDU-14 | [branch#026] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 2255 [branch#16] [A] W | 3.528 | 6-DaHall 1-PDU-14 | [branch#027] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 2395 [branch#17] [A] W | 1.469 | 6-DaHall 1-PDU-14 | [branch#028] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 2535 [branch#18] [A] W | 1.844 | 6-DaHall 1-PDU-14 | [branch#029] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 2675 [branch#19] [A] W | 1.771 | 6-DaHall 1-PDU-14 | [branch#030] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 2815 [branch#20] [A] W | 1.317 | 6-DaHall 1-PDU-14 | [branch#031] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 2955 [branch#21] [A] W | 0 | 6-DaHall 1-PDU-14 | [branch#032] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 3095 [branch#22] [A] W | 0.792 | 6-DaHall 1-PDU-14 | [branch#033] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 3235 [branch#23] [A] W | 1.447 | 6-DaHall 1-PDU-14 | [branch#034] [A] W | 0
|  |  | 5-DaHall 1-PDU-20 | 3375 [branch#24] [A] W | 0 | 6-DaHall 1-PDU-14 | [branch#035] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 0155 [branch#01] [A] W | 2.197 | 6-DaHall 1-PDU-14 | [branch#036] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 0295 [branch#02] [A] W | 2.067 | 6-DaHall 1-PDU-14 | [branch#037] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 0435 [branch#03] [A] W | 1.967 | 6-DaHall 1-PDU-14 | [branch#038] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 0575 [branch#04] [A] W | 2.11 | 6-DaHall 1-PDU-14 | [branch#039] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 0715 [branch#05] [A] W | 0.958 | 6-DaHall 1-PDU-14 | [branch#040] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 0855 [branch#06] [A] W | 1.231 | 6-DaHall 1-PDU-14 | [branch#041] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 0995 [branch#07] [A] W | 2.787 | 6-DaHall 1-PDU-14 | [branch#042] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 1135 [branch#08] [A] W | 1.72 | 6-DaHall 1-PDU-14 | [branch#043] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 1275 [branch#09] [A] W | 2.959 | 6-DaHall 1-PDU-14 | [branch#044] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 1415 [branch#10] [A] W | 2.411 | 6-DaHall 1-PDU-14 | [branch#045] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 1555 [branch#11] [A] W | 2.643 | 6-DaHall 1-PDU-14 | [branch#046] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 1695 [branch#12] [A] W | 0.655 | 6-DaHall 1-PDU-14 | [branch#047] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 1835 [branch#13] [A] W | 2.392 | 6-DaHall 1-PDU-14 | [branch#048] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 1975 [branch#14] [A] W | 0.381 | 6-DaHall 1-PDU-14 | [branch#049] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 2115 [branch#15] [A] W | 1.152 | 6-DaHall 1-PDU-14 | [branch#050] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 2255 [branch#16] [A] W | 2.499 | 6-DaHall 1-PDU-14 | [branch#051] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 2395 [branch#17] [A] W | 1.476 | 6-DaHall 1-PDU-14 | [branch#052] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 2535 [branch#18] [A] W | 2.196 | 6-DaHall 1-PDU-14 | [branch#053] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 2675 [branch#19] [A] W | 1.418 | 6-DaHall 1-PDU-14 | [branch#054] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 2815 [branch#20] [A] W | 2.534
|  |  | 5-DaHall 1-PDU-21 | 2955 [branch#21] [A] W | 0
|  |  | 5-DaHall 1-PDU-21 | 3095 [branch#22] [A] W | 1.857
|  |  | 5-DaHall 1-PDU-21 | 3235 [branch#23] [A] W | 1.382
|  |  | 5-DaHall 1-PDU-21 | 3375 [branch#24] [A] W | 0
|  |  | 5-DaHall 1-PDU-22 | 0155 [branch#01] [A] W | 2.426
|  |  | 5-DaHall 1-PDU-22 | 0295 [branch#02] [A] W | 2.082
|  |  | 5-DaHall 1-PDU-22 | 0435 [branch#03] [A] W | 2.044
|  |  | 5-DaHall 1-PDU-22 | 0575 [branch#04] [A] W | 2.125
|  |  | 5-DaHall 1-PDU-22 | 0715 [branch#05] [A] W | 0.929
|  |  | 5-DaHall 1-PDU-22 | 0855 [branch#06] [A] W | 1.007
|  |  | 5-DaHall 1-PDU-22 | 0995 [branch#07] [A] W | 2.764
|  |  | 5-DaHall 1-PDU-22 | 1135 [branch#08] [A] W | 2.225
|  |  | 5-DaHall 1-PDU-22 | 1275 [branch#09] [A] W | 2.961
|  |  | 5-DaHall 1-PDU-22 | 1415 [branch#10] [A] W | 2.318
|  |  | 5-DaHall 1-PDU-22 | 1555 [branch#11] [A] W | 2.779
|  |  | 5-DaHall 1-PDU-22 | 1695 [branch#12] [A] W | 0.684
|  |  | 5-DaHall 1-PDU-22 | 1835 [branch#13] [A] W | 2.248
|  |  | 5-DaHall 1-PDU-22 | 1975 [branch#14] [A] W | 0.381
|  |  | 5-DaHall 1-PDU-22 | 2115 [branch#15] [A] W | 1.251
|  |  | 5-DaHall 1-PDU-22 | 2255 [branch#16] [A] W | 2.584
|  |  | 5-DaHall 1-PDU-22 | 2395 [branch#17] [A] W | 1.425
|  |  | 5-DaHall 1-PDU-22 | 2535 [branch#18] [A] W | 2.153
|  |  | 5-DaHall 1-PDU-22 | 2675 [branch#19] [A] W | 1.426
|  |  | 5-DaHall 1-PDU-22 | 2815 [branch#20] [A] W | 0.987
|  |  | 5-DaHall 1-PDU-22 | 2955 [branch#21] [A] W | 0
|  |  | 5-DaHall 1-PDU-22 | 3095 [branch#22] [A] W | 0.691
|  |  | 5-DaHall 1-PDU-22 | 3235 [branch#23] [A] W | 1.425
|  |  | 5-DaHall 1-PDU-22 | 3375 [branch#24] [A] W | 0

## 각층분기별_유효전력량(전월)
Date : 2024-01-01 ~ 2024-01-31
4F | 포인트명 | kWh(전월유효전력량) | 5F | 포인트명 | kWh(전월유효전력량) | 6F | 포인트명 | kWh(전월유효전력량) | 7F | 포인트명 | kWh(전월유효전력량)
4-CRACRm-CEP-01 | 0119 [branch#01] [A] KWh last month | 0 | 5-CRACRm-CEP-01 | 0119 [branch#01] [A] KWh last month | 20.1 | 6-DaHall 1-CEP-05 | [branch#001] [A] kWh last month | 212.9 | 7-DaHall 1-PDU-01 | [branch#001] [A] kWh last month | 0
4-CRACRm-CEP-01 | 0279 [branch#02] [A] KWh last month | 13916.1 | 5-CRACRm-CEP-01 | 0279 [branch#02] [A] KWh last month | 13892.8 | 6-DaHall 1-CEP-05 | [branch#002] [A] kWh last month | 1.1 | 7-DaHall 1-PDU-01 | [branch#002] [A] kWh last month | 0
4-CRACRm-CEP-01 | 0439 [branch#03] [A] KWh last month | 12.2 | 5-CRACRm-CEP-01 | 0439 [branch#03] [A] KWh last month | 18.6 | 6-DaHall 1-CEP-05 | [branch#003] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#003] [A] kWh last month | 349.5
4-CRACRm-CEP-01 | 0599 [branch#04] [A] KWh last month | 6705.5 | 5-CRACRm-CEP-01 | 0599 [branch#04] [A] KWh last month | 14183.9 | 6-DaHall 1-CEP-05 | [branch#004] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#004] [A] kWh last month | 0
4-CRACRm-CEP-02 | 0119 [branch#01] [A] KWh last month | 14935.3 | 5-CRACRm-CEP-02 | 0119 [branch#01] [A] KWh last month | 3333.4 | 6-DaHall 1-CEP-05 | [branch#005] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#005] [A] kWh last month | 753.8
4-CRACRm-CEP-02 | 0279 [branch#02] [A] KWh last month | 19.7 | 5-CRACRm-CEP-02 | 0279 [branch#02] [A] KWh last month | 19.4 | 6-DaHall 1-CEP-05 | [branch#006] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#006] [A] kWh last month | 0
4-CRACRm-CEP-02 | 0439 [branch#03] [A] KWh last month | 14790.7 | 5-CRACRm-CEP-02 | 0439 [branch#03] [A] KWh last month | 25973.8 | 6-DaHall 1-CEP-05 | [branch#007] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#007] [A] kWh last month | 950.5
4-CRACRm-CEP-02 | 0599 [branch#04] [A] KWh last month | 17.1 | 5-CRACRm-CEP-02 | 0599 [branch#04] [A] KWh last month | 15.3 | 6-DaHall 1-CEP-05 | [branch#008] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#008] [A] kWh last month | 269.9
4-DaHall 1-CEP-05 | 0119 [branch#01] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#001] [A] kWh last month | 27.1 | 6-DaHall 1-CEP-05 | [branch#009] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#009] [A] kWh last month | 950.1
4-DaHall 1-CEP-05 | 0279 [branch#02] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#002] [A] kWh last month | 54.2 | 6-DaHall 1-CEP-05 | [branch#010] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#010] [A] kWh last month | 341.9
4-DaHall 1-CEP-05 | 0439 [branch#03] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#003] [A] kWh last month | 70.7 | 6-DaHall 1-CEP-05 | [branch#011] [A] kWh last month | 3696.3 | 7-DaHall 1-PDU-01 | [branch#011] [A] kWh last month | 1005.9
4-DaHall 1-CEP-05 | 0599 [branch#04] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#004] [A] kWh last month | 8336.8 | 6-DaHall 1-CEP-05 | [branch#012] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#012] [A] kWh last month | 0
4-DaHall 1-CEP-05 | 0759 [branch#05] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#005] [A] kWh last month | 71 | 6-DaHall 1-CEP-05 | [branch#013] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#013] [A] kWh last month | 1044.8
4-DaHall 1-CEP-05 | 0919 [branch#06] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#006] [A] kWh last month | 8425.9 | 6-DaHall 1-CEP-05 | [branch#014] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#014] [A] kWh last month | 671.6
4-DaHall 1-CEP-05 | 1079 [branch#07] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#007] [A] kWh last month | 8211.4 | 6-DaHall 1-CEP-05 | [branch#015] [A] kWh last month | 1441.2 | 7-DaHall 1-PDU-01 | [branch#015] [A] kWh last month | 71.1
4-DaHall 1-CEP-05 | 1239 [branch#08] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#008] [A] kWh last month | 5815.1 | 6-DaHall 1-CEP-05 | [branch#016] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#016] [A] kWh last month | 335.5
4-DaHall 1-CEP-05 | 1399 [branch#09] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#009] [A] kWh last month | 88.2 | 6-DaHall 1-CEP-05 | [branch#017] [A] kWh last month | 1378.8 | 7-DaHall 1-PDU-01 | [branch#017] [A] kWh last month | 442
4-DaHall 1-CEP-05 | 1559 [branch#10] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#010] [A] kWh last month | 71.1 | 6-DaHall 1-PDU-01 | [branch#001] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#018] [A] kWh last month | 272
4-DaHall 1-CEP-05 | 1719 [branch#11] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#011] [A] kWh last month | 70.8 | 6-DaHall 1-PDU-01 | [branch#002] [A] kWh last month | 245.9 | 7-DaHall 1-PDU-01 | [branch#019] [A] kWh last month | 602.4
4-DaHall 1-CEP-05 | 1879 [branch#12] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#012] [A] kWh last month | 32.5 | 6-DaHall 1-PDU-01 | [branch#003] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#020] [A] kWh last month | 291.1
4-DaHall 1-PDU-01 | [branch#001] [A] kWh last month | 450.8 | 5-DaHall 1-CEP-05 | [branch#013] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#004] [A] kWh last month | 561.1 | 7-DaHall 1-PDU-01 | [branch#021] [A] kWh last month | 606.7
4-DaHall 1-PDU-01 | [branch#002] [A] kWh last month | 5920.3 | 5-DaHall 1-CEP-05 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#005] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#022] [A] kWh last month | 269.4
4-DaHall 1-PDU-01 | [branch#003] [A] kWh last month | 5395 | 5-DaHall 1-CEP-05 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#006] [A] kWh last month | 421.3 | 7-DaHall 1-PDU-01 | [branch#023] [A] kWh last month | 273.4
4-DaHall 1-PDU-01 | [branch#004] [A] kWh last month | 5765.4 | 5-DaHall 1-CEP-05 | [branch#016] [A] kWh last month | 1898.6 | 6-DaHall 1-PDU-01 | [branch#007] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#024] [A] kWh last month | 426.1
4-DaHall 1-PDU-01 | [branch#005] [A] kWh last month | 6731.3 | 5-DaHall 1-CEP-05 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#008] [A] kWh last month | 743.1 | 7-DaHall 1-PDU-01 | [branch#025] [A] kWh last month | 225.6
4-DaHall 1-PDU-01 | [branch#006] [A] kWh last month | 3598.1 | 5-DaHall 1-CEP-05 | [branch#018] [A] kWh last month | 1209.6 | 6-DaHall 1-PDU-01 | [branch#009] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#026] [A] kWh last month | 523.4
4-DaHall 1-PDU-01 | [branch#007] [A] kWh last month | 1852.3 | 5-DaHall 1-CEP-06 | 0119 [branch#01] [A] KWh last month | 72.8 | 6-DaHall 1-PDU-01 | [branch#010] [A] kWh last month | 1202.2 | 7-DaHall 1-PDU-01 | [branch#027] [A] kWh last month | 535.6
4-DaHall 1-PDU-01 | [branch#008] [A] kWh last month | 0 | 5-DaHall 1-CEP-06 | 0279 [branch#02] [A] KWh last month | 72.1 | 6-DaHall 1-PDU-01 | [branch#011] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#028] [A] kWh last month | 846
4-DaHall 1-PDU-01 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-CEP-06 | 0439 [branch#03] [A] KWh last month | 68.8 | 6-DaHall 1-PDU-01 | [branch#012] [A] kWh last month | 1209.7 | 7-DaHall 1-PDU-01 | [branch#029] [A] kWh last month | 0
4-DaHall 1-PDU-02 | [branch#001] [A] kWh last month | 227.7 | 5-DaHall 1-CEP-06 | 0599 [branch#04] [A] KWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#013] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#030] [A] kWh last month | 41.8
4-DaHall 1-PDU-02 | [branch#002] [A] kWh last month | 5510.8 | 5-DaHall 1-PDU-01 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#014] [A] kWh last month | 867.3 | 7-DaHall 1-PDU-01 | [branch#031] [A] kWh last month | 687.6
4-DaHall 1-PDU-02 | [branch#003] [A] kWh last month | 5102.3 | 5-DaHall 1-PDU-01 | [branch#055] [A] kWh last month | 33.9 | 6-DaHall 1-PDU-01 | [branch#015] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#032] [A] kWh last month | 291.8
4-DaHall 1-PDU-02 | [branch#004] [A] kWh last month | 5538.1 | 5-DaHall 1-PDU-01 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#016] [A] kWh last month | 882.4 | 7-DaHall 1-PDU-01 | [branch#033] [A] kWh last month | 1396.1
4-DaHall 1-PDU-02 | [branch#005] [A] kWh last month | 6686.9 | 5-DaHall 1-PDU-01 | [branch#056] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#017] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#034] [A] kWh last month | 0
4-DaHall 1-PDU-02 | [branch#006] [A] kWh last month | 1841.8 | 5-DaHall 1-PDU-01 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#018] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#035] [A] kWh last month | 1091.2
4-DaHall 1-PDU-02 | [branch#007] [A] kWh last month | 4472.4 | 5-DaHall 1-PDU-01 | [branch#057] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#019] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#036] [A] kWh last month | 0
4-DaHall 1-PDU-02 | [branch#008] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#020] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#037] [A] kWh last month | 0
4-DaHall 1-PDU-02 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#058] [A] kWh last month | 232.1 | 6-DaHall 1-PDU-01 | [branch#021] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#038] [A] kWh last month | 396.7
4-DaHall 1-PDU-03 | [branch#001] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#022] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#039] [A] kWh last month | 139.9
4-DaHall 1-PDU-03 | [branch#002] [A] kWh last month | 5187.4 | 5-DaHall 1-PDU-01 | [branch#059] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#023] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#040] [A] kWh last month | 482.4
4-DaHall 1-PDU-03 | [branch#003] [A] kWh last month | 4489.6 | 5-DaHall 1-PDU-01 | [branch#006] [A] kWh last month | 1973.1 | 6-DaHall 1-PDU-01 | [branch#024] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#041] [A] kWh last month | 128.2
4-DaHall 1-PDU-03 | [branch#004] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#060] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#025] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#042] [A] kWh last month | 493.8
4-DaHall 1-PDU-03 | [branch#005] [A] kWh last month | 1012.6 | 5-DaHall 1-PDU-01 | [branch#007] [A] kWh last month | 1730.2 | 6-DaHall 1-PDU-01 | [branch#026] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#043] [A] kWh last month | 0
4-DaHall 1-PDU-03 | [branch#006] [A] kWh last month | 1528.2 | 5-DaHall 1-PDU-01 | [branch#061] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#027] [A] kWh last month | 305.1 | 7-DaHall 1-PDU-01 | [branch#044] [A] kWh last month | 1065.9
4-DaHall 1-PDU-03 | [branch#007] [A] kWh last month | 4443.1 | 5-DaHall 1-PDU-01 | [branch#008] [A] kWh last month | 2058.1 | 6-DaHall 1-PDU-01 | [branch#028] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#045] [A] kWh last month | 0
4-DaHall 1-PDU-03 | [branch#008] [A] kWh last month | 2694.4 | 5-DaHall 1-PDU-01 | [branch#062] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#029] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#046] [A] kWh last month | 0
4-DaHall 1-PDU-03 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#009] [A] kWh last month | 326.6 | 6-DaHall 1-PDU-01 | [branch#030] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#047] [A] kWh last month | 0
4-DaHall 1-PDU-04 | [branch#001] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#063] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#031] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#048] [A] kWh last month | 357.1
4-DaHall 1-PDU-04 | [branch#002] [A] kWh last month | 6295.6 | 5-DaHall 1-PDU-01 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#032] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#049] [A] kWh last month | 0
4-DaHall 1-PDU-04 | [branch#003] [A] kWh last month | 4603.6 | 5-DaHall 1-PDU-01 | [branch#064] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#033] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#050] [A] kWh last month | 0
4-DaHall 1-PDU-04 | [branch#004] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#011] [A] kWh last month | 127.6 | 6-DaHall 1-PDU-01 | [branch#034] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#051] [A] kWh last month | 0
4-DaHall 1-PDU-04 | [branch#005] [A] kWh last month | 1518.2 | 5-DaHall 1-PDU-01 | [branch#065] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#035] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#052] [A] kWh last month | 0
4-DaHall 1-PDU-04 | [branch#006] [A] kWh last month | 2259.6 | 5-DaHall 1-PDU-01 | [branch#012] [A] kWh last month | 192 | 6-DaHall 1-PDU-01 | [branch#036] [A] kWh last month | 134.8 | 7-DaHall 1-PDU-01 | [branch#053] [A] kWh last month | 0
4-DaHall 1-PDU-04 | [branch#007] [A] kWh last month | 3121.7 | 5-DaHall 1-PDU-01 | [branch#066] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#037] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#054] [A] kWh last month | 43.3
4-DaHall 1-PDU-04 | [branch#008] [A] kWh last month | 3301 | 5-DaHall 1-PDU-01 | [branch#013] [A] kWh last month | 233.9 | 6-DaHall 1-PDU-01 | [branch#038] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#001] [A] kWh last month | 0
4-DaHall 1-PDU-04 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#067] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#039] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#002] [A] kWh last month | 0
4-DaHall 1-PDU-05 | [branch#001] [A] kWh last month | 1414.2 | 5-DaHall 1-PDU-01 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#040] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#003] [A] kWh last month | 688.7
4-DaHall 1-PDU-05 | [branch#002] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#068] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#041] [A] kWh last month | 120.7 | 7-DaHall 1-PDU-02 | [branch#004] [A] kWh last month | 0
4-DaHall 1-PDU-05 | [branch#003] [A] kWh last month | 1150.2 | 5-DaHall 1-PDU-01 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#042] [A] kWh last month | 634 | 7-DaHall 1-PDU-02 | [branch#005] [A] kWh last month | 0
4-DaHall 1-PDU-05 | [branch#004] [A] kWh last month | 1070.4 | 5-DaHall 1-PDU-01 | [branch#069] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#043] [A] kWh last month | 585.4 | 7-DaHall 1-PDU-02 | [branch#006] [A] kWh last month | 0
4-DaHall 1-PDU-05 | [branch#005] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#044] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#007] [A] kWh last month | 910.4
4-DaHall 1-PDU-05 | [branch#006] [A] kWh last month | 1771.4 | 5-DaHall 1-PDU-01 | [branch#070] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#045] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#008] [A] kWh last month | 0
4-DaHall 1-PDU-05 | [branch#007] [A] kWh last month | 979 | 5-DaHall 1-PDU-01 | [branch#017] [A] kWh last month | 1821.6 | 6-DaHall 1-PDU-01 | [branch#046] [A] kWh last month | 77.5 | 7-DaHall 1-PDU-02 | [branch#009] [A] kWh last month | 946.7
4-DaHall 1-PDU-05 | [branch#008] [A] kWh last month | 1997.5 | 5-DaHall 1-PDU-01 | [branch#071] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#047] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#010] [A] kWh last month | 516.1
4-DaHall 1-PDU-05 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#018] [A] kWh last month | 1603 | 6-DaHall 1-PDU-01 | [branch#048] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#011] [A] kWh last month | 808.9
4-DaHall 1-PDU-05 | [branch#010] [A] kWh last month | 4916.7 | 5-DaHall 1-PDU-01 | [branch#072] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#049] [A] kWh last month | 1274.5 | 7-DaHall 1-PDU-02 | [branch#012] [A] kWh last month | 0
4-DaHall 1-PDU-05 | [branch#011] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#019] [A] kWh last month | 1917 | 6-DaHall 1-PDU-01 | [branch#050] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#013] [A] kWh last month | 814.4
4-DaHall 1-PDU-05 | [branch#012] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#073] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#001] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#014] [A] kWh last month | 365.5
4-DaHall 1-PDU-06 | [branch#001] [A] kWh last month | 1654 | 5-DaHall 1-PDU-01 | [branch#020] [A] kWh last month | 1567.9 | 6-DaHall 1-PDU-02 | [branch#002] [A] kWh last month | 174.5 | 7-DaHall 1-PDU-02 | [branch#015] [A] kWh last month | 96.5
4-DaHall 1-PDU-06 | [branch#002] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#074] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#003] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#016] [A] kWh last month | 410.3
4-DaHall 1-PDU-06 | [branch#003] [A] kWh last month | 1397.2 | 5-DaHall 1-PDU-01 | [branch#021] [A] kWh last month | 1813.7 | 6-DaHall 1-PDU-02 | [branch#004] [A] kWh last month | 418.2 | 7-DaHall 1-PDU-02 | [branch#017] [A] kWh last month | 553.1
4-DaHall 1-PDU-06 | [branch#004] [A] kWh last month | 1030.5 | 5-DaHall 1-PDU-01 | [branch#075] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#005] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#018] [A] kWh last month | 269.3
4-DaHall 1-PDU-06 | [branch#005] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#006] [A] kWh last month | 748.6 | 7-DaHall 1-PDU-02 | [branch#019] [A] kWh last month | 1380.9
4-DaHall 1-PDU-06 | [branch#006] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#076] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#007] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#020] [A] kWh last month | 313.9
4-DaHall 1-PDU-06 | [branch#007] [A] kWh last month | 1262.5 | 5-DaHall 1-PDU-01 | [branch#023] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#008] [A] kWh last month | 456.2 | 7-DaHall 1-PDU-02 | [branch#021] [A] kWh last month | 626.8
4-DaHall 1-PDU-06 | [branch#008] [A] kWh last month | 2082.2 | 5-DaHall 1-PDU-01 | [branch#077] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#009] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#022] [A] kWh last month | 307.8
4-DaHall 1-PDU-06 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#010] [A] kWh last month | 1157.6 | 7-DaHall 1-PDU-02 | [branch#023] [A] kWh last month | 397.2
4-DaHall 1-PDU-06 | [branch#010] [A] kWh last month | 6001.7 | 5-DaHall 1-PDU-01 | [branch#078] [A] kWh last month | 80.8 | 6-DaHall 1-PDU-02 | [branch#011] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#024] [A] kWh last month | 343
4-DaHall 1-PDU-06 | [branch#011] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#012] [A] kWh last month | 1560.8 | 7-DaHall 1-PDU-02 | [branch#025] [A] kWh last month | 268.3
4-DaHall 1-PDU-06 | [branch#012] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#079] [A] kWh last month | 278.1 | 6-DaHall 1-PDU-02 | [branch#013] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#026] [A] kWh last month | 558.8
4-DaHall 1-PDU-07 | [branch#001] [A] kWh last month | 3182.9 | 5-DaHall 1-PDU-01 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#014] [A] kWh last month | 1175.7 | 7-DaHall 1-PDU-02 | [branch#027] [A] kWh last month | 599.3
4-DaHall 1-PDU-07 | [branch#002] [A] kWh last month | 5316.5 | 5-DaHall 1-PDU-01 | [branch#080] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#015] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#028] [A] kWh last month | 884.5
4-DaHall 1-PDU-07 | [branch#003] [A] kWh last month | 801.5 | 5-DaHall 1-PDU-02 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#016] [A] kWh last month | 818 | 7-DaHall 1-PDU-02 | [branch#029] [A] kWh last month | 278.9
4-DaHall 1-PDU-07 | [branch#004] [A] kWh last month | 1565.4 | 5-DaHall 1-PDU-02 | [branch#055] [A] kWh last month | 33.8 | 6-DaHall 1-PDU-02 | [branch#017] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#030] [A] kWh last month | 57.1
4-DaHall 1-PDU-07 | [branch#005] [A] kWh last month | 892 | 5-DaHall 1-PDU-02 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#018] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#031] [A] kWh last month | 527.2
4-DaHall 1-PDU-07 | [branch#006] [A] kWh last month | 2280.3 | 5-DaHall 1-PDU-02 | [branch#056] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#019] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#032] [A] kWh last month | 246.1
4-DaHall 1-PDU-07 | [branch#007] [A] kWh last month | 1920.6 | 5-DaHall 1-PDU-02 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#020] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#033] [A] kWh last month | 1354
4-DaHall 1-PDU-07 | [branch#008] [A] kWh last month | 5348.9 | 5-DaHall 1-PDU-02 | [branch#057] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#021] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#034] [A] kWh last month | 0
4-DaHall 1-PDU-07 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#022] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#035] [A] kWh last month | 1054.4
4-DaHall 1-PDU-07 | [branch#010] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#058] [A] kWh last month | 194.1 | 6-DaHall 1-PDU-02 | [branch#023] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#036] [A] kWh last month | 0
4-DaHall 1-PDU-07 | [branch#011] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#024] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#037] [A] kWh last month | 0
4-DaHall 1-PDU-07 | [branch#012] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#059] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#025] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#038] [A] kWh last month | 551.5
4-DaHall 1-PDU-08 | [branch#001] [A] kWh last month | 3569.5 | 5-DaHall 1-PDU-02 | [branch#006] [A] kWh last month | 1656 | 6-DaHall 1-PDU-02 | [branch#026] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#039] [A] kWh last month | 262.4
4-DaHall 1-PDU-08 | [branch#002] [A] kWh last month | 5247.1 | 5-DaHall 1-PDU-02 | [branch#060] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#027] [A] kWh last month | 180.4 | 7-DaHall 1-PDU-02 | [branch#040] [A] kWh last month | 446.3
4-DaHall 1-PDU-08 | [branch#003] [A] kWh last month | 823.9 | 5-DaHall 1-PDU-02 | [branch#007] [A] kWh last month | 1978.2 | 6-DaHall 1-PDU-02 | [branch#028] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#041] [A] kWh last month | 0
4-DaHall 1-PDU-08 | [branch#004] [A] kWh last month | 1483.1 | 5-DaHall 1-PDU-02 | [branch#061] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#029] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#042] [A] kWh last month | 656.8
4-DaHall 1-PDU-08 | [branch#005] [A] kWh last month | 1134.6 | 5-DaHall 1-PDU-02 | [branch#008] [A] kWh last month | 1697.8 | 6-DaHall 1-PDU-02 | [branch#030] [A] kWh last month | 1256.3 | 7-DaHall 1-PDU-02 | [branch#043] [A] kWh last month | 0
4-DaHall 1-PDU-08 | [branch#006] [A] kWh last month | 1711.6 | 5-DaHall 1-PDU-02 | [branch#062] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#031] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#044] [A] kWh last month | 317.7
4-DaHall 1-PDU-08 | [branch#007] [A] kWh last month | 1809.7 | 5-DaHall 1-PDU-02 | [branch#009] [A] kWh last month | 307 | 6-DaHall 1-PDU-02 | [branch#032] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#045] [A] kWh last month | 0
4-DaHall 1-PDU-08 | [branch#008] [A] kWh last month | 3990.1 | 5-DaHall 1-PDU-02 | [branch#063] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#033] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#046] [A] kWh last month | 0
4-DaHall 1-PDU-08 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#010] [A] kWh last month | 309.3 | 6-DaHall 1-PDU-02 | [branch#034] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#047] [A] kWh last month | 0
4-DaHall 1-PDU-08 | [branch#010] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#064] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#035] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#048] [A] kWh last month | 421.2
4-DaHall 1-PDU-08 | [branch#011] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#036] [A] kWh last month | 174.6 | 7-DaHall 1-PDU-02 | [branch#049] [A] kWh last month | 103.6
4-DaHall 1-PDU-08 | [branch#012] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#065] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#037] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#050] [A] kWh last month | 344.4
4-DaHall 1-PDU-09 | [branch#001] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#012] [A] kWh last month | 226.5 | 6-DaHall 1-PDU-02 | [branch#038] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#051] [A] kWh last month | 74
4-DaHall 1-PDU-09 | [branch#002] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#066] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#039] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#052] [A] kWh last month | 0
4-DaHall 1-PDU-09 | [branch#003] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#013] [A] kWh last month | 199.1 | 6-DaHall 1-PDU-02 | [branch#040] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#053] [A] kWh last month | 27.5
4-DaHall 1-PDU-10 | [branch#001] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#067] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#041] [A] kWh last month | 87.3 | 7-DaHall 1-PDU-02 | [branch#054] [A] kWh last month | 0
4-DaHall 1-PDU-10 | [branch#002] [A] kWh last month | 13236.5 | 5-DaHall 1-PDU-02 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#042] [A] kWh last month | 643.1 | 7-DaHall 1-PDU-03 | [branch#001] [A] kWh last month | 8634.2
4-DaHall 1-PDU-10 | [branch#003] [A] kWh last month | 6847.3 | 5-DaHall 1-PDU-02 | [branch#068] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#043] [A] kWh last month | 585.4 | 7-DaHall 1-PDU-03 | [branch#002] [A] kWh last month | 1924.8
4-DaHall 1-PDU-11 | [branch#001] [A] kWh last month | 85.9 | 5-DaHall 1-PDU-02 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#044] [A] kWh last month | 0 | 7-DaHall 1-PDU-03 | [branch#003] [A] kWh last month | 2889.1
4-DaHall 1-PDU-11 | [branch#002] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#069] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#045] [A] kWh last month | 0 | 7-DaHall 1-PDU-03 | [branch#004] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#003] [A] kWh last month | 0.1 | 5-DaHall 1-PDU-02 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#046] [A] kWh last month | 0 | 7-DaHall 1-PDU-03 | [branch#005] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#004] [A] kWh last month | 3.5 | 5-DaHall 1-PDU-02 | [branch#070] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#047] [A] kWh last month | 0 | 7-DaHall 1-PDU-03 | [branch#006] [A] kWh last month | 23753.8
4-DaHall 1-PDU-11 | [branch#005] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#017] [A] kWh last month | 1879.7 | 6-DaHall 1-PDU-02 | [branch#048] [A] kWh last month | 0 | 7-DaHall 1-PDU-03 | [branch#007] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#006] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#071] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#049] [A] kWh last month | 0 | 7-DaHall 1-PDU-03 | [branch#008] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#007] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#018] [A] kWh last month | 1896.6 | 6-DaHall 1-PDU-02 | [branch#050] [A] kWh last month | 0 | 7-DaHall 1-PDU-03 | [branch#009] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#008] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#072] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#001] [A] kWh last month | 834.6 | 7-DaHall 1-PDU-03 | [branch#010] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#019] [A] kWh last month | 1591.9 | 6-DaHall 1-PDU-03 | [branch#002] [A] kWh last month | 0 | 7-DaHall 1-PDU-04 | [branch#001] [A] kWh last month | 20745.1
4-DaHall 1-PDU-11 | [branch#010] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#073] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#003] [A] kWh last month | 702.9 | 7-DaHall 1-PDU-04 | [branch#002] [A] kWh last month | 10686
4-DaHall 1-PDU-11 | [branch#011] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#020] [A] kWh last month | 1877.2 | 6-DaHall 1-PDU-03 | [branch#004] [A] kWh last month | 0 | 7-DaHall 1-PDU-04 | [branch#003] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#012] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#074] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#005] [A] kWh last month | 133.1 | 7-DaHall 1-PDU-04 | [branch#004] [A] kWh last month | 3338.2
4-DaHall 1-PDU-11 | [branch#013] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#021] [A] kWh last month | 1451 | 6-DaHall 1-PDU-03 | [branch#006] [A] kWh last month | 0 | 7-DaHall 1-PDU-04 | [branch#005] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#014] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#075] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#007] [A] kWh last month | 601.1 | 7-DaHall 1-PDU-04 | [branch#006] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#015] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#008] [A] kWh last month | 0 | 7-DaHall 1-PDU-04 | [branch#007] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#016] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#076] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#009] [A] kWh last month | 470.6 | 7-DaHall 1-PDU-04 | [branch#008] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#017] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#023] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#010] [A] kWh last month | 0 | 7-DaHall 1-PDU-04 | [branch#009] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#018] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#077] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#011] [A] kWh last month | 524.4 | 7-DaHall 1-PDU-04 | [branch#010] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#019] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#078] [A] kWh last month | 86.8 | 6-DaHall 1-PDU-03 | [branch#012] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#001] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#020] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#013] [A] kWh last month | 695.8 | 7-DaHall 1-RPP-01 | [branch#002] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#021] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#079] [A] kWh last month | 179.7 | 6-DaHall 1-PDU-03 | [branch#014] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#003] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#022] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#015] [A] kWh last month | 609.6 | 7-DaHall 1-RPP-01 | [branch#004] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#023] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#080] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#016] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#005] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#024] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#017] [A] kWh last month | 298.4 | 7-DaHall 1-RPP-01 | [branch#006] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#025] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#018] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#007] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#026] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#055] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#019] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#008] [A] kWh last month | 342.7
4-DaHall 1-PDU-11 | [branch#027] [A] kWh last month | 1.4 | 5-DaHall 1-PDU-03 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#020] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#009] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#028] [A] kWh last month | 1.4 | 5-DaHall 1-PDU-03 | [branch#056] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#021] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#010] [A] kWh last month | 241.1
4-DaHall 1-PDU-11 | [branch#029] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#022] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#011] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#030] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#057] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#023] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#012] [A] kWh last month | 602.3
4-DaHall 1-PDU-11 | [branch#031] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#024] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#013] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#032] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#058] [A] kWh last month | 87.7 | 6-DaHall 1-PDU-03 | [branch#025] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#014] [A] kWh last month | 996.5
4-DaHall 1-PDU-11 | [branch#033] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#026] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#015] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#034] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#059] [A] kWh last month | 227.4 | 6-DaHall 1-PDU-03 | [branch#027] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#016] [A] kWh last month | 232
4-DaHall 1-PDU-11 | [branch#035] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#006] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#028] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#017] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#036] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#060] [A] kWh last month | 563.6 | 6-DaHall 1-PDU-03 | [branch#029] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#018] [A] kWh last month | 212.4
4-DaHall 1-PDU-11 | [branch#037] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#030] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#019] [A] kWh last month | 111.9
4-DaHall 1-PDU-11 | [branch#038] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#061] [A] kWh last month | 278 | 6-DaHall 1-PDU-03 | [branch#031] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#020] [A] kWh last month | 231.6
4-DaHall 1-PDU-11 | [branch#039] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#032] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#021] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#040] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#062] [A] kWh last month | 45.6 | 6-DaHall 1-PDU-03 | [branch#033] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#022] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#041] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#034] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#023] [A] kWh last month | 203.2
4-DaHall 1-PDU-11 | [branch#042] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#063] [A] kWh last month | 632.2 | 6-DaHall 1-PDU-03 | [branch#035] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#024] [A] kWh last month | 0
4-DaHall 1-PDU-11 | [branch#043] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#036] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#025] [A] kWh last month | 242.7
4-DaHall 1-PDU-11 | [branch#044] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#064] [A] kWh last month | 106.1 | 6-DaHall 1-PDU-03 | [branch#037] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#026] [A] kWh last month | 541.3
4-DaHall 1-PDU-11 | [branch#045] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#038] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#027] [A] kWh last month | 410.6
4-DaHall 1-PDU-11 | [branch#046] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#065] [A] kWh last month | 415.8 | 6-DaHall 1-PDU-03 | [branch#039] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#028] [A] kWh last month | 131.9
4-DaHall 1-PDU-11 | [branch#047] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#040] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#029] [A] kWh last month | 474.6
4-DaHall 1-PDU-11 | [branch#048] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#066] [A] kWh last month | 392 | 6-DaHall 1-PDU-03 | [branch#041] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#030] [A] kWh last month | 504.8
4-DaHall 1-PDU-11 | [branch#049] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#013] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#042] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#031] [A] kWh last month | 589.4
4-DaHall 1-PDU-11 | [branch#050] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#067] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#043] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#032] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#001] [A] kWh last month | 68.5 | 5-DaHall 1-PDU-03 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#044] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#033] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#002] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#068] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#045] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#034] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#003] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#046] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#035] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#004] [A] kWh last month | 15.5 | 5-DaHall 1-PDU-03 | [branch#069] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#047] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#036] [A] kWh last month | 527.9
4-DaHall 1-PDU-12 | [branch#005] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#048] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#037] [A] kWh last month | 922.1
4-DaHall 1-PDU-12 | [branch#006] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#070] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#049] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#038] [A] kWh last month | 321.6
4-DaHall 1-PDU-12 | [branch#007] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#050] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#039] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#008] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#071] [A] kWh last month | 256.8 | 6-DaHall 1-PDU-04 | [branch#001] [A] kWh last month | 667.8 | 7-DaHall 1-RPP-01 | [branch#040] [A] kWh last month | 757.2
4-DaHall 1-PDU-12 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#002] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#001] [A] kWh last month | 129.4
4-DaHall 1-PDU-12 | [branch#010] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#072] [A] kWh last month | 231.2 | 6-DaHall 1-PDU-04 | [branch#003] [A] kWh last month | 807.3 | 7-DaHall 1-RPP-02 | [branch#002] [A] kWh last month | 34.1
4-DaHall 1-PDU-12 | [branch#011] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#004] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#003] [A] kWh last month | 70.9
4-DaHall 1-PDU-12 | [branch#012] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#073] [A] kWh last month | 234.1 | 6-DaHall 1-PDU-04 | [branch#005] [A] kWh last month | 194.5 | 7-DaHall 1-RPP-02 | [branch#004] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#013] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#020] [A] kWh last month | 479 | 6-DaHall 1-PDU-04 | [branch#006] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#005] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#014] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#074] [A] kWh last month | 260.8 | 6-DaHall 1-PDU-04 | [branch#007] [A] kWh last month | 645.1 | 7-DaHall 1-RPP-02 | [branch#006] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#015] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#021] [A] kWh last month | 265.9 | 6-DaHall 1-PDU-04 | [branch#008] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#007] [A] kWh last month | 153.7
4-DaHall 1-PDU-12 | [branch#016] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#075] [A] kWh last month | 171.1 | 6-DaHall 1-PDU-04 | [branch#009] [A] kWh last month | 550.6 | 7-DaHall 1-RPP-02 | [branch#008] [A] kWh last month | 903.6
4-DaHall 1-PDU-12 | [branch#017] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#010] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#009] [A] kWh last month | 186.7
4-DaHall 1-PDU-12 | [branch#018] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#076] [A] kWh last month | 216.1 | 6-DaHall 1-PDU-04 | [branch#011] [A] kWh last month | 625.6 | 7-DaHall 1-RPP-02 | [branch#010] [A] kWh last month | 76.3
4-DaHall 1-PDU-12 | [branch#019] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#023] [A] kWh last month | 377.6 | 6-DaHall 1-PDU-04 | [branch#012] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#011] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#020] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#077] [A] kWh last month | 451.5 | 6-DaHall 1-PDU-04 | [branch#013] [A] kWh last month | 464 | 7-DaHall 1-RPP-02 | [branch#012] [A] kWh last month | 622.5
4-DaHall 1-PDU-12 | [branch#021] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#014] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#013] [A] kWh last month | 394
4-DaHall 1-PDU-12 | [branch#022] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#078] [A] kWh last month | 442.2 | 6-DaHall 1-PDU-04 | [branch#015] [A] kWh last month | 558.8 | 7-DaHall 1-RPP-02 | [branch#014] [A] kWh last month | 2196.2
4-DaHall 1-PDU-12 | [branch#023] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#025] [A] kWh last month | 616.5 | 6-DaHall 1-PDU-04 | [branch#016] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#015] [A] kWh last month | 272
4-DaHall 1-PDU-12 | [branch#024] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#079] [A] kWh last month | 578.6 | 6-DaHall 1-PDU-04 | [branch#017] [A] kWh last month | 265.4 | 7-DaHall 1-RPP-02 | [branch#016] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#025] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#026] [A] kWh last month | 917.8 | 6-DaHall 1-PDU-04 | [branch#018] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#017] [A] kWh last month | 434.2
4-DaHall 1-PDU-12 | [branch#026] [A] kWh last month | 0 | 5-DaHall 1-PDU-03 | [branch#080] [A] kWh last month | 644.5 | 6-DaHall 1-PDU-04 | [branch#019] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#018] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#027] [A] kWh last month | 18.1 | 5-DaHall 1-PDU-04 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#020] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#019] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#028] [A] kWh last month | 11 | 5-DaHall 1-PDU-04 | [branch#055] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#021] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#020] [A] kWh last month | 87.6
4-DaHall 1-PDU-12 | [branch#029] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#022] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#021] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#030] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#056] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#023] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#022] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#031] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#024] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#023] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#032] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#057] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#025] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#024] [A] kWh last month | 217.9
4-DaHall 1-PDU-12 | [branch#033] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#026] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#025] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#034] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#058] [A] kWh last month | 88.7 | 6-DaHall 1-PDU-04 | [branch#027] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#026] [A] kWh last month | 25.2
4-DaHall 1-PDU-12 | [branch#035] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#028] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#027] [A] kWh last month | 900.8
4-DaHall 1-PDU-12 | [branch#036] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#059] [A] kWh last month | 275 | 6-DaHall 1-PDU-04 | [branch#029] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#028] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#037] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#006] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#030] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#029] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#038] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#060] [A] kWh last month | 559.2 | 6-DaHall 1-PDU-04 | [branch#031] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#030] [A] kWh last month | 268.5
4-DaHall 1-PDU-12 | [branch#039] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#032] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#031] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#040] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#061] [A] kWh last month | 283 | 6-DaHall 1-PDU-04 | [branch#033] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#032] [A] kWh last month | 546.4
4-DaHall 1-PDU-12 | [branch#041] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#034] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#033] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#042] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#062] [A] kWh last month | 97.6 | 6-DaHall 1-PDU-04 | [branch#035] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#034] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#043] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#036] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#035] [A] kWh last month | 298.3
4-DaHall 1-PDU-12 | [branch#044] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#063] [A] kWh last month | 621 | 6-DaHall 1-PDU-04 | [branch#037] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#036] [A] kWh last month | 1098.2
4-DaHall 1-PDU-12 | [branch#045] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#038] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#037] [A] kWh last month | 670.1
4-DaHall 1-PDU-12 | [branch#046] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#064] [A] kWh last month | 108 | 6-DaHall 1-PDU-04 | [branch#039] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#038] [A] kWh last month | 772.1
4-DaHall 1-PDU-12 | [branch#047] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#040] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#039] [A] kWh last month | 291.6
4-DaHall 1-PDU-12 | [branch#048] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#065] [A] kWh last month | 272.4 | 6-DaHall 1-PDU-04 | [branch#041] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#040] [A] kWh last month | 0
4-DaHall 1-PDU-12 | [branch#049] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#042] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#001] [A] kWh last month | 157
4-DaHall 1-PDU-12 | [branch#050] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#066] [A] kWh last month | 386.6 | 6-DaHall 1-PDU-04 | [branch#043] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#002] [A] kWh last month | 130.6
4-DaHall 1-PDU-13 | [branch#001] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#013] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#044] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#003] [A] kWh last month | 393.2
4-DaHall 1-PDU-13 | [branch#002] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#067] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#045] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#004] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#003] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#046] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#005] [A] kWh last month | 505.5
4-DaHall 1-PDU-13 | [branch#004] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#068] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#047] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#006] [A] kWh last month | 242.5
4-DaHall 1-PDU-13 | [branch#005] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#048] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#007] [A] kWh last month | 398.7
4-DaHall 1-PDU-13 | [branch#006] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#069] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#049] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#008] [A] kWh last month | 303.2
4-DaHall 1-PDU-13 | [branch#007] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#050] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#009] [A] kWh last month | 407.2
4-DaHall 1-PDU-13 | [branch#008] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#070] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#001] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#010] [A] kWh last month | 355
4-DaHall 1-PDU-13 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#002] [A] kWh last month | 1875.7 | 7-DaHall 1-RPP-04 | [branch#001] [A] kWh last month | 138.4
4-DaHall 1-PDU-13 | [branch#010] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#071] [A] kWh last month | 23.1 | 6-DaHall 1-PDU-05 | [branch#003] [A] kWh last month | 0 | 7-DaHall 1-RPP-04 | [branch#002] [A] kWh last month | 257.7
4-DaHall 1-PDU-13 | [branch#011] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#004] [A] kWh last month | 780.1 | 7-DaHall 1-RPP-04 | [branch#003] [A] kWh last month | 504.2
4-DaHall 1-PDU-13 | [branch#012] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#072] [A] kWh last month | 16.1 | 6-DaHall 1-PDU-05 | [branch#005] [A] kWh last month | 0 | 7-DaHall 1-RPP-04 | [branch#004] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#013] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#073] [A] kWh last month | 253.9 | 6-DaHall 1-PDU-05 | [branch#006] [A] kWh last month | 96.8 | 7-DaHall 1-RPP-04 | [branch#005] [A] kWh last month | 697.7
4-DaHall 1-PDU-13 | [branch#014] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#007] [A] kWh last month | 0 | 7-DaHall 1-RPP-04 | [branch#006] [A] kWh last month | 179
4-DaHall 1-PDU-13 | [branch#015] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#020] [A] kWh last month | 598.4 | 6-DaHall 1-PDU-05 | [branch#008] [A] kWh last month | 395.4 | 7-DaHall 1-RPP-04 | [branch#007] [A] kWh last month | 635.8
4-DaHall 1-PDU-13 | [branch#016] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#074] [A] kWh last month | 301.3 | 6-DaHall 1-PDU-05 | [branch#009] [A] kWh last month | 0 | 7-DaHall 1-RPP-04 | [branch#008] [A] kWh last month | 296.7
4-DaHall 1-PDU-13 | [branch#017] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#075] [A] kWh last month | 186.6 | 6-DaHall 1-PDU-05 | [branch#010] [A] kWh last month | 131.5 | 7-DaHall 1-RPP-04 | [branch#009] [A] kWh last month | 243.8
4-DaHall 1-PDU-13 | [branch#018] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#021] [A] kWh last month | 156.4 | 6-DaHall 1-PDU-05 | [branch#011] [A] kWh last month | 176.8 | 7-DaHall 1-RPP-04 | [branch#010] [A] kWh last month | 383.1
4-DaHall 1-PDU-13 | [branch#019] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#012] [A] kWh last month | 212
4-DaHall 1-PDU-13 | [branch#020] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#076] [A] kWh last month | 182.8 | 6-DaHall 1-PDU-05 | [branch#013] [A] kWh last month | 215.8
4-DaHall 1-PDU-13 | [branch#021] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#077] [A] kWh last month | 338.1 | 6-DaHall 1-PDU-05 | [branch#014] [A] kWh last month | 779.2
4-DaHall 1-PDU-13 | [branch#022] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#023] [A] kWh last month | 388.7 | 6-DaHall 1-PDU-05 | [branch#015] [A] kWh last month | 503.2
4-DaHall 1-PDU-13 | [branch#023] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#016] [A] kWh last month | 487.3
4-DaHall 1-PDU-13 | [branch#024] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#078] [A] kWh last month | 338.2 | 6-DaHall 1-PDU-05 | [branch#017] [A] kWh last month | 127.6
4-DaHall 1-PDU-13 | [branch#025] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#079] [A] kWh last month | 489.7 | 6-DaHall 1-PDU-05 | [branch#018] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#026] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#025] [A] kWh last month | 656.9 | 6-DaHall 1-PDU-05 | [branch#019] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#027] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#026] [A] kWh last month | 878.5 | 6-DaHall 1-PDU-05 | [branch#020] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#028] [A] kWh last month | 0 | 5-DaHall 1-PDU-04 | [branch#080] [A] kWh last month | 623.3 | 6-DaHall 1-PDU-05 | [branch#021] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#029] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#022] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#030] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#023] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#031] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#024] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#032] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#025] [A] kWh last month | 587.4
4-DaHall 1-PDU-13 | [branch#033] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#026] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#034] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#006] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#027] [A] kWh last month | 612.2
4-DaHall 1-PDU-13 | [branch#035] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#028] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#036] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#029] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#037] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#030] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#038] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#031] [A] kWh last month | 251
4-DaHall 1-PDU-13 | [branch#039] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#032] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#040] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#033] [A] kWh last month | 146.7
4-DaHall 1-PDU-13 | [branch#041] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#013] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#034] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#042] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#035] [A] kWh last month | 88.2
4-DaHall 1-PDU-13 | [branch#043] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#036] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#044] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#037] [A] kWh last month | 528.8
4-DaHall 1-PDU-13 | [branch#045] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#038] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#046] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#039] [A] kWh last month | 327.6
4-DaHall 1-PDU-13 | [branch#047] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#040] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#048] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#020] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#041] [A] kWh last month | 207.8
4-DaHall 1-PDU-13 | [branch#049] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#021] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#042] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#050] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#043] [A] kWh last month | 867.9
4-DaHall 1-PDU-13 | [branch#051] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#023] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#044] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#052] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#045] [A] kWh last month | 722.7
4-DaHall 1-PDU-13 | [branch#053] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#046] [A] kWh last month | 0
4-DaHall 1-PDU-13 | [branch#054] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#047] [A] kWh last month | 584.9
4-DaHall 1-PDU-14 | [branch#001] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#027] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#048] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#002] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#028] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#049] [A] kWh last month | 1242.3
4-DaHall 1-PDU-14 | [branch#003] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#029] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#050] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#004] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#030] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#051] [A] kWh last month | 554.3
4-DaHall 1-PDU-14 | [branch#005] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#031] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#052] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#006] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#032] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#053] [A] kWh last month | 711.2
4-DaHall 1-PDU-14 | [branch#007] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#033] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#054] [A] kWh last month | 619.3
4-DaHall 1-PDU-14 | [branch#008] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#034] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#001] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#035] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#002] [A] kWh last month | 1692.2
4-DaHall 1-PDU-14 | [branch#010] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#036] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#003] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#011] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#037] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#004] [A] kWh last month | 629.9
4-DaHall 1-PDU-14 | [branch#012] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#038] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#005] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#013] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#039] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#006] [A] kWh last month | 92.6
4-DaHall 1-PDU-14 | [branch#014] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#040] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#007] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#015] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#041] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#008] [A] kWh last month | 530.7
4-DaHall 1-PDU-14 | [branch#016] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#042] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#009] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#017] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#043] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#010] [A] kWh last month | 72.3
4-DaHall 1-PDU-14 | [branch#018] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#044] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#011] [A] kWh last month | 194.8
4-DaHall 1-PDU-14 | [branch#019] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#045] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#012] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#020] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#046] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#013] [A] kWh last month | 438.7
4-DaHall 1-PDU-14 | [branch#021] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#047] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#014] [A] kWh last month | 450.8
4-DaHall 1-PDU-14 | [branch#022] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#048] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#015] [A] kWh last month | 446.9
4-DaHall 1-PDU-14 | [branch#023] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#049] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#016] [A] kWh last month | 605.1
4-DaHall 1-PDU-14 | [branch#024] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#050] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#017] [A] kWh last month | 121
4-DaHall 1-PDU-14 | [branch#025] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#051] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#018] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#026] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#052] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#019] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#027] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#053] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#020] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#028] [A] kWh last month | 0 | 5-DaHall 1-PDU-05 | [branch#054] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#021] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#029] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#022] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#030] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#023] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#031] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#024] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#032] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#025] [A] kWh last month | 696.3
4-DaHall 1-PDU-14 | [branch#033] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#026] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#034] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#006] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#027] [A] kWh last month | 506.7
4-DaHall 1-PDU-14 | [branch#035] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#028] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#036] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#029] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#037] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#030] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#038] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#031] [A] kWh last month | 45.4
4-DaHall 1-PDU-14 | [branch#039] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#032] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#040] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#033] [A] kWh last month | 145.5
4-DaHall 1-PDU-14 | [branch#041] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#013] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#034] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#042] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#035] [A] kWh last month | 44.7
4-DaHall 1-PDU-14 | [branch#043] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#036] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#044] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#037] [A] kWh last month | 539.7
4-DaHall 1-PDU-14 | [branch#045] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#038] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#046] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#039] [A] kWh last month | 294.5
4-DaHall 1-PDU-14 | [branch#047] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#040] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#048] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#020] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#041] [A] kWh last month | 127.7
4-DaHall 1-PDU-14 | [branch#049] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#021] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#042] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#050] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#043] [A] kWh last month | 755.7
4-DaHall 1-PDU-14 | [branch#051] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#023] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#044] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#052] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#045] [A] kWh last month | 753.7
4-DaHall 1-PDU-14 | [branch#053] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#046] [A] kWh last month | 0
4-DaHall 1-PDU-14 | [branch#054] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#047] [A] kWh last month | 534.2
4-DaHall 1-RPP-01 | [branch#001] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#027] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#048] [A] kWh last month | 0
4-DaHall 1-RPP-01 | [branch#002] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#028] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#049] [A] kWh last month | 194.9
4-DaHall 1-RPP-01 | [branch#003] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#029] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#050] [A] kWh last month | 0
4-DaHall 1-RPP-01 | [branch#004] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#030] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#051] [A] kWh last month | 652.5
4-DaHall 1-RPP-01 | [branch#005] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#031] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#052] [A] kWh last month | 0
4-DaHall 1-RPP-01 | [branch#006] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#032] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#053] [A] kWh last month | 95
4-DaHall 1-RPP-01 | [branch#007] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#033] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#054] [A] kWh last month | 362.7
4-DaHall 1-RPP-01 | [branch#008] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#034] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#001] [A] kWh last month | 0
4-DaHall 1-RPP-02 | [branch#001] [A] kWh last month | 0.1 | 5-DaHall 1-PDU-06 | [branch#035] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#002] [A] kWh last month | 0
4-DaHall 1-RPP-02 | [branch#002] [A] kWh last month | 0.1 | 5-DaHall 1-PDU-06 | [branch#036] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#003] [A] kWh last month | 0
4-DaHall 1-RPP-02 | [branch#003] [A] kWh last month | 0.1 | 5-DaHall 1-PDU-06 | [branch#037] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#004] [A] kWh last month | 0
4-DaHall 1-RPP-02 | [branch#004] [A] kWh last month | 0.1 | 5-DaHall 1-PDU-06 | [branch#038] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#005] [A] kWh last month | 0
4-DaHall 1-RPP-02 | [branch#005] [A] kWh last month | 0.1 | 5-DaHall 1-PDU-06 | [branch#039] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#006] [A] kWh last month | 0
4-DaHall 1-RPP-02 | [branch#006] [A] kWh last month | 0.1 | 5-DaHall 1-PDU-06 | [branch#040] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#007] [A] kWh last month | 0
4-DaHall 1-RPP-02 | [branch#007] [A] kWh last month | 0.1 | 5-DaHall 1-PDU-06 | [branch#041] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#008] [A] kWh last month | 0
4-DaHall 1-RPP-02 | [branch#008] [A] kWh last month | 0.1 | 5-DaHall 1-PDU-06 | [branch#042] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#009] [A] kWh last month | 0
4-EPS-CEP-06 | [branch#001] [A] kWh last month | 494.7 | 5-DaHall 1-PDU-06 | [branch#043] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#010] [A] kWh last month | 0
4-EPS-CEP-06 | [branch#002] [A] kWh last month | 5387.8 | 5-DaHall 1-PDU-06 | [branch#044] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#011] [A] kWh last month | 0
4-EPS-CEP-06 | [branch#003] [A] kWh last month | 417.6 | 5-DaHall 1-PDU-06 | [branch#045] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#012] [A] kWh last month | 0
4-EPS-CEP-06 | [branch#004] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#046] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#013] [A] kWh last month | 0
4-EPS-CEP-06 | [branch#005] [A] kWh last month | 259.3 | 5-DaHall 1-PDU-06 | [branch#047] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#014] [A] kWh last month | 0
4-EPS-CEP-06 | [branch#006] [A] kWh last month | 0 | 5-DaHall 1-PDU-06 | [branch#048] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#015] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#049] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#016] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#050] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#017] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#051] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#052] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#019] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#053] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#054] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#001] [A] kWh last month | 1244.9 | 6-DaHall 1-PDU-07 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#002] [A] kWh last month | 109.8 | 6-DaHall 1-PDU-07 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#003] [A] kWh last month | 107.5 | 6-DaHall 1-PDU-07 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#025] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#005] [A] kWh last month | 56.7 | 6-DaHall 1-PDU-07 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#006] [A] kWh last month | 57.3 | 6-DaHall 1-PDU-07 | [branch#027] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#029] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#031] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#013] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#035] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#037] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#039] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#020] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#041] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#021] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#043] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#023] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#045] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#047] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#027] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#028] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#049] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#029] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#030] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#051] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#031] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#052] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#032] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#053] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#033] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#054] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#034] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#035] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#002] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#036] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#002] [A] kWh last month | 151.2 | 6-DaHall 1-PDU-08 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#003] [A] kWh last month | 121.7 | 6-DaHall 1-PDU-08 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#008] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#006] [A] kWh last month | 183.7 | 6-DaHall 1-PDU-08 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#007] [A] kWh last month | 792.5 | 6-DaHall 1-PDU-08 | [branch#010] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#011] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#012] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#013] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#014] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#015] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#013] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#016] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#017] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#019] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#020] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#021] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#025] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#023] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#027] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#029] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#027] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#028] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#031] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#029] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#030] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#031] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#032] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#035] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#033] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#034] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#037] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#035] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#036] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#039] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#041] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#043] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#006] [A] kWh last month | 283 | 6-DaHall 1-PDU-08 | [branch#045] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#047] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#009] [A] kWh last month | 829.4 | 6-DaHall 1-PDU-08 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#049] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#051] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#013] [A] kWh last month | 304.5 | 6-DaHall 1-PDU-08 | [branch#052] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#053] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#054] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#002] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#018] [A] kWh last month | 436.8 | 6-DaHall 1-PDU-09 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#020] [A] kWh last month | 302.3 | 6-DaHall 1-PDU-09 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#021] [A] kWh last month | 362.1 | 6-DaHall 1-PDU-09 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#023] [A] kWh last month | 765.3 | 6-DaHall 1-PDU-09 | [branch#008] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#010] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#026] [A] kWh last month | 872.1 | 6-DaHall 1-PDU-09 | [branch#011] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#027] [A] kWh last month | 417.3 | 6-DaHall 1-PDU-09 | [branch#012] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#028] [A] kWh last month | 869.8 | 6-DaHall 1-PDU-09 | [branch#013] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#029] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#014] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#030] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#015] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#031] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#016] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#032] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#017] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#019] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#004] [A] kWh last month | 251.5 | 6-DaHall 1-PDU-09 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#006] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#025] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#009] [A] kWh last month | 457.4 | 6-DaHall 1-PDU-09 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#027] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#029] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#013] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#031] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#016] [A] kWh last month | 965.9 | 6-DaHall 1-PDU-09 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#018] [A] kWh last month | 504.3 | 6-DaHall 1-PDU-09 | [branch#035] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#019] [A] kWh last month | 392.6 | 6-DaHall 1-PDU-09 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#020] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#037] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#021] [A] kWh last month | 690.3 | 6-DaHall 1-PDU-09 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#039] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#023] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#024] [A] kWh last month | 567.8 | 6-DaHall 1-PDU-09 | [branch#041] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#025] [A] kWh last month | 532 | 6-DaHall 1-PDU-09 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#026] [A] kWh last month | 796.9 | 6-DaHall 1-PDU-09 | [branch#043] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#027] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#028] [A] kWh last month | 926.6 | 6-DaHall 1-PDU-09 | [branch#045] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#029] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#030] [A] kWh last month | 1041.7 | 6-DaHall 1-PDU-09 | [branch#047] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#031] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#032] [A] kWh last month | 451.6 | 6-DaHall 1-PDU-09 | [branch#049] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#003] [A] kWh last month | 894.9 | 6-DaHall 1-PDU-10 | [branch#002] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#005] [A] kWh last month | 587.6 | 6-DaHall 1-PDU-10 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#006] [A] kWh last month | 916.7 | 6-DaHall 1-PDU-10 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#008] [A] kWh last month | 613.3 | 6-DaHall 1-PDU-10 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#008] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#010] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#011] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#013] [A] kWh last month | 70.6 | 6-DaHall 1-PDU-10 | [branch#012] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#013] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#014] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#016] [A] kWh last month | 632.3 | 6-DaHall 1-PDU-10 | [branch#015] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#016] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#017] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#019] [A] kWh last month | 847.8 | 6-DaHall 1-PDU-10 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#020] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#019] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#021] [A] kWh last month | 454.7 | 6-DaHall 1-PDU-10 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#023] [A] kWh last month | 1473.3 | 6-DaHall 1-PDU-10 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#025] [A] kWh last month | 383.5 | 6-DaHall 1-PDU-10 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#026] [A] kWh last month | 270.2 | 6-DaHall 1-PDU-10 | [branch#025] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#027] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#028] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#027] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#029] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#030] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#029] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#031] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#032] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#031] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#003] [A] kWh last month | 472.4 | 6-DaHall 1-PDU-10 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#004] [A] kWh last month | 1086.6 | 6-DaHall 1-PDU-10 | [branch#035] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#006] [A] kWh last month | 422.2 | 6-DaHall 1-PDU-10 | [branch#037] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#039] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#041] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#043] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#013] [A] kWh last month | 242.6 | 6-DaHall 1-PDU-10 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#014] [A] kWh last month | 519.7 | 6-DaHall 1-PDU-10 | [branch#045] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#047] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#017] [A] kWh last month | 120.7 | 6-DaHall 1-PDU-10 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#049] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#019] [A] kWh last month | 388.2 | 6-DaHall 1-PDU-10 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#020] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#021] [A] kWh last month | 558 | 6-DaHall 1-PDU-11 | [branch#002] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#023] [A] kWh last month | 404.1 | 6-DaHall 1-PDU-11 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#024] [A] kWh last month | 759.8 | 6-DaHall 1-PDU-11 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#027] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#008] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#028] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#029] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#010] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#030] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#011] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#031] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#012] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#032] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#013] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#001] [A] kWh last month | 2224.1 | 6-DaHall 1-PDU-11 | [branch#014] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#002] [A] kWh last month | 1292.1 | 6-DaHall 1-PDU-11 | [branch#015] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#016] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#017] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#006] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#019] [A] kWh last month | 922.8
|  |  | 5-DaHall 1-PDU-15 | [branch#007] [A] kWh last month | 579.5 | 6-DaHall 1-PDU-11 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#008] [A] kWh last month | 620 | 6-DaHall 1-PDU-11 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#009] [A] kWh last month | 210.9 | 6-DaHall 1-PDU-11 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#010] [A] kWh last month | 1102.8 | 6-DaHall 1-PDU-11 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#012] [A] kWh last month | 303.4 | 6-DaHall 1-PDU-11 | [branch#025] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#013] [A] kWh last month | 84.8 | 6-DaHall 1-PDU-11 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#014] [A] kWh last month | 177 | 6-DaHall 1-PDU-11 | [branch#027] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#029] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#031] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#020] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#021] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#035] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#023] [A] kWh last month | 362.5 | 6-DaHall 1-PDU-11 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#037] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#039] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#027] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#028] [A] kWh last month | 78.2 | 6-DaHall 1-PDU-11 | [branch#041] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#029] [A] kWh last month | 22.9 | 6-DaHall 1-PDU-11 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#030] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#043] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#001] [A] kWh last month | 1679.8 | 6-DaHall 1-PDU-11 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#002] [A] kWh last month | 1289.6 | 6-DaHall 1-PDU-11 | [branch#045] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#047] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#006] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#049] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#007] [A] kWh last month | 619.8 | 6-DaHall 1-PDU-11 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#008] [A] kWh last month | 705.2 | 6-DaHall 1-PDU-12 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#009] [A] kWh last month | 221 | 6-DaHall 1-PDU-12 | [branch#002] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#010] [A] kWh last month | 26.9 | 6-DaHall 1-PDU-12 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#012] [A] kWh last month | 317 | 6-DaHall 1-PDU-12 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#013] [A] kWh last month | 271.3 | 6-DaHall 1-PDU-12 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#014] [A] kWh last month | 205.9 | 6-DaHall 1-PDU-12 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#015] [A] kWh last month | 392 | 6-DaHall 1-PDU-12 | [branch#008] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#017] [A] kWh last month | 249.3 | 6-DaHall 1-PDU-12 | [branch#010] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#011] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#012] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#020] [A] kWh last month | 80.8 | 6-DaHall 1-PDU-12 | [branch#013] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#021] [A] kWh last month | 18.4 | 6-DaHall 1-PDU-12 | [branch#014] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#022] [A] kWh last month | 80.1 | 6-DaHall 1-PDU-12 | [branch#015] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#023] [A] kWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#016] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#024] [A] kWh last month | 218.4 | 6-DaHall 1-PDU-12 | [branch#017] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#025] [A] kWh last month | 59.2 | 6-DaHall 1-PDU-12 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#019] [A] kWh last month | 828.4
|  |  | 5-DaHall 1-PDU-16 | [branch#027] [A] kWh last month | 232 | 6-DaHall 1-PDU-12 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#028] [A] kWh last month | 21.5 | 6-DaHall 1-PDU-12 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#029] [A] kWh last month | 349.2 | 6-DaHall 1-PDU-12 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#030] [A] kWh last month | 42.2 | 6-DaHall 1-PDU-12 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 0119 [branch#01] [A] KWh last month | 88.3 | 6-DaHall 1-PDU-12 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 0279 [branch#02] [A] KWh last month | 117.3 | 6-DaHall 1-PDU-12 | [branch#025] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 0439 [branch#03] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 0599 [branch#04] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#027] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 0759 [branch#05] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 0919 [branch#06] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#029] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 1079 [branch#07] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 1239 [branch#08] [A] KWh last month | 326.7 | 6-DaHall 1-PDU-12 | [branch#031] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 1399 [branch#09] [A] KWh last month | 1160.8 | 6-DaHall 1-PDU-12 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 1559 [branch#10] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 1719 [branch#11] [A] KWh last month | 71.4 | 6-DaHall 1-PDU-12 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 1879 [branch#12] [A] KWh last month | 161.9 | 6-DaHall 1-PDU-12 | [branch#035] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 2039 [branch#13] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 2199 [branch#14] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#037] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 2359 [branch#15] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 2519 [branch#16] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#039] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 2679 [branch#17] [A] KWh last month | 81 | 6-DaHall 1-PDU-12 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 2839 [branch#18] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#041] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 2999 [branch#19] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 3159 [branch#20] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#043] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 3319 [branch#21] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 3479 [branch#22] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#045] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 3639 [branch#23] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 3799 [branch#24] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#047] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 3959 [branch#25] [A] KWh last month | 252.6 | 6-DaHall 1-PDU-12 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 4119 [branch#26] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#049] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 4279 [branch#27] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 4439 [branch#28] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 4599 [branch#29] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#002] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 4759 [branch#30] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 4919 [branch#31] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 5079 [branch#32] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 5239 [branch#33] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 5399 [branch#34] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 0119 [branch#01] [A] KWh last month | 105.5 | 6-DaHall 1-PDU-13 | [branch#008] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 0279 [branch#02] [A] KWh last month | 109.6 | 6-DaHall 1-PDU-13 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 0439 [branch#03] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#010] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 0599 [branch#04] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#011] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 0759 [branch#05] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#012] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 0919 [branch#06] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#013] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 1079 [branch#07] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#014] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 1239 [branch#08] [A] KWh last month | 317.6 | 6-DaHall 1-PDU-13 | [branch#015] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 1399 [branch#09] [A] KWh last month | 782.1 | 6-DaHall 1-PDU-13 | [branch#016] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 1559 [branch#10] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#017] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 1719 [branch#11] [A] KWh last month | 52.7 | 6-DaHall 1-PDU-13 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 1879 [branch#12] [A] KWh last month | 114.4 | 6-DaHall 1-PDU-13 | [branch#019] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 2039 [branch#13] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 2199 [branch#14] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 2359 [branch#15] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 2519 [branch#16] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 2679 [branch#17] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 2839 [branch#18] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#025] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 2999 [branch#19] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 3159 [branch#20] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#027] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 3319 [branch#21] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 3479 [branch#22] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#029] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 3639 [branch#23] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 3799 [branch#24] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#031] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 3959 [branch#25] [A] KWh last month | 75.9 | 6-DaHall 1-PDU-13 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 4119 [branch#26] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 4279 [branch#27] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 4439 [branch#28] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#035] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 4599 [branch#29] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 4759 [branch#30] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#037] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 4919 [branch#31] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 5079 [branch#32] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#039] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 5239 [branch#33] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 5399 [branch#34] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#041] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 0119 [branch#01] [A] KWh last month | 595.8 | 6-DaHall 1-PDU-13 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 0279 [branch#02] [A] KWh last month | 862 | 6-DaHall 1-PDU-13 | [branch#043] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 0439 [branch#03] [A] KWh last month | 824.9 | 6-DaHall 1-PDU-13 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 0599 [branch#04] [A] KWh last month | 789.1 | 6-DaHall 1-PDU-13 | [branch#045] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 0759 [branch#05] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 0919 [branch#06] [A] KWh last month | 449.2 | 6-DaHall 1-PDU-13 | [branch#047] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 1079 [branch#07] [A] KWh last month | 1271.9 | 6-DaHall 1-PDU-13 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 1239 [branch#08] [A] KWh last month | 913.2 | 6-DaHall 1-PDU-13 | [branch#049] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 1399 [branch#09] [A] KWh last month | 907.1 | 6-DaHall 1-PDU-13 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 1559 [branch#10] [A] KWh last month | 951.7 | 6-DaHall 1-PDU-13 | [branch#051] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 1719 [branch#11] [A] KWh last month | 839.2 | 6-DaHall 1-PDU-13 | [branch#052] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 1879 [branch#12] [A] KWh last month | 562.8 | 6-DaHall 1-PDU-13 | [branch#053] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 2039 [branch#13] [A] KWh last month | 874.8 | 6-DaHall 1-PDU-13 | [branch#054] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 2199 [branch#14] [A] KWh last month | 232.4 | 6-DaHall 1-PDU-14 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 2359 [branch#15] [A] KWh last month | 990.9 | 6-DaHall 1-PDU-14 | [branch#002] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 2519 [branch#16] [A] KWh last month | 1364.8 | 6-DaHall 1-PDU-14 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 2679 [branch#17] [A] KWh last month | 574.2 | 6-DaHall 1-PDU-14 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 2839 [branch#18] [A] KWh last month | 931.9 | 6-DaHall 1-PDU-14 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 2999 [branch#19] [A] KWh last month | 545.2 | 6-DaHall 1-PDU-14 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 3159 [branch#20] [A] KWh last month | 1510.1 | 6-DaHall 1-PDU-14 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 3319 [branch#21] [A] KWh last month | 0 | 6-DaHall 1-PDU-14 | [branch#008] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 3479 [branch#22] [A] KWh last month | 1369.8 | 6-DaHall 1-PDU-14 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 3639 [branch#23] [A] KWh last month | 632 | 6-DaHall 1-PDU-14 | [branch#010] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 3799 [branch#24] [A] KWh last month | 0 | 6-DaHall 1-PDU-14 | [branch#011] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 0119 [branch#01] [A] KWh last month | 791.4 | 6-DaHall 1-PDU-14 | [branch#012] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 0279 [branch#02] [A] KWh last month | 910.9 | 6-DaHall 1-PDU-14 | [branch#013] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 0439 [branch#03] [A] KWh last month | 836.1 | 6-DaHall 1-PDU-14 | [branch#014] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 0599 [branch#04] [A] KWh last month | 768.6 | 6-DaHall 1-PDU-14 | [branch#015] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 0759 [branch#05] [A] KWh last month | 0 | 6-DaHall 1-PDU-14 | [branch#016] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 0919 [branch#06] [A] KWh last month | 264.2 | 6-DaHall 1-PDU-14 | [branch#017] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 1079 [branch#07] [A] KWh last month | 1321.7 | 6-DaHall 1-PDU-14 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 1239 [branch#08] [A] KWh last month | 936.3 | 6-DaHall 1-PDU-14 | [branch#019] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 1399 [branch#09] [A] KWh last month | 886.7 | 6-DaHall 1-PDU-14 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 1559 [branch#10] [A] KWh last month | 940.6 | 6-DaHall 1-PDU-14 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 1719 [branch#11] [A] KWh last month | 739 | 6-DaHall 1-PDU-14 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 1879 [branch#12] [A] KWh last month | 540.9 | 6-DaHall 1-PDU-14 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 2039 [branch#13] [A] KWh last month | 809.1 | 6-DaHall 1-PDU-14 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 2199 [branch#14] [A] KWh last month | 214.4 | 6-DaHall 1-PDU-14 | [branch#025] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 2359 [branch#15] [A] KWh last month | 1186.2 | 6-DaHall 1-PDU-14 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 2519 [branch#16] [A] KWh last month | 1384.2 | 6-DaHall 1-PDU-14 | [branch#027] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 2679 [branch#17] [A] KWh last month | 638.2 | 6-DaHall 1-PDU-14 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 2839 [branch#18] [A] KWh last month | 894.8 | 6-DaHall 1-PDU-14 | [branch#029] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 2999 [branch#19] [A] KWh last month | 552.9 | 6-DaHall 1-PDU-14 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 3159 [branch#20] [A] KWh last month | 289.1 | 6-DaHall 1-PDU-14 | [branch#031] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 3319 [branch#21] [A] KWh last month | 0 | 6-DaHall 1-PDU-14 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 3479 [branch#22] [A] KWh last month | 133.3 | 6-DaHall 1-PDU-14 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 3639 [branch#23] [A] KWh last month | 659.7 | 6-DaHall 1-PDU-14 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 3799 [branch#24] [A] KWh last month | 0 | 6-DaHall 1-PDU-14 | [branch#035] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 0119 [branch#01] [A] KWh last month | 1186.6 | 6-DaHall 1-PDU-14 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 0279 [branch#02] [A] KWh last month | 668 | 6-DaHall 1-PDU-14 | [branch#037] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 0439 [branch#03] [A] KWh last month | 1058.7 | 6-DaHall 1-PDU-14 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 0599 [branch#04] [A] KWh last month | 620.6 | 6-DaHall 1-PDU-14 | [branch#039] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 0759 [branch#05] [A] KWh last month | 332.7 | 6-DaHall 1-PDU-14 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 0919 [branch#06] [A] KWh last month | 662.5 | 6-DaHall 1-PDU-14 | [branch#041] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 1079 [branch#07] [A] KWh last month | 736.5 | 6-DaHall 1-PDU-14 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 1239 [branch#08] [A] KWh last month | 957.8 | 6-DaHall 1-PDU-14 | [branch#043] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 1399 [branch#09] [A] KWh last month | 1159.6 | 6-DaHall 1-PDU-14 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 1559 [branch#10] [A] KWh last month | 1067 | 6-DaHall 1-PDU-14 | [branch#045] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 1719 [branch#11] [A] KWh last month | 814.8 | 6-DaHall 1-PDU-14 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 1879 [branch#12] [A] KWh last month | 197.5 | 6-DaHall 1-PDU-14 | [branch#047] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 2039 [branch#13] [A] KWh last month | 900.8 | 6-DaHall 1-PDU-14 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 2199 [branch#14] [A] KWh last month | 268.8 | 6-DaHall 1-PDU-14 | [branch#049] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 2359 [branch#15] [A] KWh last month | 528.6 | 6-DaHall 1-PDU-14 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 2519 [branch#16] [A] KWh last month | 1146 | 6-DaHall 1-PDU-14 | [branch#051] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 2679 [branch#17] [A] KWh last month | 709.6 | 6-DaHall 1-PDU-14 | [branch#052] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 2839 [branch#18] [A] KWh last month | 874.2 | 6-DaHall 1-PDU-14 | [branch#053] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 2999 [branch#19] [A] KWh last month | 624.1 | 6-DaHall 1-PDU-14 | [branch#054] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 3159 [branch#20] [A] KWh last month | 1449.6
|  |  | 5-DaHall 1-PDU-21 | 3319 [branch#21] [A] KWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 3479 [branch#22] [A] KWh last month | 1132.9
|  |  | 5-DaHall 1-PDU-21 | 3639 [branch#23] [A] KWh last month | 619.6
|  |  | 5-DaHall 1-PDU-21 | 3799 [branch#24] [A] KWh last month | 0
|  |  | 5-DaHall 1-PDU-22 | 0119 [branch#01] [A] KWh last month | 1237.8
|  |  | 5-DaHall 1-PDU-22 | 0279 [branch#02] [A] KWh last month | 656.8
|  |  | 5-DaHall 1-PDU-22 | 0439 [branch#03] [A] KWh last month | 1098.5
|  |  | 5-DaHall 1-PDU-22 | 0599 [branch#04] [A] KWh last month | 604
|  |  | 5-DaHall 1-PDU-22 | 0759 [branch#05] [A] KWh last month | 315.7
|  |  | 5-DaHall 1-PDU-22 | 0919 [branch#06] [A] KWh last month | 361.5
|  |  | 5-DaHall 1-PDU-22 | 1079 [branch#07] [A] KWh last month | 717.7
|  |  | 5-DaHall 1-PDU-22 | 1239 [branch#08] [A] KWh last month | 1026.4
|  |  | 5-DaHall 1-PDU-22 | 1399 [branch#09] [A] KWh last month | 1173.3
|  |  | 5-DaHall 1-PDU-22 | 1559 [branch#10] [A] KWh last month | 1119.9
|  |  | 5-DaHall 1-PDU-22 | 1719 [branch#11] [A] KWh last month | 870.2
|  |  | 5-DaHall 1-PDU-22 | 1879 [branch#12] [A] KWh last month | 208.6
|  |  | 5-DaHall 1-PDU-22 | 2039 [branch#13] [A] KWh last month | 820.2
|  |  | 5-DaHall 1-PDU-22 | 2199 [branch#14] [A] KWh last month | 270.5
|  |  | 5-DaHall 1-PDU-22 | 2359 [branch#15] [A] KWh last month | 649.7
|  |  | 5-DaHall 1-PDU-22 | 2519 [branch#16] [A] KWh last month | 1201.6
|  |  | 5-DaHall 1-PDU-22 | 2679 [branch#17] [A] KWh last month | 594.6
|  |  | 5-DaHall 1-PDU-22 | 2839 [branch#18] [A] KWh last month | 838.4
|  |  | 5-DaHall 1-PDU-22 | 2999 [branch#19] [A] KWh last month | 676.6
|  |  | 5-DaHall 1-PDU-22 | 3159 [branch#20] [A] KWh last month | 164.8
|  |  | 5-DaHall 1-PDU-22 | 3319 [branch#21] [A] KWh last month | 0
|  |  | 5-DaHall 1-PDU-22 | 3479 [branch#22] [A] KWh last month | 134.1
|  |  | 5-DaHall 1-PDU-22 | 3639 [branch#23] [A] KWh last month | 642.8
|  |  | 5-DaHall 1-PDU-22 | 3799 [branch#24] [A] KWh last month | 0

## 8층 사무실 분전반 (hidden)
2023 년 9 월 25 일
Main CB 4P 100A
8층 사무실 창고 : UPS 출력(From:7F 창고)
[10 empty] | MAIN 계측값 : | 3.1 | 2.7 | 7.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
DEK LOC #01 | O | ON | 1.5 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 1.6 |  |  |  | O | ON | SECURITY #02
DEK LOC #03 | O | ON |  | 1.2 |  |  | 2P 30A | #03 | #04 | 2P 30A |  |  |  |  | O | OFF | KIOSK #04
DEK LOC #05 | O | ON |  |  | 2.2 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 3 |  | O | ON | RACK #06
| X | OFF |  |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | ON | 통합경보반 #08
| X | OFF |  |  |  |  | 2P 30A | #09 | #10 | 2P 30A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 2P 30A | #11 | #12 | 2P 30A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 2P 30A | #13 | #14 | 2P 30A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 2P 30A | #15 | #16 | 2P 30A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 2P 30A | #17 | #18 | 2P 30A |  |  |  |  | X | OFF | SELABLE #18
SJT 모니터 #19 | O | ON | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A |  |  |  |  | X | OFF | SELABLE #20
STJ 사무실 # 21 | O | ON |  | 1.7 |  |  | 2P 30A | #21 | #22 | 2P 30A |  |  |  |  | X | OFF | SELABLE #22
SJT (SERVER) # 23 | O | ON |  |  | 2.6 |  | 2P 30A | #21 | #22 | 2P 30A |  |  |  |  | X | OFF | SELABLE #24
[10 empty] | 총합: | 3.1 | 2.9 | 7.8
Main CB 4P 100A
8층 복도 : 에어컨 분전함 (From:6층 보조항온항습기 분전반)
[10 empty] | MAIN 계측값 : | 2.3 | 2.2 | 7.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
사무실, 회의실 실외기 | O | ON | 0.3 | 0.3 | 0.3 | 0.1 | 3P 50A | #01 | #02 | 3P 50A | 2.6 | 2.6 | 2.7 | 0.1 | O | ON | 임대오피스 실외기
사무실 외의실 실내기 | O | ON | 0.2 |  |  |  | 2P 30A | #03 | #04 | 2P 30A |  |  |  |  | X | OFF
실외기실 동파방지열선 | O | ON |  | 0 |  |  | 2P 30A | #05 | #06 | 2P 30A |  | 0.3 |  |  | O | ON | 임대오피스 실내기
| X | OFF |  |  |  |  | 2P 30A | #07 | #08 | 2P 30A |  |  | 5.4 |  | O | ON | SJT 에어컨
[10 empty] | 총합: | 3.1 | 3.2 | 8.4

## 7층_부하량(월간_MIN)
Date : 2024-01-01 ~ 2024-01-31
7-DaHall 1-RPP-01 |  |  | PDU : 7-DaHall 1-RPP-01 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 26 | 14 | 21.8 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
W-DCS 8000 | O | ON | 0 |  |  |  | 2P 20A | #01 | 전송 |  | #02 | 2P 30A | 0 |  |  |  | O | ON | TO 8F 보안실 UPS항온 항습기 모니터용PC
?? | O | ON |  | 0 |  |  | 2P 20A | #03 | 전송 | 넷피플 | #04 | 2P 30A |  | 0 |  |  | O | ON | E-4-B
?? | O | ON |  |  | 0 |  | 2P 20A | #05 | 전송 | 넷피플 | #06 | 2P 30A |  |  | 0 |  | O | OFF | E-3-B
517 BAY | O | ON | 0 |  |  |  | 2P 20A | #07 | 전송 | 전송 | #08 | 2P 30A | 2.38 |  |  |  | O | ON | 406BAY 405BAY DCN-1B
Voice사업팀 MMS용-B | X | OFF |  | 0 |  |  | 2P 20A | #09 | IDC | 전송 | #10 | 2P 30A |  | 1.67 |  |  | O | ON | 407BAY 406BAY DCN-2B
Voice사업팀 D-7 RACK | O | ON |  |  | 0 |  | 2P 20A | #11 | 니즈텔레콤 | 전송 | #12 | 2P 30A |  |  | 3.36 |  | O | ON | 408BAY 407BAY DCN-3B
ONS1064 SERVER | O | ON | 0 |  |  |  | 2P 20A | #13 | 전송 | 엑사넷 | #14 | 2P 30A | 6.26 |  |  |  | O | ON | E-8-B
NTT 하-1 | X | ON |  | 0 |  |  | 2P 20A | #15 | IDC | 델피콤 | #16 | 2P 30A |  | 2.54 |  |  | O | ON | F-5-B
8층 보안실 CCTV 모니터 | O | ON |  |  | 0 |  | 2P 20A | #17 | 공통 | CARANG ('23.09.19) | #18 | 2P 30A |  |  | 1.28 |  | O | ON | C604 / F-7-A
G-10-A | O | ON | 0.99 |  |  |  | 2P 20A | #19 | 신한금융투자 | IDC | #20 | 2P 30A | 1.48 |  |  |  | O | ON | 인터넷운영팀MAN RACK#2 전원A
NTT 하-3 | X | OFF |  | 0 |  |  | 2P 20A | #21 |  | NTT | #22 | 2P 30A |  | 0 |  |  | O | ON | G-4-B
C-7-A-Q1 | O | ON |  |  | 1.44 |  | 2P 20A | #23 | NTT | NTT | #24 | 2P 30A |  |  | 0 |  | O | ON | G-6-B
인터넷운영팀MAN RACK#2 전원B | O | ON | 1.5 |  |  |  | 2P 20A | #25 | IDC | 교환라우터(총무팀 ??) | #26 | 2P 30A | 1.52 |  |  |  | O | ON | F-3-B
NMS B-15 | O | ON |  | 2.96 |  |  | 2P 20A | #27 | 전송 | 공통 | #28 | 2P 30A |  | 0.87 |  |  | O | ON | 운용실콘센트
NMS B-16 | O | ON |  |  | 3.94 |  | 2P 20A | #29 | 전송 | 공통 | #30 | 2P 30A |  |  | 3.74 |  | O | ON | 운용실콘센트 창가1열
?? | O | ON | 5.38 |  |  |  | 2P 20A | #31 | 전송 | 전송 | #32 | 2P 30A | 0 |  |  |  | O | ON | 전산랙 410BAY(B)
G-5-B | O | ON |  | 0 |  |  | 2P 20A | #33 | NTT | 니즈텔레콤 | #34 | 2P 30A |  | 0 |  |  | O | OFF | D-6-B
G-1-B | O | ON |  |  | 0 |  | 2P 20A | #35 |  | 르네트 | #36 | 2P 30A |  |  | 3.17 |  | O | ON | E-9-B
C-7-B-Q1 | O | ON | 5.47 |  |  |  | 2P 20A | #37 | NTT | 니즈텔레콤 | #38 | 2P 30A | 2.16 |  |  |  | O | ON | D-7-B
G-2-B | O | ON |  | 0 |  |  | 2P 20A | #39 |  | IDC | #40 | 2P 30A |  | 4.7 |  |  | O | ON | 341BAY / IDC MAN POP AC전원(B)
[12 empty] | 총합: | 27.14 | 12.74 | 16.93
7-DaHall 1-PDU-02 |  |  | PDU : 7-DaHall 1-PDU-02 | [5 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 30.2 | 45.2 | 46.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
G-3-B (NTT#8-B) | O | ON |  | 0 |  |  | 2P 30A | #01 | NTT | 쿼드마이너 | #02 | 2P 30A |  | 0 |  |  | O | ON | C503 | 쿼드마이너 예약상면
7B-342BAY | O | ON |  |  | 5.13 |  | 2P 30A | #03 | 인터넷 IP 랙 |  | #04 | 2P 30A |  |  | 0 |  | O | ON | U3-7B-D1
| X | OFF | 0 |  |  |  | 2P 30A | #05 |  | NTT | #06 | 2P 30A | 0 |  |  |  | O | ON | U3-7B-D5 B
241BAY-B | O | ON |  | 5.7 |  |  | 2P 30A | #07 |  | 전송 | #08 | 2P 30A |  | 0 |  |  | O | ON | U3-7B-337
242BAY-B | O | ON |  |  | 4.45 |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  |  | 2.26 |  | O | ON | 7F-C-6-NTT#3-B
209Bay - B | O | ON | 5.67 |  |  |  | 2P 30A | #11 |  | NTT | #12 | 2P 30A | 0 |  |  |  | O | ON | U3-7B G-3-B
210Bay - B | O | ON |  | 5.22 |  |  | 2P 30A | #13 |  | DEKR Network Rack | #14 | 2P 30A |  | 3.06 |  |  | O | ON | 218Bay - A전원 ('22.01.12 투입)
TATA#1/B | O | ON |  |  | 1.08 |  | 2P 30A | #15 | TATA | DEKR Network Rack | #16 | 2P 30A |  |  | 2.92 |  | O | ON | 217Bay - A전원 ('22.01.12 투입)
208BAY-B | O | ON | 3.27 |  |  |  | 2P 30A | #17 |  | 318Bay - DEK Network Rack | #18 | 2P 30A | 1.32 |  |  |  | O | ON | 318BAY-B U3-7B-18
207BAY-B | O | ON |  | 8.82 |  |  | 2P 30A | #19 |  | 317Bay - DEK Network Rack | #20 | 2P 30A |  | 1.97 |  |  | O | ON | 317BAY-B U3-7B-20
206BAY-B | O | ON |  |  | 3.85 |  | 2P 30A | #21 |  | 316Bay - DEK Network Rack | #22 | 2P 30A |  |  | 1.19 |  | O | ON | 316BAY-B U3-7B-22
205BAY-B | O | ON | 2.54 |  |  |  | 2P 30A | #23 |  | 315Bay - DEK Network Rack | #24 | 2P 30A | 2.21 |  |  |  | O | ON | 315BAY-B U3-7B-24
204BAY-B | O | ON |  | 1.72 |  |  | 2P 30A | #25 |  | 314Bay - DEK Network Rack | #26 | 2P 30A |  | 3.57 |  |  | O | ON | 314BAY-B U3-7B-26
208BAY-B(2) | O | ON |  |  | 3.55 |  | 2P 30A | #27 |  | 313Bay - DEK Network Rack | #28 | 2P 30A |  |  | 5.73 |  | O | ON | 313BAY-B U3-7B-28
C604 / F-7-B | O | ON | 1.47 |  |  |  | 2P 30A | #29 | CARANG ('23.09.19) | 드림라인 | #30 | 2P 30A | 0.51 |  |  |  | O | ON | 301BAY U3-7B-30
U3-7B-31 B-6-B | O | ON |  | 3.65 |  |  | 2P 30A | #31 | 세종 인터넷(클라우드이음) | 203Bay - 세종-아톤AWS | #32 | 2P 30A |  | 1.89 |  |  | O | ON | 203Bay-B ('22.07.14 투입) U3-7B-32
B-7-B | O | ON |  |  | 8.26 |  | 2P 30A | #33 | 세종 인터넷(클라우드이음) | C909 (舊 C-02) / TATA#02 | #34 | 2P 30A |  |  | 0 |  | O | ON | C-02(C909-B) U3-7B-34
B-8-B | O | ON | 6.45 |  |  |  | 2P 30A | #35 | 세종 인터넷(클라우드이음) |  | #36 | 2P 30A | 0 |  |  |  | O | ON | B424(310BAY-B)
Test Bed #2 U3-7B-37 | O | ON |  | 0 |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  | 3.82 |  |  | O | ON | B423(311BAY-B)
7-1-B2-30-39 | O | ON |  |  | 1.83 |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  |  | 2.93 |  | O | ON | B422(312BAY-B)
7B-30-41(C409) | O | ON | 0 |  |  |  | 2P 30A | #41 | C409 |  | #42 | 2P 30A | 4.42 |  |  |  | O | ON | 7-1-B2-30-42
| X | OFF |  | 0 |  |  | 2P 30A | #43 |  | 쿼드마이너 | #44 | 2P 30A |  | 1.34 |  |  | O | ON | C502 | 2023/04/10 랙 반입 예정
| X | OFF |  |  | 0 |  | 2P 30A | #45 |  | 쿼드마이너 | #46 | 2P 30A |  |  | 0 |  | O | ON | C504 | 쿼드마이너 예약상면
| X | OFF | 0 |  |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A | 1.36 |  |  |  | X | OFF
신규BMS(20F TPS실) Rack | O | ON |  | 0.88 |  |  | 2P 30A | #49 | 20F BMS |  | #50 | 2P 30A |  | 2.06 |  |  | O | ON | 7층 출입카드
신규BMS(7F TPS실) Rack | O | ON |  |  | 0.55 |  | 2P 30A | #51 | 7F BMS |  | #52 | 2P 30A |  |  | 0 |  | O | ON | 20F MAIN (FMS)
7B-D5-#1 | O | ON | 0.23 |  |  |  | 2P 30A | #53 | NTT |  | #54 | 2P 30A | 0 |  |  |  | O | ON | 7F MAIN (FMS)
[12 empty] | 총합: | 29.45 | 43.7 | 43.73 | 0
7-DaHall 1-PDU-01 |  |  | PDU : 7-DaHall 1-PDU-01 | [5 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 33.4 | 43.4 | 40.1 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
G-3-A (NTT#8-A) | O | ON |  | 0 |  |  | 2P 30A | #01 | NTT | 쿼드마이너 | #02 | 2P 30A |  | 0 |  |  | O | ON | G-8-A (C503) | 쿼드마이너 예약상면
F-5-A | O | ON |  |  | 2.07 |  | 2P 30A | #03 | 텔피콤 |  | #04 | 2P 30A |  |  | 0 |  | O | ON | D-1-A
7A-342BAY | O | ON | 4.91 |  |  |  | 2P 30A | #05 | 인터넷 IP 랙 | NTT | #06 | 2P 30A | 0 |  |  |  | O | ON | D-5-A
241BAY-A | O | ON |  | 5.94 |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  | 1.53 |  |  | O | ON | 405BAY / U3-7A-405BAY(A)
242BAY-A | O | ON |  |  | 5.7 |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  |  | 1.48 |  | O | ON | C-6-A
209Bay - A | O | ON | 6.79 |  |  |  | 2P 30A | #11 | 인터넷 IP 랙 | NTT | #12 | 2P 30A | 0 |  |  |  | O | ON | U3-7A G-3-A
210Bay - A | O | ON |  | 6.58 |  |  | 2P 30A | #13 | 인터넷 IP 랙 | DEKR Network Rack | #14 | 2P 30A |  | 4.11 |  |  | O | ON | 218Bay - A전원 ('22.01.12 투입)
TATA#1/A | O | ON |  |  | 0.78 |  | 2P 30A | #15 | TATA | DEKR Network Rack | #16 | 2P 30A |  |  | 2.28 |  | O | ON | 217Bay - A전원 ('22.01.12 투입)
208BYA-A | O | ON | 2.73 |  |  |  | 2P 30A | #17 | 인터넷 IP 랙 | 318Bay - DEK Network Rack | #18 | 2P 30A | 1.33 |  |  |  | O | ON | 318BAY-A U3-7A-18
207BYA-A | O | ON |  | 3.87 |  |  | 2P 30A | #19 | 인터넷 IP 랙 | 317Bay - DEK Network Rack | #20 | 2P 30A |  | 0.9 |  |  | O | ON | 317BAY-A U3-7A-20
206BYA-A | O | ON |  |  | 3.87 |  | 2P 30A | #21 | 인터넷 IP 랙 | 316Bay - DEK Network Rack | #22 | 2P 30A |  |  | 1.7 |  | O | ON | 316BAY-A U3-7A-22
205BYA-A | O | ON | 1.74 |  |  |  | 2P 30A | #23 | 인터넷 IP 랙 | 315Bay - DEK Network Rack | #24 | 2P 30A | 2.58 |  |  |  | O | ON | 315BAY-A U3-7A-24
204BYA-A | O | ON |  | 1.44 |  |  | 2P 30A | #25 | 인터넷 IP 랙 | 314Bay - DEK Network Rack | #26 | 2P 30A |  | 3.35 |  |  | O | ON | 314BAY-A U3-7A-26
208BAY 207BAY - A(2) | O | ON |  |  | 3.21 |  | 2P 30A | #27 | 인터넷 IP 랙 | 313Bay - DEK Network Rack | #28 | 2P 30A |  |  | 5.5 |  | O | ON | 313BAY-A U3-7A-28
322BAY 331BAY | O | ON | 0 |  |  |  | 2P 30A | #29 | 김종원M 요구회로 | 드림라인 | #30 | 2P 30A | 0.34 |  |  |  | O | ON | 301BAY U3-7A-30
U3-7A-31 B-6-A | O | ON |  | 4.44 |  |  | 2P 30A | #31 | 세종 인터넷(클라우드이음) | 203Bay - 세종-아톤AWS | #32 | 2P 30A |  | 2.09 |  |  | O | ON | 203Bay-A ('22.07.14 투입) U3-7A-32
B-7-A | O | ON |  |  | 8.55 |  | 2P 30A | #33 | 세종 인터넷(클라우드이음) | C909 (舊 C-02) / TATA#02 | #34 | 2P 30A |  |  | 0 |  | O | ON | C-02(C909-A) U3-7A-34
B-8-A | O | ON | 6.51 |  |  |  | 2P 30A | #35 | 세종 인터넷(클라우드이음) |  | #36 | 2P 30A | 0 |  |  |  | O | ON | B424(310BAY-A)
Test Bed #1 U3-7A-37 | O | ON |  | 0 |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  | 2.75 |  |  | O | ON | B423(311BAY-A)
7-1-A2-30-39 | O | ON |  |  | 1.03 |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  |  | 3.31 |  | O | ON | B422(312BAY-A)
7A-30-41(C409) | O | ON | 1.05 |  |  |  | 2P 30A | #41 | C409 |  | #42 | 2P 30A | 3.32 |  |  |  | O | ON | 7-1-A2-30-42
| X | OFF |  | 0 |  |  | 2P 30A | #43 |  | 쿼드마이너 | #44 | 2P 30A |  | 5.57 |  |  | O | ON | C502 | 2023/04/10 랙 반입 예정
| X | OFF |  |  | 0 |  | 2P 30A | #45 |  | 쿼드마이너 | #46 | 2P 30A |  |  | 0 |  | O | ON | C504 | 쿼드마이너 예약상면
| X | OFF | 0 |  |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A | 1 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #51 |  |  | #52 | 2P 30A |  |  | 0 |  | O | ON | 7F NTT CCTV 전원
| X | OFF | 0 |  |  |  | 2P 30A | #53 |  | NTT | #54 | 2P 30A | 0.34 |  |  |  | O | ON | 7A-D5-#1
[12 empty] | 총합: | 32.64 | 42.57 | 39.48 | 0
7-DaHall 1-RPP-02 |  |  | PDU : 7-DaHall 1-RPP-02 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 39 | 12.5 | 20.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO | NO. | NO. | NO | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
강남방향 창가열 콘센트 | O | ON | 0.87 |  |  |  | 2P 20A | #01 | 공통 | 공통 | #02 | 2P 30A | 0 |  |  |  | O | ON | 정면창가 콘센트
?? | O | ON |  | 0.54 |  |  | 2P 20A | #03 | 공통 |  | #04 | 2P 30A |  | 0 |  |  | X | OFF | NTT 상-1
301 BAY | O | OFF |  |  | 0 |  | 2P 20A | #05 | 전송 | 전송 | #06 | 2P 30A |  |  | 0 |  | O | ON | GAINS
C2C DWDM EMS RACK | O | ON | 1.12 |  |  |  | 2P 20A | #07 | 전송 | NTT | #08 | 2P 30A | 5.83 |  |  |  | O | ON | C-8-A
405BAY / U3-7A-405BAY(A) | O | ON |  | 0.85 |  |  | 2P 20A | #09 | 전송 | 신한금융투자 | #10 | 2P 30A |  | 0.66 |  |  | O | ON | G-10-B
ONS1064 SERVER | O | ON |  |  | 0 |  | 2P 20A | #11 | 전송 | NTT | #12 | 2P 30A |  |  | 3.06 |  | O | ON | C-8-B
406BAY 405 BAY (DCN-1A) | O | ON | 2.84 |  |  |  | 2P 20A | #13 | 전송 | 유엔시스 | #14 | 2P 30A | 12.97 |  |  |  | O | ON | D-3-A
407BAY 406 BAY (DCN-2A) | O | ON |  | 1.76 |  |  | 2P 20A | #15 | 전송 | NTT | #16 | 2P 30A |  | 0 |  |  | O | ON | G-4-A (NTT#7)
408BAY 407 BAY (DCN-3A) | O | ON |  |  | 2.44 |  | 2P 20A | #17 | 전송 | NTT | #18 | 2P 30A |  |  | 0 |  | O | ON | G-6-A
E-2-A | O | ON | 0 |  |  |  | 2P 20A | #19 |  | 교환라우터(총무팀 ??) | #20 | 2P 30A | 0 |  |  |  | O | ON | F-3-A
E-5-A | X | OFF |  | 0 |  |  | 2P 20A | #21 | 니즈텔레콤 | 공통 | #22 | 2P 30A |  | 0 |  |  | O | ON | 운용실 바닥콘센트
E-6-A | O | ON |  |  | 0 |  | 2P 20A | #23 |  | 공통 | #24 | 2P 30A |  |  | 1.42 |  | O | ON | 운용실 콘센트 창가1열
E-7-A | O | ON | 0 |  |  |  | 2P 20A | #25 |  | 전송 | #26 | 2P 30A | 0.28 |  |  |  | O | ON | 전산랙 410 BAY-A
E-8-A | O | ON |  | 5.65 |  |  | 2P 20A | #27 | 엑사넷 | 니즈텔레콤 | #28 | 2P 30A |  | 0 |  |  | O | OFF | D-6-A
G-5-A | O | ON |  |  | 0 |  | 2P 20A | #29 | NTT | 르네트 | #30 | 2P 30A |  |  | 1.7 |  | O | ON | E-9-A
Voice사업팀 NMS용-A | X | OFF | 0 |  |  |  | 2P 20A | #31 | IDC | 니즈텔레콤 | #32 | 2P 30A | 3.33 |  |  |  | O | ON | D-7-A
NTT 상-3 | X | OFF |  | 0 |  |  | 2P 20A | #33 | IDC |  | #34 | 2P 30A |  | 0 |  |  | O | ON | F-8-A
7F NMS A-18 | O | ON |  |  | 2.4 |  | 2P 20A | #35 | 전송 | 델피콤 | #36 | 2P 30A |  |  | 6.81 |  | O | ON | F-6-A
7F NMS A-19 | O | ON | 5.44 |  |  |  | 2P 20A | #37 | 전송 | IDC | #38 | 2P 30A | 4.79 |  |  |  | O | ON | 341BAY / IDC MAN POP
7F NMS A-20 | O | ON |  | 2.72 |  |  | 2P 20A | #39 | 전송 |  | #40 | 2P 30A |  | 0 |  |  | O | ON | F-9-A
[12 empty] | 총합: | 37.47 | 12.18 | 17.83
7-DaHall 1-RPP-03 |  |  | PDU : 7-DaHall 1-RPP-03 | [5 empty] | Main CB 4P 225A
[12 empty] | MAIN 계측값 : | 6.8 | 8 | 5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A-1-A [A2-7-1] | O | ON | 0 |  |  |  | 2P 50A | #01 | CJ HELLOVISION | NTT | #02 | 2P 50A | 0.81 |  |  |  | O | ON | D-4-A [D3-A]
A-2-A [A2-7-2] | O | ON |  | 2.76 |  |  | 2P 50A | #03 | CJ HELLOVISION | NTT | #04 | 2P 50A |  | 0 |  |  | X | OFF | G-7-A
A-3-A [A2-7-3] | O | ON |  |  | 3.36 |  | 2P 50A | #05 | CJ HELLOVISION | CJ HELLOVISION | #06 | 2P 50A |  |  | 1.55 |  | O | ON | A-7-A [A2-7-7]
A-4-A [A2-7-4] | O | ON | 2.48 |  |  |  | 2P 50A | #07 | CJ HELLOVISION | CJ HELLOVISION | #08 | 2P 50A | 1.94 |  |  |  | O | ON | A-8-A [A2-7-8]
A-5-A [A2-7-5] | O | ON |  | 2.72 |  |  | 2P 50A | #09 | CJ HELLOVISION | CJ HELLOVISION | #10 | 2P 50A |  | 2.57 |  |  | O | ON | A-6-A [A2-7-6]
[12 empty] | 총합: | 5.23 | 8.05 | 4.91
7-DaHall 1-RPP-04 |  |  | PDU : 7-DaHall 1-RPP-04
[7 empty] | [A] |  | Main CB 4P 225A |  |  | MAIN 계측값 : | 8.6 | 7.6 | 5.7 | <- 실측값
A-1-B [B2-7-1] | O | ON | 0 |  |  |  | 2P 50A | #01 | CJ HELLOVISION | NTT | #02 | 2P 50A | 1.55 |  |  |  | O | ON | D-4-B [D3-B]
A-2-B [B2-7-2] | O | ON |  | 3.32 |  |  | 2P 50A | #03 | CJ HELLOVISION | NTT | #04 | 2P 50A |  | 0 |  |  | X | OFF | G-7-B
A-3-B [B2-7-3] | O | ON |  |  | 4.45 |  | 2P 50A | #05 | CJ HELLOVISION | CJ HELLOVISION | #06 | 2P 50A |  |  | 1.19 |  | O | ON | A-7-B [B2-7-7]
A-4-B [B2-7-4] | O | ON | 4.09 |  |  |  | 2P 50A | #07 | CJ HELLOVISION | CJ HELLOVISION | #08 | 2P 50A | 1.91 |  |  |  | O | ON | A-8-B [B2-7-8]
A-5-B [B2-7-5] | O | ON |  | 1.61 |  |  | 2P 50A | #09 | CJ HELLOVISION | CJ HELLOVISION | #10 | 2P 50A |  | 2.8 |  |  | O | ON | A-6-B [B2-7-6]
[12 empty] | 총합: | 7.55 | 7.73 | 5.64
7-DaHall 1-PDU-03 |  |  | PDU : 7-DaHall 1-PDU-03 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 82.2 | 71.2 | 81.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
7-DaHall 1-RPP-01 | O | ON | 26.65 | 12.11 | 16.87 |  | 4P 225A | #01 | . |  | #02 | 4P 225A | 3.05 | 2.49 | 7.22 |  | O | ON | 8층 Office 분전반(창고)
7-DaHall 1-RPP-03 | O | ON | 5.27 | 7.93 | 4.91 |  | 4P 225A | #03 | . |  | #04 | 4P 225A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #05 |  |  | #06 | 4P 225A | 50.79 | 51.45 | 53.94 |  | O | ON | 정류기시스템#1
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #07 |  |  | #08 | 4P 225A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #09 |  |  | #10 | 4P 225A | 0 | 0 | 0 |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #11 |  |  | #12 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #13 |  |  | #14 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #15 |  |  | #16 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #17 |  |  | #18 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 4P 100A | #19 |  |  | #20 | 4P 100A |  |  |  |  | X | OFF
[12 empty] | 총합: | 85.76 | 73.98 | 82.94
7-DaHall 1-PDU-04 |  |  | PDU : 7-DaHall 1-PDU-04 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 88.3 | 66 | 69.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
정류기시스템#2 | O | ON | 44.75 | 45.63 | 47.97 |  | 3P 150A | #01 |  | . | #02 | 3P 150A | 37.09 | 11.58 | 17.88 |  | O | ON | 7-DaHall 1-RPP-02
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #03 | . | . | #04 | 3P 150A | 7.78 | 7.57 | 5.59 |  | O | ON | 7-DaHall 1-RPP-04
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #05 | . |  | #06 | 3P 150A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #07 |  |  | #08 | 3P 150A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #09 |  |  | #10 | 3P 150A | 0 | 0 | 0 |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #11 |  |  | #12 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #13 |  |  | #14 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #15 |  |  | #16 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #17 |  |  | #18 | 3P 100A |  |  |  |  | X | OFF
| O | OFF |  |  |  |  | 4P 50A | #19 |  |  | #20 | 4P 50A |  |  |  |  | O | OFF
[12 empty] | 총합: | 89.62 | 64.78 | 71.44
|  |  | 사용량 | 층 배분
DEK | IDC | IDC상면 | 191.74 | 27.3% | [7 empty] | 7-1-A1 | 27.14 | 12.74 | 16.93
| 세종 | 인터넷 | 153.87 | 21.91% | [7 empty] | 7-1-B1 | 37.47 | 12.18 | 17.83
| 전송 | 전송 | 41.92 | 5.969% | [7 empty] | 7-1-A3 | 5.23 | 8.05 | 4.91
| 전송 | 정류기 | 294.53 | 41.94% | [7 empty] | 7-1-B3 | 7.55 | 7.73 | 5.64
| 전송/인터넷 | NOC | 7.44 | 1.059% | [7 empty] | 7-1-A2 | 32.64 | 42.57 | 39.48
| 8F Office |  | 12.76 | 1.817% | [7 empty] | 7-1-B2 | 29.45 | 43.7 | 43.73
|  | 총 합 | 702.26 | 100% | [7 empty] | 세종 정류기 | 95.54 | 97.08 | 101.91
[12 empty] | 8F Office | 3.05 | 2.49 | 7.22
[12 empty] | 총계 | 702.26
154.4972
Note on K18: 이현상: 변익준M에게 확인 요구 (2021.03.05)
Note on T21: 이현상: 기존부하명 : 전산랙 440BAY(B)
Note on A36: 이현상: 기존부하명 : 409BAY-B
Note on A37: 이현상: 기존부하명 : 410BAY-B 전원
Note on A68: 이현상: 기존부하명 : 409BAY-A
Note on A69: 이현상: 기존부하명 : 410BAY-A 전원
Note on A76: 이현상: 부하명은 207BAY-A(2)이지만, 실사용은 208BAY임

## 7층_부하량(월간_MAX)
Date : 2024-01-01 ~ 2024-01-31
7-DaHall 1-RPP-01 |  |  | PDU : 7-DaHall 1-RPP-01 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 26 | 14 | 21.8 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
W-DCS 8000 | O | ON | 0 |  |  |  | 2P 20A | #01 | 전송 |  | #02 | 2P 30A | 0 |  |  |  | O | ON | TO 8F 보안실 UPS항온 항습기 모니터용PC
?? | O | ON |  | 0 |  |  | 2P 20A | #03 | 전송 | 넷피플 | #04 | 2P 30A |  | 0 |  |  | O | ON | E-4-B
?? | O | ON |  |  | 0 |  | 2P 20A | #05 | 전송 | 넷피플 | #06 | 2P 30A |  |  | 0 |  | O | OFF | E-3-B
517 BAY | O | ON | 0 |  |  |  | 2P 20A | #07 | 전송 | 전송 | #08 | 2P 30A | 2.4 |  |  |  | O | ON | 406BAY 405BAY DCN-1B
Voice사업팀 MMS용-B | X | OFF |  | 0 |  |  | 2P 20A | #09 | IDC | 전송 | #10 | 2P 30A |  | 1.68 |  |  | O | ON | 407BAY 406BAY DCN-2B
Voice사업팀 D-7 RACK | O | ON |  |  | 0 |  | 2P 20A | #11 | 니즈텔레콤 | 전송 | #12 | 2P 30A |  |  | 5.58 |  | O | ON | 408BAY 407BAY DCN-3B
ONS1064 SERVER | O | ON | 0 |  |  |  | 2P 20A | #13 | 전송 | 엑사넷 | #14 | 2P 30A | 7.19 |  |  |  | O | ON | E-8-B
NTT 하-1 | X | ON |  | 0 |  |  | 2P 20A | #15 | IDC | 델피콤 | #16 | 2P 30A |  | 2.66 |  |  | O | ON | F-5-B
8층 보안실 CCTV 모니터 | O | ON |  |  | 0 |  | 2P 20A | #17 | 공통 | CARANG ('23.09.19) | #18 | 2P 30A |  |  | 2.04 |  | O | ON | C604 / F-7-A
G-10-A | O | ON | 1.04 |  |  |  | 2P 20A | #19 | 신한금융투자 | IDC | #20 | 2P 30A | 1.51 |  |  |  | O | ON | 인터넷운영팀MAN RACK#2 전원A
NTT 하-3 | X | OFF |  | 0 |  |  | 2P 20A | #21 |  | NTT | #22 | 2P 30A |  | 0 |  |  | O | ON | G-4-B
C-7-A-Q1 | O | ON |  |  | 2.12 |  | 2P 20A | #23 | NTT | NTT | #24 | 2P 30A |  |  | 0 |  | O | ON | G-6-B
인터넷운영팀MAN RACK#2 전원B | O | ON | 1.53 |  |  |  | 2P 20A | #25 | IDC | 교환라우터(총무팀 ??) | #26 | 2P 30A | 4.54 |  |  |  | O | ON | F-3-B
NMS B-15 | O | ON |  | 3.53 |  |  | 2P 20A | #27 | 전송 | 공통 | #28 | 2P 30A |  | 4.32 |  |  | O | ON | 운용실콘센트
NMS B-16 | O | ON |  |  | 4.6 |  | 2P 20A | #29 | 전송 | 공통 | #30 | 2P 30A |  |  | 5.83 |  | O | ON | 운용실콘센트 창가1열
?? | O | ON | 6.61 |  |  |  | 2P 20A | #31 | 전송 | 전송 | #32 | 2P 30A | 0 |  |  |  | O | ON | 전산랙 410BAY(B)
G-5-B | O | ON |  | 0 |  |  | 2P 20A | #33 | NTT | 니즈텔레콤 | #34 | 2P 30A |  | 0 |  |  | O | OFF | D-6-B
G-1-B | O | ON |  |  | 0 |  | 2P 20A | #35 |  | 르네트 | #36 | 2P 30A |  |  | 4.03 |  | O | ON | E-9-B
C-7-B-Q1 | O | ON | 7.12 |  |  |  | 2P 20A | #37 | NTT | 니즈텔레콤 | #38 | 2P 30A | 2.29 |  |  |  | O | ON | D-7-B
G-2-B | O | ON |  | 0 |  |  | 2P 20A | #39 |  | IDC | #40 | 2P 30A |  | 5 |  |  | O | ON | 341BAY / IDC MAN POP AC전원(B)
[12 empty] | 총합: | 34.23 | 17.19 | 24.2
7-DaHall 1-PDU-02 |  |  | PDU : 7-DaHall 1-PDU-02 | [5 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 30.2 | 45.2 | 46.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
G-3-B (NTT#8-B) | O | ON |  | 0 |  |  | 2P 30A | #01 | NTT | 쿼드마이너 | #02 | 2P 30A |  | 0 |  |  | O | ON | C503 | 쿼드마이너 예약상면
7B-342BAY | O | ON |  |  | 5.27 |  | 2P 30A | #03 | 인터넷 IP 랙 |  | #04 | 2P 30A |  |  | 0 |  | O | ON | U3-7B-D1
| X | OFF | 0 |  |  |  | 2P 30A | #05 |  | NTT | #06 | 2P 30A | 0 |  |  |  | O | ON | U3-7B-D5 B
241BAY-B | O | ON |  | 6.34 |  |  | 2P 30A | #07 |  | 전송 | #08 | 2P 30A |  | 0 |  |  | O | ON | U3-7B-337
242BAY-B | O | ON |  |  | 6.04 |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  |  | 4.45 |  | O | ON | 7F-C-6-NTT#3-B
209Bay - B | O | ON | 5.72 |  |  |  | 2P 30A | #11 |  | NTT | #12 | 2P 30A | 0 |  |  |  | O | ON | U3-7B G-3-B
210Bay - B | O | ON |  | 5.27 |  |  | 2P 30A | #13 |  | DEKR Network Rack | #14 | 2P 30A |  | 3.16 |  |  | O | ON | 218Bay - A전원 ('22.01.12 투입)
TATA#1/B | O | ON |  |  | 1.09 |  | 2P 30A | #15 | TATA | DEKR Network Rack | #16 | 2P 30A |  |  | 3.11 |  | O | ON | 217Bay - A전원 ('22.01.12 투입)
208BAY-B | O | ON | 3.67 |  |  |  | 2P 30A | #17 |  | 318Bay - DEK Network Rack | #18 | 2P 30A | 2.1 |  |  |  | O | ON | 318BAY-B U3-7B-18
207BAY-B | O | ON |  | 9.23 |  |  | 2P 30A | #19 |  | 317Bay - DEK Network Rack | #20 | 2P 30A |  | 3.06 |  |  | O | ON | 317BAY-B U3-7B-20
206BAY-B | O | ON |  |  | 4.46 |  | 2P 30A | #21 |  | 316Bay - DEK Network Rack | #22 | 2P 30A |  |  | 1.98 |  | O | ON | 316BAY-B U3-7B-22
205BAY-B | O | ON | 2.89 |  |  |  | 2P 30A | #23 |  | 315Bay - DEK Network Rack | #24 | 2P 30A | 2.7 |  |  |  | O | ON | 315BAY-B U3-7B-24
204BAY-B | O | ON |  | 1.77 |  |  | 2P 30A | #25 |  | 314Bay - DEK Network Rack | #26 | 2P 30A |  | 3.65 |  |  | O | ON | 314BAY-B U3-7B-26
208BAY-B(2) | O | ON |  |  | 4.23 |  | 2P 30A | #27 |  | 313Bay - DEK Network Rack | #28 | 2P 30A |  |  | 5.84 |  | O | ON | 313BAY-B U3-7B-28
C604 / F-7-B | O | ON | 2.48 |  |  |  | 2P 30A | #29 | CARANG ('23.09.19) | 드림라인 | #30 | 2P 30A | 0.68 |  |  |  | O | ON | 301BAY U3-7B-30
U3-7B-31 B-6-B | O | ON |  | 3.79 |  |  | 2P 30A | #31 | 세종 인터넷(클라우드이음) | 203Bay - 세종-아톤AWS | #32 | 2P 30A |  | 1.91 |  |  | O | ON | 203Bay-B ('22.07.14 투입) U3-7B-32
B-7-B | O | ON |  |  | 8.6 |  | 2P 30A | #33 | 세종 인터넷(클라우드이음) | C909 (舊 C-02) / TATA#02 | #34 | 2P 30A |  |  | 0 |  | O | ON | C-02(C909-B) U3-7B-34
B-8-B | O | ON | 6.72 |  |  |  | 2P 30A | #35 | 세종 인터넷(클라우드이음) |  | #36 | 2P 30A | 0 |  |  |  | O | ON | B424(310BAY-B)
Test Bed #2 U3-7B-37 | O | ON |  | 0.69 |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  | 4.08 |  |  | O | ON | B423(311BAY-B)
7-1-B2-30-39 | O | ON |  |  | 1.87 |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  |  | 3.34 |  | O | ON | B422(312BAY-B)
7B-30-41(C409) | O | ON | 0 |  |  |  | 2P 30A | #41 | C409 |  | #42 | 2P 30A | 4.96 |  |  |  | O | ON | 7-1-B2-30-42
| X | OFF |  | 0 |  |  | 2P 30A | #43 |  | 쿼드마이너 | #44 | 2P 30A |  | 3.42 |  |  | O | ON | C502 | 2023/04/10 랙 반입 예정
| X | OFF |  |  | 0 |  | 2P 30A | #45 |  | 쿼드마이너 | #46 | 2P 30A |  |  | 0 |  | O | ON | C504 | 쿼드마이너 예약상면
| X | OFF | 0 |  |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A | 3.57 |  |  |  | X | OFF
신규BMS(20F TPS실) Rack | O | ON |  | 0.93 |  |  | 2P 30A | #49 | 20F BMS |  | #50 | 2P 30A |  | 3.82 |  |  | O | ON | 7층 출입카드
신규BMS(7F TPS실) Rack | O | ON |  |  | 0.56 |  | 2P 30A | #51 | 7F BMS |  | #52 | 2P 30A |  |  | 0 |  | O | ON | 20F MAIN (FMS)
7B-D5-#1 | O | ON | 0.24 |  |  |  | 2P 30A | #53 | NTT |  | #54 | 2P 30A | 0 |  |  |  | O | ON | 7F MAIN (FMS)
[12 empty] | 총합: | 35.73 | 51.12 | 50.84 | 0
7-DaHall 1-PDU-01 |  |  | PDU : 7-DaHall 1-PDU-01 | [5 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 33.4 | 43.4 | 40.1 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
G-3-A (NTT#8-A) | O | ON |  | 0 |  |  | 2P 30A | #01 | NTT | 쿼드마이너 | #02 | 2P 30A |  | 0 |  |  | O | ON | G-8-A (C503) | 쿼드마이너 예약상면
F-5-A | O | ON |  |  | 3.01 |  | 2P 30A | #03 | 텔피콤 |  | #04 | 2P 30A |  |  | 0 |  | O | ON | D-1-A
7A-342BAY | O | ON | 5.12 |  |  |  | 2P 30A | #05 | 인터넷 IP 랙 | NTT | #06 | 2P 30A | 0 |  |  |  | O | ON | D-5-A
241BAY-A | O | ON |  | 6.22 |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  | 2.29 |  |  | O | ON | 405BAY / U3-7A-405BAY(A)
242BAY-A | O | ON |  |  | 7.42 |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  |  | 2.84 |  | O | ON | C-6-A
209Bay - A | O | ON | 6.92 |  |  |  | 2P 30A | #11 | 인터넷 IP 랙 | NTT | #12 | 2P 30A | 0 |  |  |  | O | ON | U3-7A G-3-A
210Bay - A | O | ON |  | 6.72 |  |  | 2P 30A | #13 | 인터넷 IP 랙 | DEKR Network Rack | #14 | 2P 30A |  | 4.61 |  |  | O | ON | 218Bay - A전원 ('22.01.12 투입)
TATA#1/A | O | ON |  |  | 0.79 |  | 2P 30A | #15 | TATA | DEKR Network Rack | #16 | 2P 30A |  |  | 2.45 |  | O | ON | 217Bay - A전원 ('22.01.12 투입)
208BYA-A | O | ON | 3.24 |  |  |  | 2P 30A | #17 | 인터넷 IP 랙 | 318Bay - DEK Network Rack | #18 | 2P 30A | 2.14 |  |  |  | O | ON | 318BAY-A U3-7A-18
207BYA-A | O | ON |  | 4.21 |  |  | 2P 30A | #19 | 인터넷 IP 랙 | 317Bay - DEK Network Rack | #20 | 2P 30A |  | 1.88 |  |  | O | ON | 317BAY-A U3-7A-20
206BYA-A | O | ON |  |  | 4.12 |  | 2P 30A | #21 | 인터넷 IP 랙 | 316Bay - DEK Network Rack | #22 | 2P 30A |  |  | 1.77 |  | O | ON | 316BAY-A U3-7A-22
205BYA-A | O | ON | 2.09 |  |  |  | 2P 30A | #23 | 인터넷 IP 랙 | 315Bay - DEK Network Rack | #24 | 2P 30A | 3.18 |  |  |  | O | ON | 315BAY-A U3-7A-24
204BYA-A | O | ON |  | 1.65 |  |  | 2P 30A | #25 | 인터넷 IP 랙 | 314Bay - DEK Network Rack | #26 | 2P 30A |  | 3.46 |  |  | O | ON | 314BAY-A U3-7A-26
208BAY 207BAY - A(2) | O | ON |  |  | 3.58 |  | 2P 30A | #27 | 인터넷 IP 랙 | 313Bay - DEK Network Rack | #28 | 2P 30A |  |  | 5.63 |  | O | ON | 313BAY-A U3-7A-28
322BAY 331BAY | O | ON | 0.4 |  |  |  | 2P 30A | #29 | 김종원M 요구회로 | 드림라인 | #30 | 2P 30A | 0.35 |  |  |  | O | ON | 301BAY U3-7A-30
U3-7A-31 B-6-A | O | ON |  | 4.59 |  |  | 2P 30A | #31 | 세종 인터넷(클라우드이음) | 203Bay - 세종-아톤AWS | #32 | 2P 30A |  | 2.21 |  |  | O | ON | 203Bay-A ('22.07.14 투입) U3-7A-32
B-7-A | O | ON |  |  | 8.96 |  | 2P 30A | #33 | 세종 인터넷(클라우드이음) | C909 (舊 C-02) / TATA#02 | #34 | 2P 30A |  |  | 0 |  | O | ON | C-02(C909-A) U3-7A-34
B-8-A | O | ON | 7.11 |  |  |  | 2P 30A | #35 | 세종 인터넷(클라우드이음) |  | #36 | 2P 30A | 0 |  |  |  | O | ON | B424(310BAY-A)
Test Bed #1 U3-7A-37 | O | ON |  | 0 |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  | 3.02 |  |  | O | ON | B423(311BAY-A)
7-1-A2-30-39 | O | ON |  |  | 1.06 |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  |  | 3.67 |  | O | ON | B422(312BAY-A)
7A-30-41(C409) | O | ON | 1.07 |  |  |  | 2P 30A | #41 | C409 |  | #42 | 2P 30A | 3.48 |  |  |  | O | ON | 7-1-A2-30-42
| X | OFF |  | 0 |  |  | 2P 30A | #43 |  | 쿼드마이너 | #44 | 2P 30A |  | 8.03 |  |  | O | ON | C502 | 2023/04/10 랙 반입 예정
| X | OFF |  |  | 0 |  | 2P 30A | #45 |  | 쿼드마이너 | #46 | 2P 30A |  |  | 0 |  | O | ON | C504 | 쿼드마이너 예약상면
| X | OFF | 0 |  |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A | 2.9 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #51 |  |  | #52 | 2P 30A |  |  | 0 |  | O | ON | 7F NTT CCTV 전원
| X | OFF | 0 |  |  |  | 2P 30A | #53 |  | NTT | #54 | 2P 30A | 0.35 |  |  |  | O | ON | 7A-D5-#1
[12 empty] | 총합: | 38.35 | 48.89 | 45.3 | 0
7-DaHall 1-RPP-02 |  |  | PDU : 7-DaHall 1-RPP-02 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 39 | 12.5 | 20.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO | NO. | NO. | NO | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
강남방향 창가열 콘센트 | O | ON | 1.09 |  |  |  | 2P 20A | #01 | 공통 | 공통 | #02 | 2P 30A | 17.49 |  |  |  | O | ON | 정면창가 콘센트
?? | O | ON |  | 0.8 |  |  | 2P 20A | #03 | 공통 |  | #04 | 2P 30A |  | 0 |  |  | X | OFF | NTT 상-1
301 BAY | O | OFF |  |  | 0 |  | 2P 20A | #05 | 전송 | 전송 | #06 | 2P 30A |  |  | 0 |  | O | ON | GAINS
C2C DWDM EMS RACK | O | ON | 1.13 |  |  |  | 2P 20A | #07 | 전송 | NTT | #08 | 2P 30A | 6.67 |  |  |  | O | ON | C-8-A
405BAY / U3-7A-405BAY(A) | O | ON |  | 1.57 |  |  | 2P 20A | #09 | 전송 | 신한금융투자 | #10 | 2P 30A |  | 0.71 |  |  | O | ON | G-10-B
ONS1064 SERVER | O | ON |  |  | 0 |  | 2P 20A | #11 | 전송 | NTT | #12 | 2P 30A |  |  | 4.69 |  | O | ON | C-8-B
406BAY 405 BAY (DCN-1A) | O | ON | 2.92 |  |  |  | 2P 20A | #13 | 전송 | 유엔시스 | #14 | 2P 30A | 15.69 |  |  |  | O | ON | D-3-A
407BAY 406 BAY (DCN-2A) | O | ON |  | 1.77 |  |  | 2P 20A | #15 | 전송 | NTT | #16 | 2P 30A |  | 0 |  |  | O | ON | G-4-A (NTT#7)
408BAY 407 BAY (DCN-3A) | O | ON |  |  | 4.59 |  | 2P 20A | #17 | 전송 | NTT | #18 | 2P 30A |  |  | 0 |  | O | ON | G-6-A
E-2-A | O | ON | 0 |  |  |  | 2P 20A | #19 |  | 교환라우터(총무팀 ??) | #20 | 2P 30A | 1.2 |  |  |  | O | ON | F-3-A
E-5-A | X | OFF |  | 0 |  |  | 2P 20A | #21 | 니즈텔레콤 | 공통 | #22 | 2P 30A |  | 0 |  |  | O | ON | 운용실 바닥콘센트
E-6-A | O | ON |  |  | 0 |  | 2P 20A | #23 |  | 공통 | #24 | 2P 30A |  |  | 4.45 |  | O | ON | 운용실 콘센트 창가1열
E-7-A | O | ON | 0 |  |  |  | 2P 20A | #25 |  | 전송 | #26 | 2P 30A | 0.45 |  |  |  | O | ON | 전산랙 410 BAY-A
E-8-A | O | ON |  | 6.39 |  |  | 2P 20A | #27 | 엑사넷 | 니즈텔레콤 | #28 | 2P 30A |  | 0 |  |  | O | OFF | D-6-A
G-5-A | O | ON |  |  | 0 |  | 2P 20A | #29 | NTT | 르네트 | #30 | 2P 30A |  |  | 2.4 |  | O | ON | E-9-A
Voice사업팀 NMS용-A | X | OFF | 0 |  |  |  | 2P 20A | #31 | IDC | 니즈텔레콤 | #32 | 2P 30A | 3.73 |  |  |  | O | ON | D-7-A
NTT 상-3 | X | OFF |  | 0 |  |  | 2P 20A | #33 | IDC |  | #34 | 2P 30A |  | 0 |  |  | O | ON | F-8-A
7F NMS A-18 | O | ON |  |  | 3.11 |  | 2P 20A | #35 | 전송 | 델피콤 | #36 | 2P 30A |  |  | 8.22 |  | O | ON | F-6-A
7F NMS A-19 | O | ON | 6.52 |  |  |  | 2P 20A | #37 | 전송 | IDC | #38 | 2P 30A | 5.12 |  |  |  | O | ON | 341BAY / IDC MAN POP
7F NMS A-20 | O | ON |  | 14.65 |  |  | 2P 20A | #39 | 전송 |  | #40 | 2P 30A |  | 0 |  |  | O | ON | F-9-A
[12 empty] | 총합: | 62.01 | 25.89 | 27.46
7-DaHall 1-RPP-03 |  |  | PDU : 7-DaHall 1-RPP-03 | [5 empty] | Main CB 4P 225A
[12 empty] | MAIN 계측값 : | 6.8 | 8 | 5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A-1-A [A2-7-1] | O | ON | 1.19 |  |  |  | 2P 50A | #01 | CJ HELLOVISION | NTT | #02 | 2P 50A | 1.19 |  |  |  | O | ON | D-4-A [D3-A]
A-2-A [A2-7-2] | O | ON |  | 2.87 |  |  | 2P 50A | #03 | CJ HELLOVISION | NTT | #04 | 2P 50A |  | 0 |  |  | X | OFF | G-7-A
A-3-A [A2-7-3] | O | ON |  |  | 3.47 |  | 2P 50A | #05 | CJ HELLOVISION | CJ HELLOVISION | #06 | 2P 50A |  |  | 1.72 |  | O | ON | A-7-A [A2-7-7]
A-4-A [A2-7-4] | O | ON | 2.61 |  |  |  | 2P 50A | #07 | CJ HELLOVISION | CJ HELLOVISION | #08 | 2P 50A | 2.08 |  |  |  | O | ON | A-8-A [A2-7-8]
A-5-A [A2-7-5] | O | ON |  | 2.99 |  |  | 2P 50A | #09 | CJ HELLOVISION | CJ HELLOVISION | #10 | 2P 50A |  | 2.78 |  |  | O | ON | A-6-A [A2-7-6]
[12 empty] | 총합: | 7.07 | 8.64 | 5.19
7-DaHall 1-RPP-04 |  |  | PDU : 7-DaHall 1-RPP-04
[7 empty] | [A] |  | Main CB 4P 225A |  |  | MAIN 계측값 : | 8.6 | 7.6 | 5.7 | <- 실측값
A-1-B [B2-7-1] | O | ON | 6.2 |  |  |  | 2P 50A | #01 | CJ HELLOVISION | NTT | #02 | 2P 50A | 1.9 |  |  |  | O | ON | D-4-B [D3-B]
A-2-B [B2-7-2] | O | ON |  | 3.39 |  |  | 2P 50A | #03 | CJ HELLOVISION | NTT | #04 | 2P 50A |  | 0 |  |  | X | OFF | G-7-B
A-3-B [B2-7-3] | O | ON |  |  | 4.55 |  | 2P 50A | #05 | CJ HELLOVISION | CJ HELLOVISION | #06 | 2P 50A |  |  | 1.33 |  | O | ON | A-7-B [B2-7-7]
A-4-B [B2-7-4] | O | ON | 4.23 |  |  |  | 2P 50A | #07 | CJ HELLOVISION | CJ HELLOVISION | #08 | 2P 50A | 2.07 |  |  |  | O | ON | A-8-B [B2-7-8]
A-5-B [B2-7-5] | O | ON |  | 1.77 |  |  | 2P 50A | #09 | CJ HELLOVISION | CJ HELLOVISION | #10 | 2P 50A |  | 3.01 |  |  | O | ON | A-6-B [B2-7-6]
[12 empty] | 총합: | 14.4 | 8.17 | 5.88
7-DaHall 1-PDU-03 |  |  | PDU : 7-DaHall 1-PDU-03 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 82.2 | 71.2 | 81.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
7-DaHall 1-RPP-01 | O | ON | 30.18 | 15.55 | 21.14 |  | 4P 225A | #01 | . |  | #02 | 4P 225A | 4.42 | 4.19 | 9.23 |  | O | ON | 8층 Office 분전반(창고)
7-DaHall 1-RPP-03 | O | ON | 6.81 | 8.24 | 5.12 |  | 4P 225A | #03 | . |  | #04 | 4P 225A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #05 |  |  | #06 | 4P 225A | 52.53 | 53.02 | 55.71 |  | O | ON | 정류기시스템#1
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #07 |  |  | #08 | 4P 225A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #09 |  |  | #10 | 4P 225A | 0 | 0 | 0 |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #11 |  |  | #12 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #13 |  |  | #14 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #15 |  |  | #16 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #17 |  |  | #18 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 4P 100A | #19 |  |  | #20 | 4P 100A |  |  |  |  | X | OFF
[12 empty] | 총합: | 93.94 | 81 | 91.2
7-DaHall 1-PDU-04 |  |  | PDU : 7-DaHall 1-PDU-04 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 88.3 | 66 | 69.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
정류기시스템#2 | O | ON | 46.47 | 47.22 | 49.94 |  | 3P 150A | #01 |  | . | #02 | 3P 150A | 54.64 | 23.85 | 23.85 |  | O | ON | 7-DaHall 1-RPP-02
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #03 | . | . | #04 | 3P 150A | 9.11 | 7.82 | 5.78 |  | O | ON | 7-DaHall 1-RPP-04
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #05 | . |  | #06 | 3P 150A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #07 |  |  | #08 | 3P 150A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #09 |  |  | #10 | 3P 150A | 0 | 0 | 0 |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #11 |  |  | #12 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #13 |  |  | #14 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #15 |  |  | #16 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #17 |  |  | #18 | 3P 100A |  |  |  |  | X | OFF
| O | OFF |  |  |  |  | 4P 50A | #19 |  |  | #20 | 4P 50A |  |  |  |  | O | OFF
[12 empty] | 총합: | 110.22 | 78.89 | 79.57
|  |  | 사용량 | 층 배분
DEK | IDC | IDC상면 | 227.41 | 27.29% | [7 empty] | 7-1-A1 | 34.23 | 17.19 | 24.2
| 세종 | 인터넷 | 166.16 | 19.94% | [7 empty] | 7-1-B1 | 62.01 | 25.89 | 27.46
| 전송 | 전송 | 83.01 | 9.962% | [7 empty] | 7-1-A3 | 7.07 | 8.64 | 5.19
| 전송 | 정류기 | 304.89 | 36.59% | [7 empty] | 7-1-B3 | 14.4 | 8.17 | 5.88
| 전송/인터넷 | NOC | 33.98 | 4.078% | [7 empty] | 7-1-A2 | 38.35 | 48.89 | 45.3
| 8F Office |  | 17.84 | 2.141% | [7 empty] | 7-1-B2 | 35.73 | 51.12 | 50.84
|  | 총 합 | 833.29 | 100% | [7 empty] | 세종 정류기 | 99 | 100.24 | 105.65
[12 empty] | 8F Office | 4.42 | 4.19 | 9.23
[12 empty] | 총계 | 833.29
183.3238
Note on K18: 이현상: 변익준M에게 확인 요구 (2021.03.05)
Note on T21: 이현상: 기존부하명 : 전산랙 440BAY(B)
Note on A36: 이현상: 기존부하명 : 409BAY-B
Note on A37: 이현상: 기존부하명 : 410BAY-B 전원
Note on A68: 이현상: 기존부하명 : 409BAY-A
Note on A69: 이현상: 기존부하명 : 410BAY-A 전원
Note on A76: 이현상: 부하명은 207BAY-A(2)이지만, 실사용은 208BAY임

## 7층_부하량(월간_AVG)
Date : 2024-01-01 ~ 2024-01-31
7-DaHall 1-RPP-01 |  |  | PDU : 7-DaHall 1-RPP-01 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 26 | 14 | 21.8 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
W-DCS 8000 | O | ON | 0 |  |  |  | 2P 20A | #01 | 전송 |  | #02 | 2P 30A | 0 |  |  |  | O | ON | TO 8F 보안실 UPS항온 항습기 모니터용PC
?? | O | ON |  | 0 |  |  | 2P 20A | #03 | 전송 | 넷피플 | #04 | 2P 30A |  | 0 |  |  | O | ON | E-4-B
?? | O | ON |  |  | 0 |  | 2P 20A | #05 | 전송 | 넷피플 | #06 | 2P 30A |  |  | 0 |  | O | OFF | E-3-B
517 BAY | O | ON | 0 |  |  |  | 2P 20A | #07 | 전송 | 전송 | #08 | 2P 30A | 2.39 |  |  |  | O | ON | 406BAY 405BAY DCN-1B
Voice사업팀 MMS용-B | X | OFF |  | 0 |  |  | 2P 20A | #09 | IDC | 전송 | #10 | 2P 30A |  | 1.6797 |  |  | O | ON | 407BAY 406BAY DCN-2B
Voice사업팀 D-7 RACK | O | ON |  |  | 0 |  | 2P 20A | #11 | 니즈텔레콤 | 전송 | #12 | 2P 30A |  |  | 4.1494 |  | O | ON | 408BAY 407BAY DCN-3B
ONS1064 SERVER | O | ON | 0 |  |  |  | 2P 20A | #13 | 전송 | 엑사넷 | #14 | 2P 30A | 6.4544 |  |  |  | O | ON | E-8-B
NTT 하-1 | X | ON |  | 0 |  |  | 2P 20A | #15 | IDC | 델피콤 | #16 | 2P 30A |  | 2.6061 |  |  | O | ON | F-5-B
8층 보안실 CCTV 모니터 | O | ON |  |  | 0 |  | 2P 20A | #17 | 공통 | CARANG ('23.09.19) | #18 | 2P 30A |  |  | 1.5619 |  | O | ON | C604 / F-7-A
G-10-A | O | ON | 1.0023 |  |  |  | 2P 20A | #19 | 신한금융투자 | IDC | #20 | 2P 30A | 1.4935 |  |  |  | O | ON | 인터넷운영팀MAN RACK#2 전원A
NTT 하-3 | X | OFF |  | 0 |  |  | 2P 20A | #21 |  | NTT | #22 | 2P 30A |  | 0 |  |  | O | ON | G-4-B
C-7-A-Q1 | O | ON |  |  | 1.5585 |  | 2P 20A | #23 | NTT | NTT | #24 | 2P 30A |  |  | 0 |  | O | ON | G-6-B
인터넷운영팀MAN RACK#2 전원B | O | ON | 1.5116 |  |  |  | 2P 20A | #25 | IDC | 교환라우터(총무팀 ??) | #26 | 2P 30A | 3.3147 |  |  |  | O | ON | F-3-B
NMS B-15 | O | ON |  | 3.1544 |  |  | 2P 20A | #27 | 전송 | 공통 | #28 | 2P 30A |  | 1.6154 |  |  | O | ON | 운용실콘센트
NMS B-16 | O | ON |  |  | 4.1315 |  | 2P 20A | #29 | 전송 | 공통 | #30 | 2P 30A |  |  | 4.2718 |  | O | ON | 운용실콘센트 창가1열
?? | O | ON | 5.7882 |  |  |  | 2P 20A | #31 | 전송 | 전송 | #32 | 2P 30A | 0 |  |  |  | O | ON | 전산랙 410BAY(B)
G-5-B | O | ON |  | 0 |  |  | 2P 20A | #33 | NTT | 니즈텔레콤 | #34 | 2P 30A |  | 0 |  |  | O | OFF | D-6-B
G-1-B | O | ON |  |  | 0 |  | 2P 20A | #35 |  | 르네트 | #36 | 2P 30A |  |  | 3.4232 |  | O | ON | E-9-B
C-7-B-Q1 | O | ON | 6.1548 |  |  |  | 2P 20A | #37 | NTT | 니즈텔레콤 | #38 | 2P 30A | 2.2006 |  |  |  | O | ON | D-7-B
G-2-B | O | ON |  | 0 |  |  | 2P 20A | #39 |  | IDC | #40 | 2P 30A |  | 4.7992 |  |  | O | ON | 341BAY / IDC MAN POP AC전원(B)
[12 empty] | 총합: | 30.3101 | 13.8547 | 19.0963
7-DaHall 1-PDU-02 |  |  | PDU : 7-DaHall 1-PDU-02 | [5 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 30.2 | 45.2 | 46.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
G-3-B (NTT#8-B) | O | ON |  | 0 |  |  | 2P 30A | #01 | NTT | 쿼드마이너 | #02 | 2P 30A |  | 0 |  |  | O | ON | C503 | 쿼드마이너 예약상면
7B-342BAY | O | ON |  |  | 5.2018 |  | 2P 30A | #03 | 인터넷 IP 랙 |  | #04 | 2P 30A |  |  | 0 |  | O | ON | U3-7B-D1
| X | OFF | 0 |  |  |  | 2P 30A | #05 |  | NTT | #06 | 2P 30A | 0 |  |  |  | O | ON | U3-7B-D5 B
241BAY-B | O | ON |  | 5.7373 |  |  | 2P 30A | #07 |  | 전송 | #08 | 2P 30A |  | 0 |  |  | O | ON | U3-7B-337
242BAY-B | O | ON |  |  | 5.8618 |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  |  | 3.4529 |  | O | ON | 7F-C-6-NTT#3-B
209Bay - B | O | ON | 5.6908 |  |  |  | 2P 30A | #11 |  | NTT | #12 | 2P 30A | 0 |  |  |  | O | ON | U3-7B G-3-B
210Bay - B | O | ON |  | 5.2444 |  |  | 2P 30A | #13 |  | DEKR Network Rack | #14 | 2P 30A |  | 3.0858 |  |  | O | ON | 218Bay - A전원 ('22.01.12 투입)
TATA#1/B | O | ON |  |  | 1.08 |  | 2P 30A | #15 | TATA | DEKR Network Rack | #16 | 2P 30A |  |  | 2.958 |  | O | ON | 217Bay - A전원 ('22.01.12 투입)
208BAY-B | O | ON | 3.3793 |  |  |  | 2P 30A | #17 |  | 318Bay - DEK Network Rack | #18 | 2P 30A | 1.7399 |  |  |  | O | ON | 318BAY-B U3-7B-18
207BAY-B | O | ON |  | 8.9772 |  |  | 2P 30A | #19 |  | 317Bay - DEK Network Rack | #20 | 2P 30A |  | 1.9885 |  |  | O | ON | 317BAY-B U3-7B-20
206BAY-B | O | ON |  |  | 4.0522 |  | 2P 30A | #21 |  | 316Bay - DEK Network Rack | #22 | 2P 30A |  |  | 1.9621 |  | O | ON | 316BAY-B U3-7B-22
205BAY-B | O | ON | 2.6319 |  |  |  | 2P 30A | #23 |  | 315Bay - DEK Network Rack | #24 | 2P 30A | 2.2777 |  |  |  | O | ON | 315BAY-B U3-7B-24
204BAY-B | O | ON |  | 1.7329 |  |  | 2P 30A | #25 |  | 314Bay - DEK Network Rack | #26 | 2P 30A |  | 3.6147 |  |  | O | ON | 314BAY-B U3-7B-26
208BAY-B(2) | O | ON |  |  | 3.7863 |  | 2P 30A | #27 |  | 313Bay - DEK Network Rack | #28 | 2P 30A |  |  | 5.7776 |  | O | ON | 313BAY-B U3-7B-28
C604 / F-7-B | O | ON | 1.8013 |  |  |  | 2P 30A | #29 | CARANG ('23.09.19) | 드림라인 | #30 | 2P 30A | 0.56793 |  |  |  | O | ON | 301BAY U3-7B-30
U3-7B-31 B-6-B | O | ON |  | 3.712 |  |  | 2P 30A | #31 | 세종 인터넷(클라우드이음) | 203Bay - 세종-아톤AWS | #32 | 2P 30A |  | 1.8987 |  |  | O | ON | 203Bay-B ('22.07.14 투입) U3-7B-32
B-7-B | O | ON |  |  | 8.3825 |  | 2P 30A | #33 | 세종 인터넷(클라우드이음) | C909 (舊 C-02) / TATA#02 | #34 | 2P 30A |  |  | 0 |  | O | ON | C-02(C909-B) U3-7B-34
B-8-B | O | ON | 6.5469 |  |  |  | 2P 30A | #35 | 세종 인터넷(클라우드이음) |  | #36 | 2P 30A | 0 |  |  |  | O | ON | B424(310BAY-B)
Test Bed #2 U3-7B-37 | O | ON |  | 0.0040889 |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  | 3.8721 |  |  | O | ON | B423(311BAY-B)
7-1-B2-30-39 | O | ON |  |  | 1.8556 |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  |  | 3.0254 |  | O | ON | B422(312BAY-B)
7B-30-41(C409) | O | ON | 0 |  |  |  | 2P 30A | #41 | C409 |  | #42 | 2P 30A | 4.4681 |  |  |  | O | ON | 7-1-B2-30-42
| X | OFF |  | 0 |  |  | 2P 30A | #43 |  | 쿼드마이너 | #44 | 2P 30A |  | 2.3385 |  |  | O | ON | C502 | 2023/04/10 랙 반입 예정
| X | OFF |  |  | 0 |  | 2P 30A | #45 |  | 쿼드마이너 | #46 | 2P 30A |  |  | 0 |  | O | ON | C504 | 쿼드마이너 예약상면
| X | OFF | 0 |  |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A | 2.6815 |  |  |  | X | OFF
신규BMS(20F TPS실) Rack | O | ON |  | 0.90141 |  |  | 2P 30A | #49 | 20F BMS |  | #50 | 2P 30A |  | 3.5322 |  |  | O | ON | 7층 출입카드
신규BMS(7F TPS실) Rack | O | ON |  |  | 0.55004 |  | 2P 30A | #51 | 7F BMS |  | #52 | 2P 30A |  |  | 0 |  | O | ON | 20F MAIN (FMS)
7B-D5-#1 | O | ON | 0.23004 |  |  |  | 2P 30A | #53 | NTT |  | #54 | 2P 30A | 0 |  |  |  | O | ON | 7F MAIN (FMS)
[12 empty] | 총합: | 32.0153 | 46.6398 | 47.9462 | 0
7-DaHall 1-PDU-01 |  |  | PDU : 7-DaHall 1-PDU-01 | [5 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 33.4 | 43.4 | 40.1 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
G-3-A (NTT#8-A) | O | ON |  | 0 |  |  | 2P 30A | #01 | NTT | 쿼드마이너 | #02 | 2P 30A |  | 0 |  |  | O | ON | G-8-A (C503) | 쿼드마이너 예약상면
F-5-A | O | ON |  |  | 2.4923 |  | 2P 30A | #03 | 텔피콤 |  | #04 | 2P 30A |  |  | 0 |  | O | ON | D-1-A
7A-342BAY | O | ON | 4.9726 |  |  |  | 2P 30A | #05 | 인터넷 IP 랙 | NTT | #06 | 2P 30A | 0 |  |  |  | O | ON | D-5-A
241BAY-A | O | ON |  | 5.9719 |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  | 1.8243 |  |  | O | ON | 405BAY / U3-7A-405BAY(A)
242BAY-A | O | ON |  |  | 5.8963 |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  |  | 2.39 |  | O | ON | C-6-A
209Bay - A | O | ON | 6.8332 |  |  |  | 2P 30A | #11 | 인터넷 IP 랙 | NTT | #12 | 2P 30A | 0 |  |  |  | O | ON | U3-7A G-3-A
210Bay - A | O | ON |  | 6.6294 |  |  | 2P 30A | #13 | 인터넷 IP 랙 | DEKR Network Rack | #14 | 2P 30A |  | 4.2837 |  |  | O | ON | 218Bay - A전원 ('22.01.12 투입)
TATA#1/A | O | ON |  |  | 0.78998 |  | 2P 30A | #15 | TATA | DEKR Network Rack | #16 | 2P 30A |  |  | 2.3023 |  | O | ON | 217Bay - A전원 ('22.01.12 투입)
208BYA-A | O | ON | 2.9146 |  |  |  | 2P 30A | #17 | 인터넷 IP 랙 | 318Bay - DEK Network Rack | #18 | 2P 30A | 1.7558 |  |  |  | O | ON | 318BAY-A U3-7A-18
207BYA-A | O | ON |  | 3.9278 |  |  | 2P 30A | #19 | 인터넷 IP 랙 | 317Bay - DEK Network Rack | #20 | 2P 30A |  | 1.8689 |  |  | O | ON | 317BAY-A U3-7A-20
206BYA-A | O | ON |  |  | 3.95 |  | 2P 30A | #21 | 인터넷 IP 랙 | 316Bay - DEK Network Rack | #22 | 2P 30A |  |  | 1.7334 |  | O | ON | 316BAY-A U3-7A-22
205BYA-A | O | ON | 1.8176 |  |  |  | 2P 30A | #23 | 인터넷 IP 랙 | 315Bay - DEK Network Rack | #24 | 2P 30A | 2.7407 |  |  |  | O | ON | 315BAY-A U3-7A-24
204BYA-A | O | ON |  | 1.4568 |  |  | 2P 30A | #25 | 인터넷 IP 랙 | 314Bay - DEK Network Rack | #26 | 2P 30A |  | 3.4165 |  |  | O | ON | 314BAY-A U3-7A-26
208BAY 207BAY - A(2) | O | ON |  |  | 3.2932 |  | 2P 30A | #27 | 인터넷 IP 랙 | 313Bay - DEK Network Rack | #28 | 2P 30A |  |  | 5.5626 |  | O | ON | 313BAY-A U3-7A-28
322BAY 331BAY | O | ON | 0.003338 |  |  |  | 2P 30A | #29 | 김종원M 요구회로 | 드림라인 | #30 | 2P 30A | 0.34967 |  |  |  | O | ON | 301BAY U3-7A-30
U3-7A-31 B-6-A | O | ON |  | 4.519 |  |  | 2P 30A | #31 | 세종 인터넷(클라우드이음) | 203Bay - 세종-아톤AWS | #32 | 2P 30A |  | 2.1083 |  |  | O | ON | 203Bay-A ('22.07.14 투입) U3-7A-32
B-7-A | O | ON |  |  | 8.6702 |  | 2P 30A | #33 | 세종 인터넷(클라우드이음) | C909 (舊 C-02) / TATA#02 | #34 | 2P 30A |  |  | 0 |  | O | ON | C-02(C909-A) U3-7A-34
B-8-A | O | ON | 6.7996 |  |  |  | 2P 30A | #35 | 세종 인터넷(클라우드이음) |  | #36 | 2P 30A | 0 |  |  |  | O | ON | B424(310BAY-A)
Test Bed #1 U3-7A-37 | O | ON |  | 0 |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  | 2.808 |  |  | O | ON | B423(311BAY-A)
7-1-A2-30-39 | O | ON |  |  | 1.0399 |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  |  | 3.3906 |  | O | ON | B422(312BAY-A)
7A-30-41(C409) | O | ON | 1.0602 |  |  |  | 2P 30A | #41 | C409 |  | #42 | 2P 30A | 3.3412 |  |  |  | O | ON | 7-1-A2-30-42
| X | OFF |  | 0 |  |  | 2P 30A | #43 |  | 쿼드마이너 | #44 | 2P 30A |  | 6.7731 |  |  | O | ON | C502 | 2023/04/10 랙 반입 예정
| X | OFF |  |  | 0 |  | 2P 30A | #45 |  | 쿼드마이너 | #46 | 2P 30A |  |  | 0 |  | O | ON | C504 | 쿼드마이너 예약상면
| X | OFF | 0 |  |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A | 2.2292 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #51 |  |  | #52 | 2P 30A |  |  | 0 |  | O | ON | 7F NTT CCTV 전원
| X | OFF | 0 |  |  |  | 2P 30A | #53 |  | NTT | #54 | 2P 30A | 0.34008 |  |  |  | O | ON | 7A-D5-#1
[12 empty] | 총합: | 35.1578 | 45.5878 | 41.5109 | 0
7-DaHall 1-RPP-02 |  |  | PDU : 7-DaHall 1-RPP-02 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 39 | 12.5 | 20.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO | NO. | NO. | NO | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
강남방향 창가열 콘센트 | O | ON | 0.9106 |  |  |  | 2P 20A | #01 | 공통 | 공통 | #02 | 2P 30A | 0.28097 |  |  |  | O | ON | 정면창가 콘센트
?? | O | ON |  | 0.55027 |  |  | 2P 20A | #03 | 공통 |  | #04 | 2P 30A |  | 0 |  |  | X | OFF | NTT 상-1
301 BAY | O | OFF |  |  | 0 |  | 2P 20A | #05 | 전송 | 전송 | #06 | 2P 30A |  |  | 0 |  | O | ON | GAINS
C2C DWDM EMS RACK | O | ON | 1.1224 |  |  |  | 2P 20A | #07 | 전송 | NTT | #08 | 2P 30A | 6.0969 |  |  |  | O | ON | C-8-A
405BAY / U3-7A-405BAY(A) | O | ON |  | 1.1694 |  |  | 2P 20A | #09 | 전송 | 신한금융투자 | #10 | 2P 30A |  | 0.66886 |  |  | O | ON | G-10-B
ONS1064 SERVER | O | ON |  |  | 0 |  | 2P 20A | #11 | 전송 | NTT | #12 | 2P 30A |  |  | 4.3486 |  | O | ON | C-8-B
406BAY 405 BAY (DCN-1A) | O | ON | 2.8659 |  |  |  | 2P 20A | #13 | 전송 | 유엔시스 | #14 | 2P 30A | 14.0604 |  |  |  | O | ON | D-3-A
407BAY 406 BAY (DCN-2A) | O | ON |  | 1.7634 |  |  | 2P 20A | #15 | 전송 | NTT | #16 | 2P 30A |  | 0 |  |  | O | ON | G-4-A (NTT#7)
408BAY 407 BAY (DCN-3A) | O | ON |  |  | 3.0968 |  | 2P 20A | #17 | 전송 | NTT | #18 | 2P 30A |  |  | 0 |  | O | ON | G-6-A
E-2-A | O | ON | 0 |  |  |  | 2P 20A | #19 |  | 교환라우터(총무팀 ??) | #20 | 2P 30A | 0.6567 |  |  |  | O | ON | F-3-A
E-5-A | X | OFF |  | 0 |  |  | 2P 20A | #21 | 니즈텔레콤 | 공통 | #22 | 2P 30A |  | 0 |  |  | O | ON | 운용실 바닥콘센트
E-6-A | O | ON |  |  | 0 |  | 2P 20A | #23 |  | 공통 | #24 | 2P 30A |  |  | 2.2591 |  | O | ON | 운용실 콘센트 창가1열
E-7-A | O | ON | 0 |  |  |  | 2P 20A | #25 |  | 전송 | #26 | 2P 30A | 0.42936 |  |  |  | O | ON | 전산랙 410 BAY-A
E-8-A | O | ON |  | 5.8135 |  |  | 2P 20A | #27 | 엑사넷 | 니즈텔레콤 | #28 | 2P 30A |  | 0 |  |  | O | OFF | D-6-A
G-5-A | O | ON |  |  | 0 |  | 2P 20A | #29 | NTT | 르네트 | #30 | 2P 30A |  |  | 1.8465 |  | O | ON | E-9-A
Voice사업팀 NMS용-A | X | OFF | 0 |  |  |  | 2P 20A | #31 | IDC | 니즈텔레콤 | #32 | 2P 30A | 3.4779 |  |  |  | O | ON | D-7-A
NTT 상-3 | X | OFF |  | 0 |  |  | 2P 20A | #33 | IDC |  | #34 | 2P 30A |  | 0 |  |  | O | ON | F-8-A
7F NMS A-18 | O | ON |  |  | 2.539 |  | 2P 20A | #35 | 전송 | 델피콤 | #36 | 2P 30A |  |  | 7.3429 |  | O | ON | F-6-A
7F NMS A-19 | O | ON | 5.8492 |  |  |  | 2P 20A | #37 | 전송 | IDC | #38 | 2P 30A | 4.9175 |  |  |  | O | ON | 341BAY / IDC MAN POP
7F NMS A-20 | O | ON |  | 3.1025 |  |  | 2P 20A | #39 | 전송 |  | #40 | 2P 30A |  | 0 |  |  | O | ON | F-9-A
[12 empty] | 총합: | 40.6677 | 13.068 | 21.4329
7-DaHall 1-RPP-03 |  |  | PDU : 7-DaHall 1-RPP-03 | [5 empty] | Main CB 4P 225A
[12 empty] | MAIN 계측값 : | 6.8 | 8 | 5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A-1-A [A2-7-1] | O | ON | 1.1335 |  |  |  | 2P 50A | #01 | CJ HELLOVISION | NTT | #02 | 2P 50A | 0.88832 |  |  |  | O | ON | D-4-A [D3-A]
A-2-A [A2-7-2] | O | ON |  | 2.7946 |  |  | 2P 50A | #03 | CJ HELLOVISION | NTT | #04 | 2P 50A |  | 0 |  |  | X | OFF | G-7-A
A-3-A [A2-7-3] | O | ON |  |  | 3.4057 |  | 2P 50A | #05 | CJ HELLOVISION | CJ HELLOVISION | #06 | 2P 50A |  |  | 1.584 |  | O | ON | A-7-A [A2-7-7]
A-4-A [A2-7-4] | O | ON | 2.5091 |  |  |  | 2P 50A | #07 | CJ HELLOVISION | CJ HELLOVISION | #08 | 2P 50A | 1.9716 |  |  |  | O | ON | A-8-A [A2-7-8]
A-5-A [A2-7-5] | O | ON |  | 2.7464 |  |  | 2P 50A | #09 | CJ HELLOVISION | CJ HELLOVISION | #10 | 2P 50A |  | 2.6123 |  |  | O | ON | A-6-A [A2-7-6]
[12 empty] | 총합: | 6.5025 | 8.1534 | 4.9897
7-DaHall 1-RPP-04 |  |  | PDU : 7-DaHall 1-RPP-04
[7 empty] | [A] |  | Main CB 4P 225A |  |  | MAIN 계측값 : | 8.6 | 7.6 | 5.7 | <- 실측값
A-1-B [B2-7-1] | O | ON | 1.0665 |  |  |  | 2P 50A | #01 | CJ HELLOVISION | NTT | #02 | 2P 50A | 1.744 |  |  |  | O | ON | D-4-B [D3-B]
A-2-B [B2-7-2] | O | ON |  | 3.3461 |  |  | 2P 50A | #03 | CJ HELLOVISION | NTT | #04 | 2P 50A |  | 0 |  |  | X | OFF | G-7-B
A-3-B [B2-7-3] | O | ON |  |  | 4.4897 |  | 2P 50A | #05 | CJ HELLOVISION | CJ HELLOVISION | #06 | 2P 50A |  |  | 1.2212 |  | O | ON | A-7-B [B2-7-7]
A-4-B [B2-7-4] | O | ON | 4.1687 |  |  |  | 2P 50A | #07 | CJ HELLOVISION | CJ HELLOVISION | #08 | 2P 50A | 1.9433 |  |  |  | O | ON | A-8-B [B2-7-8]
A-5-B [B2-7-5] | O | ON |  | 1.6301 |  |  | 2P 50A | #09 | CJ HELLOVISION | CJ HELLOVISION | #10 | 2P 50A |  | 2.8519 |  |  | O | ON | A-6-B [B2-7-6]
[12 empty] | 총합: | 8.9224 | 7.8281 | 5.7108
7-DaHall 1-PDU-03 |  |  | PDU : 7-DaHall 1-PDU-03 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 82.2 | 71.2 | 81.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
7-DaHall 1-RPP-01 | O | ON | 28.6837 | 12.8868 | 18.4604 |  | 4P 225A | #01 | . |  | #02 | 4P 225A | 3.5694 | 2.9388 | 8.0101 |  | O | ON | 8층 Office 분전반(창고)
7-DaHall 1-RPP-03 | O | ON | 6.3958 | 8.0085 | 4.9588 |  | 4P 225A | #03 | . |  | #04 | 4P 225A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #05 |  |  | #06 | 4P 225A | 51.759 | 52.3709 | 54.9917 |  | O | ON | 정류기시스템#1
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #07 |  |  | #08 | 4P 225A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #09 |  |  | #10 | 4P 225A | 0 | 0 | 0 |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #11 |  |  | #12 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #13 |  |  | #14 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #15 |  |  | #16 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #17 |  |  | #18 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 4P 100A | #19 |  |  | #20 | 4P 100A |  |  |  |  | X | OFF
[12 empty] | 총합: | 90.408 | 76.2049 | 86.421
7-DaHall 1-PDU-04 |  |  | PDU : 7-DaHall 1-PDU-04 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 88.3 | 66 | 69.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
정류기시스템#2 | O | ON | 45.7119 | 46.5412 | 49.1551 |  | 3P 150A | #01 |  | . | #02 | 3P 150A | 38.6346 | 12.134 | 20.6119 |  | O | ON | 7-DaHall 1-RPP-02
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #03 | . | . | #04 | 3P 150A | 8.8396 | 7.6418 | 5.6394 |  | O | ON | 7-DaHall 1-RPP-04
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #05 | . |  | #06 | 3P 150A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #07 |  |  | #08 | 3P 150A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #09 |  |  | #10 | 3P 150A | 0 | 0 | 0 |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #11 |  |  | #12 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #13 |  |  | #14 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #15 |  |  | #16 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #17 |  |  | #18 | 3P 100A |  |  |  |  | X | OFF
| O | OFF |  |  |  |  | 4P 50A | #19 |  |  | #20 | 4P 50A |  |  |  |  | O | OFF
[12 empty] | 총합: | 93.1861 | 66.317 | 75.4065
|  |  | 사용량 | 층 배분
DEK | IDC | IDC상면 | 215.0306 | 28.88% | [7 empty] | 7-1-A1 | 30.3101 | 13.8547 | 19.0963
| 세종 | 인터넷 | 158.2138 | 21.25% | [7 empty] | 7-1-B1 | 40.6677 | 13.068 | 21.4329
| 전송 | 전송 | 46.2616 | 6.214% | [7 empty] | 7-1-A3 | 6.5025 | 8.1534 | 4.9897
| 전송 | 정류기 | 300.5299 | 40.37% | [7 empty] | 7-1-B3 | 8.9224 | 7.8281 | 5.7108
| 전송/인터넷 | NOC | 9.8881 | 1.328% | [7 empty] | 7-1-A2 | 35.1578 | 45.5878 | 41.5109
| 8F Office |  | 14.5183 | 1.95% | [7 empty] | 7-1-B2 | 32.0153 | 46.6398 | 47.9462
|  | 총 합 | 744.4424 | 100% | [7 empty] | 세종 정류기 | 97.4709 | 98.9121 | 104.1469
[12 empty] | 8F Office | 3.5694 | 2.9388 | 8.0101
[12 empty] | 총계 | 744.4424
163.7773
Note on K18: 이현상: 변익준M에게 확인 요구 (2021.03.05)
Note on T21: 이현상: 기존부하명 : 전산랙 440BAY(B)
Note on A36: 이현상: 기존부하명 : 409BAY-B
Note on A37: 이현상: 기존부하명 : 410BAY-B 전원
Note on A68: 이현상: 기존부하명 : 409BAY-A
Note on A69: 이현상: 기존부하명 : 410BAY-A 전원
Note on A76: 이현상: 부하명은 207BAY-A(2)이지만, 실사용은 208BAY임

## 7F_current (hidden)
7F | A(전류)
7-DaHall 1-PDU-01-01 | [branch#001] [A] current
7-DaHall 1-PDU-01-02 | [branch#002] [A] current
7-DaHall 1-PDU-01-03 | [branch#003] [A] current
7-DaHall 1-PDU-01-04 | [branch#004] [A] current
7-DaHall 1-PDU-01-05 | [branch#005] [A] current
7-DaHall 1-PDU-01-06 | [branch#006] [A] current
7-DaHall 1-PDU-01-07 | [branch#007] [A] current
7-DaHall 1-PDU-01-08 | [branch#008] [A] current
7-DaHall 1-PDU-01-09 | [branch#009] [A] current
7-DaHall 1-PDU-01-10 | [branch#010] [A] current
7-DaHall 1-PDU-01-11 | [branch#011] [A] current
7-DaHall 1-PDU-01-12 | [branch#012] [A] current
7-DaHall 1-PDU-01-13 | [branch#013] [A] current
7-DaHall 1-PDU-01-14 | [branch#014] [A] current
7-DaHall 1-PDU-01-15 | [branch#015] [A] current
7-DaHall 1-PDU-01-16 | [branch#016] [A] current
7-DaHall 1-PDU-01-17 | [branch#017] [A] current
7-DaHall 1-PDU-01-18 | [branch#018] [A] current
7-DaHall 1-PDU-01-19 | [branch#019] [A] current
7-DaHall 1-PDU-01-20 | [branch#020] [A] current
7-DaHall 1-PDU-01-21 | [branch#021] [A] current
7-DaHall 1-PDU-01-22 | [branch#022] [A] current
7-DaHall 1-PDU-01-23 | [branch#023] [A] current
7-DaHall 1-PDU-01-24 | [branch#024] [A] current
7-DaHall 1-PDU-01-25 | [branch#025] [A] current
7-DaHall 1-PDU-01-26 | [branch#026] [A] current
7-DaHall 1-PDU-01-27 | [branch#027] [A] current
7-DaHall 1-PDU-01-28 | [branch#028] [A] current
7-DaHall 1-PDU-01-29 | [branch#029] [A] current
7-DaHall 1-PDU-01-30 | [branch#030] [A] current
7-DaHall 1-PDU-01-31 | [branch#031] [A] current
7-DaHall 1-PDU-01-32 | [branch#032] [A] current
7-DaHall 1-PDU-01-33 | [branch#033] [A] current
7-DaHall 1-PDU-01-34 | [branch#034] [A] current
7-DaHall 1-PDU-01-35 | [branch#035] [A] current
7-DaHall 1-PDU-01-36 | [branch#036] [A] current
7-DaHall 1-PDU-01-37 | [branch#037] [A] current
7-DaHall 1-PDU-01-38 | [branch#038] [A] current
7-DaHall 1-PDU-01-39 | [branch#039] [A] current
7-DaHall 1-PDU-01-40 | [branch#040] [A] current
7-DaHall 1-PDU-01-41 | [branch#041] [A] current
7-DaHall 1-PDU-01-42 | [branch#042] [A] current
7-DaHall 1-PDU-01-43 | [branch#043] [A] current
7-DaHall 1-PDU-01-44 | [branch#044] [A] current
7-DaHall 1-PDU-01-45 | [branch#045] [A] current
7-DaHall 1-PDU-01-46 | [branch#046] [A] current
7-DaHall 1-PDU-01-47 | [branch#047] [A] current
7-DaHall 1-PDU-01-48 | [branch#048] [A] current
7-DaHall 1-PDU-01-49 | [branch#049] [A] current
7-DaHall 1-PDU-01-50 | [branch#050] [A] current
7-DaHall 1-PDU-01-51 | [branch#051] [A] current
7-DaHall 1-PDU-01-52 | [branch#052] [A] current
7-DaHall 1-PDU-01-53 | [branch#053] [A] current
7-DaHall 1-PDU-01-54 | [branch#054] [A] current
7-DaHall 1-PDU-02-01 | [branch#001] [A] current
7-DaHall 1-PDU-02-02 | [branch#002] [A] current
7-DaHall 1-PDU-02-03 | [branch#003] [A] current
7-DaHall 1-PDU-02-04 | [branch#004] [A] current
7-DaHall 1-PDU-02-05 | [branch#005] [A] current
7-DaHall 1-PDU-02-06 | [branch#006] [A] current
7-DaHall 1-PDU-02-07 | [branch#007] [A] current
7-DaHall 1-PDU-02-08 | [branch#008] [A] current
7-DaHall 1-PDU-02-09 | [branch#009] [A] current
7-DaHall 1-PDU-02-10 | [branch#010] [A] current
7-DaHall 1-PDU-02-11 | [branch#011] [A] current
7-DaHall 1-PDU-02-12 | [branch#012] [A] current
7-DaHall 1-PDU-02-13 | [branch#013] [A] current
7-DaHall 1-PDU-02-14 | [branch#014] [A] current
7-DaHall 1-PDU-02-15 | [branch#015] [A] current
7-DaHall 1-PDU-02-16 | [branch#016] [A] current
7-DaHall 1-PDU-02-17 | [branch#017] [A] current
7-DaHall 1-PDU-02-18 | [branch#018] [A] current
7-DaHall 1-PDU-02-19 | [branch#019] [A] current
7-DaHall 1-PDU-02-20 | [branch#020] [A] current
7-DaHall 1-PDU-02-21 | [branch#021] [A] current
7-DaHall 1-PDU-02-22 | [branch#022] [A] current
7-DaHall 1-PDU-02-23 | [branch#023] [A] current
7-DaHall 1-PDU-02-24 | [branch#024] [A] current
7-DaHall 1-PDU-02-25 | [branch#025] [A] current
7-DaHall 1-PDU-02-26 | [branch#026] [A] current
7-DaHall 1-PDU-02-27 | [branch#027] [A] current
7-DaHall 1-PDU-02-28 | [branch#028] [A] current
7-DaHall 1-PDU-02-29 | [branch#029] [A] current
7-DaHall 1-PDU-02-30 | [branch#030] [A] current
7-DaHall 1-PDU-02-31 | [branch#031] [A] current
7-DaHall 1-PDU-02-32 | [branch#032] [A] current
7-DaHall 1-PDU-02-33 | [branch#033] [A] current
7-DaHall 1-PDU-02-34 | [branch#034] [A] current
7-DaHall 1-PDU-02-35 | [branch#035] [A] current
7-DaHall 1-PDU-02-36 | [branch#036] [A] current
7-DaHall 1-PDU-02-37 | [branch#037] [A] current
7-DaHall 1-PDU-02-38 | [branch#038] [A] current
7-DaHall 1-PDU-02-39 | [branch#039] [A] current
7-DaHall 1-PDU-02-40 | [branch#040] [A] current
7-DaHall 1-PDU-02-41 | [branch#041] [A] current
7-DaHall 1-PDU-02-42 | [branch#042] [A] current
7-DaHall 1-PDU-02-43 | [branch#043] [A] current
7-DaHall 1-PDU-02-44 | [branch#044] [A] current
7-DaHall 1-PDU-02-45 | [branch#045] [A] current
7-DaHall 1-PDU-02-46 | [branch#046] [A] current
7-DaHall 1-PDU-02-47 | [branch#047] [A] current
7-DaHall 1-PDU-02-48 | [branch#048] [A] current
7-DaHall 1-PDU-02-49 | [branch#049] [A] current
7-DaHall 1-PDU-02-50 | [branch#050] [A] current
7-DaHall 1-PDU-02-51 | [branch#051] [A] current
7-DaHall 1-PDU-02-52 | [branch#052] [A] current
7-DaHall 1-PDU-02-53 | [branch#053] [A] current
7-DaHall 1-PDU-02-54 | [branch#054] [A] current
7-DaHall 1-PDU-03-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
7-DaHall 1-PDU-03-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
7-DaHall 1-PDU-03-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
7-DaHall 1-PDU-03-04 | [branch#004] [R] I1 | [branch#004] [S] I2 | [branch#004] [T] I3
7-DaHall 1-PDU-03-05 | [branch#005] [R] I1 | [branch#005] [S] I2 | [branch#005] [T] I3
7-DaHall 1-PDU-03-06 | [branch#006] [R] I1 | [branch#006] [S] I2 | [branch#006] [T] I3
7-DaHall 1-PDU-03-07 | [branch#007] [R] I1 | [branch#007] [S] I2 | [branch#007] [T] I3
7-DaHall 1-PDU-03-08 | [branch#008] [R] I1 | [branch#008] [S] I2 | [branch#008] [T] I3
7-DaHall 1-PDU-03-09 | [branch#009] [R] I1 | [branch#009] [S] I2 | [branch#009] [T] I3
7-DaHall 1-PDU-03-10 | [branch#010] [R] I1 | [branch#010] [S] I2 | [branch#010] [T] I3
7-DaHall 1-PDU-04-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
7-DaHall 1-PDU-04-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
7-DaHall 1-PDU-04-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
7-DaHall 1-PDU-04-04 | [branch#004] [R] I1 | [branch#004] [S] I2 | [branch#004] [T] I3
7-DaHall 1-PDU-04-05 | [branch#005] [R] I1 | [branch#005] [S] I2 | [branch#005] [T] I3
7-DaHall 1-PDU-04-06 | [branch#006] [R] I1 | [branch#006] [S] I2 | [branch#006] [T] I3
7-DaHall 1-PDU-04-07 | [branch#007] [R] I1 | [branch#007] [S] I2 | [branch#007] [T] I3
7-DaHall 1-PDU-04-08 | [branch#008] [R] I1 | [branch#008] [S] I2 | [branch#008] [T] I3
7-DaHall 1-PDU-04-09 | [branch#009] [R] I1 | [branch#009] [S] I2 | [branch#009] [T] I3
7-DaHall 1-PDU-04-10 | [branch#010] [R] I1 | [branch#010] [S] I2 | [branch#010] [T] I3
7-DaHall 1-RPP-01-01 | [branch#001] [A] current
7-DaHall 1-RPP-01-02 | [branch#002] [A] current
7-DaHall 1-RPP-01-03 | [branch#003] [A] current
7-DaHall 1-RPP-01-04 | [branch#004] [A] current
7-DaHall 1-RPP-01-05 | [branch#005] [A] current
7-DaHall 1-RPP-01-06 | [branch#006] [A] current
7-DaHall 1-RPP-01-07 | [branch#007] [A] current
7-DaHall 1-RPP-01-08 | [branch#008] [A] current
7-DaHall 1-RPP-01-09 | [branch#009] [A] current
7-DaHall 1-RPP-01-10 | [branch#010] [A] current
7-DaHall 1-RPP-01-11 | [branch#011] [A] current
7-DaHall 1-RPP-01-12 | [branch#012] [A] current
7-DaHall 1-RPP-01-13 | [branch#013] [A] current
7-DaHall 1-RPP-01-14 | [branch#014] [A] current
7-DaHall 1-RPP-01-15 | [branch#015] [A] current
7-DaHall 1-RPP-01-16 | [branch#016] [A] current
7-DaHall 1-RPP-01-17 | [branch#017] [A] current
7-DaHall 1-RPP-01-18 | [branch#018] [A] current
7-DaHall 1-RPP-01-19 | [branch#019] [A] current
7-DaHall 1-RPP-01-20 | [branch#020] [A] current
7-DaHall 1-RPP-01-21 | [branch#021] [A] current
7-DaHall 1-RPP-01-22 | [branch#022] [A] current
7-DaHall 1-RPP-01-23 | [branch#023] [A] current
7-DaHall 1-RPP-01-24 | [branch#024] [A] current
7-DaHall 1-RPP-01-25 | [branch#025] [A] current
7-DaHall 1-RPP-01-26 | [branch#026] [A] current
7-DaHall 1-RPP-01-27 | [branch#027] [A] current
7-DaHall 1-RPP-01-28 | [branch#028] [A] current
7-DaHall 1-RPP-01-29 | [branch#029] [A] current
7-DaHall 1-RPP-01-30 | [branch#030] [A] current
7-DaHall 1-RPP-01-31 | [branch#031] [A] current
7-DaHall 1-RPP-01-32 | [branch#032] [A] current
7-DaHall 1-RPP-01-33 | [branch#033] [A] current
7-DaHall 1-RPP-01-34 | [branch#034] [A] current
7-DaHall 1-RPP-01-35 | [branch#035] [A] current
7-DaHall 1-RPP-01-36 | [branch#036] [A] current
7-DaHall 1-RPP-01-37 | [branch#037] [A] current
7-DaHall 1-RPP-01-38 | [branch#038] [A] current
7-DaHall 1-RPP-01-39 | [branch#039] [A] current
7-DaHall 1-RPP-01-40 | [branch#040] [A] current
7-DaHall 1-RPP-02-01 | [branch#001] [A] current
7-DaHall 1-RPP-02-02 | [branch#002] [A] current
7-DaHall 1-RPP-02-03 | [branch#003] [A] current
7-DaHall 1-RPP-02-04 | [branch#004] [A] current
7-DaHall 1-RPP-02-05 | [branch#005] [A] current
7-DaHall 1-RPP-02-06 | [branch#006] [A] current
7-DaHall 1-RPP-02-07 | [branch#007] [A] current
7-DaHall 1-RPP-02-08 | [branch#008] [A] current
7-DaHall 1-RPP-02-09 | [branch#009] [A] current
7-DaHall 1-RPP-02-10 | [branch#010] [A] current
7-DaHall 1-RPP-02-11 | [branch#011] [A] current
7-DaHall 1-RPP-02-12 | [branch#012] [A] current
7-DaHall 1-RPP-02-13 | [branch#013] [A] current
7-DaHall 1-RPP-02-14 | [branch#014] [A] current
7-DaHall 1-RPP-02-15 | [branch#015] [A] current
7-DaHall 1-RPP-02-16 | [branch#016] [A] current
7-DaHall 1-RPP-02-17 | [branch#017] [A] current
7-DaHall 1-RPP-02-18 | [branch#018] [A] current
7-DaHall 1-RPP-02-19 | [branch#019] [A] current
7-DaHall 1-RPP-02-20 | [branch#020] [A] current
7-DaHall 1-RPP-02-21 | [branch#021] [A] current
7-DaHall 1-RPP-02-22 | [branch#022] [A] current
7-DaHall 1-RPP-02-23 | [branch#023] [A] current
7-DaHall 1-RPP-02-24 | [branch#024] [A] current
7-DaHall 1-RPP-02-25 | [branch#025] [A] current
7-DaHall 1-RPP-02-26 | [branch#026] [A] current
7-DaHall 1-RPP-02-27 | [branch#027] [A] current
7-DaHall 1-RPP-02-28 | [branch#028] [A] current
7-DaHall 1-RPP-02-29 | [branch#029] [A] current
7-DaHall 1-RPP-02-30 | [branch#030] [A] current
7-DaHall 1-RPP-02-31 | [branch#031] [A] current
7-DaHall 1-RPP-02-32 | [branch#032] [A] current
7-DaHall 1-RPP-02-33 | [branch#033] [A] current
7-DaHall 1-RPP-02-34 | [branch#034] [A] current
7-DaHall 1-RPP-02-35 | [branch#035] [A] current
7-DaHall 1-RPP-02-36 | [branch#036] [A] current
7-DaHall 1-RPP-02-37 | [branch#037] [A] current
7-DaHall 1-RPP-02-38 | [branch#038] [A] current
7-DaHall 1-RPP-02-39 | [branch#039] [A] current
7-DaHall 1-RPP-02-40 | [branch#040] [A] current
7-DaHall 1-RPP-03-01 | [branch#001] [A] current
7-DaHall 1-RPP-03-02 | [branch#002] [A] current
7-DaHall 1-RPP-03-03 | [branch#003] [A] current
7-DaHall 1-RPP-03-04 | [branch#004] [A] current
7-DaHall 1-RPP-03-05 | [branch#005] [A] current
7-DaHall 1-RPP-03-06 | [branch#006] [A] current
7-DaHall 1-RPP-03-07 | [branch#007] [A] current
7-DaHall 1-RPP-03-08 | [branch#008] [A] current
7-DaHall 1-RPP-03-09 | [branch#009] [A] current
7-DaHall 1-RPP-03-10 | [branch#010] [A] current
7-DaHall 1-RPP-04-01 | [branch#001] [A] current
7-DaHall 1-RPP-04-02 | [branch#002] [A] current
7-DaHall 1-RPP-04-03 | [branch#003] [A] current
7-DaHall 1-RPP-04-04 | [branch#004] [A] current
7-DaHall 1-RPP-04-05 | [branch#005] [A] current
7-DaHall 1-RPP-04-06 | [branch#006] [A] current
7-DaHall 1-RPP-04-07 | [branch#007] [A] current
7-DaHall 1-RPP-04-08 | [branch#008] [A] current
7-DaHall 1-RPP-04-09 | [branch#009] [A] current
7-DaHall 1-RPP-04-10 | [branch#010] [A] current

## 6층_부하량(월간_MIN)
Date : 2024-01-01 ~ 2024-01-31
6-DaHall 1-CEP-05 | [7 empty] | Main CB 4P 350A
[10 empty] | MAIN 계측값 : | 2.3 | 2.1 | 2.9 | <- 실측값 |  |  | 5-DaHall 1-EH-01
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
5-DaHall 1-CEP-06 | O | ON | 0 | 0.75 | 0.68 |  | 4P 150A | #01
| X | OFF | 사 | 용 | 금 | 지 | 4P 50A | #02 | #03 | 4P 50A | 0 | 0 | 0 |  | X | OFF
5-DaHall 1-CRAC-14 (CF CRAC #02) | O | ON | 0 | 0 | 0 |  | 4P 50A | #04 | #05 | 4P 50A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 50A | #06 | #07 | 4P 50A | 0 | 0 | 0 |  | O | OFF | 급배기휀
| X | OFF | 0 | 0 | 0 |  | 4P 50A | #08 | #09 | 4P 50A | 0 | 0 | 0 |  | X | OFF
spare | X | OFF | 0 | 0 | 0 |  | 4P 50A | #10 | #11 | 4P 100A | 2.19 | 1.81 | 3.13 |  | O | ON | 8층 냉방분전반
| O | OFF | 0 |  |  |  | 2P 30A | #12 | #13 | 2P 30A | 0 |  |  |  | O | OFF
| O | OFF |  | 0 |  |  | 2P 30A | #14 | #15 | 2P 50A |  | 5.15 |  |  | O | ON | 7-DaHall 1-EH (7층 가습기 Main)
| O | OFF |  |  | 0 |  | 2P 30A | #16 | #17 | 2P 50A |  |  | 6.93 |  | O | ON | 6-DaHall 1-EH (6층 가습기 Main)
|  | 6층 사무실 | 12.08 | [6 empty] | 총합: | 2.19 | 7.71 | 10.74 | 0
[11 empty] | 20.64 | 12.08 | 58.53%
6-DaHall 1-PDU-13 |  | PDU : SEL1 - 6-1 - A7 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A7-18-6 | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | DE운용실 사무#1 A7-30-8
A7-18-7 | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | DE 출입통제Desk A7-31-1
A7-18-8 | O | ON | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | 6F DE 가청경보 PNL
A7-18-9 | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | OFF | A7-31-3
A7-28-1 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-4
A7-28-2 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | OFF | A7-31-5
A7-28-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | OFF | A7-31-6
A7-28-4 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-7
A7-28-5 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | A7-31-8
A7-28-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | #A7-28-3
A7-28-7 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | OFF | #A7-28-6
A7-28-8 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | OFF | #A7-29-3
A7-29-1 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | OFF | #A7-29-6
A7-29-2 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | A7-21-4(3) (M-14)
A7-29-3 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | A7-21-3(3) (M-13)
A7-29-4 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | A7-21-3(2) (M-13)
A7-29-5 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | A7-21-4(2) (M-14)
A7-29-6 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | OFF | A7-26-8(2)
A7-29-7 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | OFF | A7-26-9(2)
A7-29-8 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A7-28-9 (6층 인터넷장비)
A7-30-1 | O | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | OFF | A7-29-9
A7-30-2 | O | OFF |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | OFF | A7-30-9
A7-30-3 | O | OFF |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-9
A7-30-4 | O | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | A7-27-6
A7-30-5 | O | OFF |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | A7-26-6
A7-30-6 | O | OFF |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | ON | A4-19-1 (O-11)
A7-30-7 | O | OFF | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | OFF | A4-27-9 (G-19)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-14 |  | PDU : SEL1 - 6-1 - B7 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B7-18-6 | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | DE운용실 감시모니터 B7-30-8
B7-18-7 | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | DE운용실 사무#2 B7-31-1
B7-18-8 | O | ON | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-2
B7-18-9 | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | OFF | B7-31-3
B7-28-1 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-4
B7-28-2 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-5
B7-28-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | OFF | B7-31-6
B7-28-4 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-7
B7-28-5 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-8
B7-28-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | ON | B7-32-1 (사무실)
B7-28-7 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | OFF | B7-32-2 (사무실)
B7-28-8 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | OFF | B7-32-3 (사무실)
B7-29-1 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | OFF | B7-32-4 (사무실)
B7-29-2 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | B7-21-4(3) (M-14)
B7-29-3 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | B7-21-3(3) (M-13)
B7-29-4 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | B7-21-4(2) (M-13)
B7-29-5 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | B7-21-3(2) (M-14)
B7-29-6 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | OFF | B7-26-8(2)
B7-29-7 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | OFF | B7-26-9(2)
B7-29-8 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | OFF | B7-28-9
B7-30-1 | O | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | OFF | B7-29-9
B7-30-2 | O | OFF |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | OFF | B7-30-9
B7-30-3 | O | OFF |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-9
B7-30-4 | O | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | B7-26-6
B7-30-5 | O | OFF |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | B7-27-6
B7-30-6 | O | OFF |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | ON | B4-19-1 (O-11)
B7-30-7 | O | OFF | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | OFF | A4-27-8
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-09 |  | PDU : SEL1 - 6-1 - A5 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A3-21-1 (M-11) | O | ON | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | ON | A3-22-1 (L-11)
A3-21-2 (M-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | ON | A3-22-2 (L-12)
A3-21-3 (M-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | ON | A3-22-3 (L-13)
A3-21-4 (M-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | ON | A3-22-4 (L-14)
A3-21-5 (M-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | A3-22-5 (L-15)
A3-21-6 (M-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | A3-22-6 (L-16)
A3-21-7 (M-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | A3-22-7 (L-17)
A3-21-8 (M-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A3-22-8 (L-18)
A3-21-9 (M-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A3-22-9 (L-19)
#A3-19-4 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | A3-23-1 (K-11)
#A3-19-7 | O | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | A3-23-2 (K-12)
#A3-36-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A3-23-3 (K-13)
#A3-36-6 | O | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | A3-23-4 (K-14)
#A3-23-4 (K-14) | O | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | A3-23-5 (K-15)
#A3-23-7 (K-17) | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | A3-23-6 (K-16)
B4-19-7 (O-17) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | A3-23-7 / 6F-K-17
#A3-24-7 | O | OFF |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | A3-23-8 / 6F-K-18)
A3-24-8 (J-18) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | ON | A3-23-9 / 6F-K-19
A3-24-9 (J-19) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-1 (J-11)
#A3-25-4 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | A3-24-2 (J-12)
#A3-26-4 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | A3-24-3 (J-13)
#A3-27-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-4 (J-14)
A3-27-1 (G-11) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | A3-24-5 (J-15)
A3-27-2 (G-12) | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | OFF | A3-24-6 (J-16)
A3-27-3 (G-13) | O | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-7 (J-17)
[10 empty] | 총합: | 0 | 0 | 0 | 0
6-DaHall 1-PDU-10 |  | PDU : SEL1 - 6-1 - B5 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B3-21-1 (M-11) | O | ON | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | ON | B3-22-1 (L-11)
B3-21-2 (M-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | ON | B3-22-2 (L-12)
B3-21-3 (M-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | ON | B3-22-3 (L-13)
B3-21-4 (M-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | ON | B3-22-4 (L-14)
B3-21-5 (M-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | B3-22-5 (L-15)
B3-21-6 (M-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | B3-22-6 (L-16)
B3-21-7 (M-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | B3-22-7 (L-17)
B3-21-8 (M-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B3-22-8 (L-18)
B3-21-9 (M-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B3-22-9 (L-19)
#B3-20-4 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | B3-23-1 (K-11)
#B3-20-7 (N-17) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | B3-23-2 (K-12)
#B3-21-4 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B3-24-6 (J-16)
#B3-21-7 | O | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | B3-23-4 (K-14)
#B3-22-4 | O | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | B3-23-5 (K-15)
#B3-22-7 | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | B3-23-6 (K-16)
#B3-25-7 | O | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | B3-23-7 / 6F-K-17
#B3-26-7 | O | OFF |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B3-23-8 / 6F-K-18
B3-24-8 (J-18) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | ON | B3-23-9 / 6F-K-19
B3-24-9 (J-19) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-1 (J-11)
#B3-27-7 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | B3-24-2 (J-12)
B3-27-1 (G-11) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | B3-24-3 (J-13)
B3-27-2 (G-12) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-4 (J-14)
B3-27-3 (G-13) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | B3-24-5 (J-15)
spare | X | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B3-23-3 (K-13)
spare | X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-7 (J-17)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-11 |  | PDU : SEL1 - 6-1 - A6 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 5.1 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | OFF | A4-20-1 (N-11)
A4-19-2 (O-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | OFF | A4-20-2 (N-12)
A4-19-3 (O-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | OFF | A4-20-3 (N-13)
A4-19-4 (O-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | OFF | A4-20-4 (N-14)
A4-19-5 (O-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | A4-20-5 (N-15)
A4-19-6 (O-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | A4-20-6 (N-16)
A4-19-7 (O-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | A4-20-7 (N-17)
A4-19-8 (O-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A4-20-8 (N-18)
A4-19-9 (O-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A4-20-9 (N-19)
A4-36-1 (AG-19) | O | ON | 4.92 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | A4-25-9 (I-19)
A4-36-2 (S-10) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-1 (H-11)
A4-36-3 (S-11) | O | ON |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-2 (H-12)
A4-36-4 (S-12) | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | OFF | A4-26-3 (H-13)
A4-36-5 (S-13) | O | ON |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-4 (H-14)
A4-36-6 (S-14) | O | ON |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-5 (H-15)
A4-36-7 (S-15) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | X | OFF
A4-36-8 (S-16) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-7 (H-17)
A4-25-1 (I-11) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-8 (H-18)
A4-25-2 (I-12) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | A4-26-9 (H-19)
A4-25-3 (I-13) | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | A4-27-4 (G-14)
A4-25-4 (I-14) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | A4-27-5 (G-15)
A4-25-5 (I-15) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | A4-36-9 (AG-20)
A4-25-6 (I-16) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | A4-27-7 (G-17)
Rack S-15 | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | X | OFF
Rack S-13 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 4.92 | 0 | 0
6-DaHall 1-PDU-12 |  | PDU : SEL1 - 6-1 - B6 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 5.1 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-1 (N-11)
B4-19-2 (O-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B4-20-2 (N-12)
B4-19-3 (O-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | OFF | B4-20-3 (N-13)
B4-19-4 (O-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-4 (N-14)
B4-19-5 (O-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | B4-20-5 (N-15)
B4-19-6 (O-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | B4-20-6 (N-16)
#A3-24-4 | O | OFF | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-7 (N-17)
B4-19-8 (O-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B4-20-8 (N-18)
B4-19-9 (O-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B4-20-9 (N-19)
B4-36-1 (AG-19) | O | ON | 4.84 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | B4-25-9 (I-19)
B4-36-2 (S-10) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-1 (H-11)
B4-36-3 (S-11) | O | ON |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-2 (H-12)
B4-36-4 (S-12) | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B4-26-3 (H-13)
B4-36-5 (S-13) | O | ON |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-4 (H-14)
B4-36-6 (S-14) | O | ON |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-5 (H-15)
B4-36-7 (S-15) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | X | OFF
B4-36-8 (S-16) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-7 (H-17)
B4-25-1 (I-11) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-8 (H-18)
B4-25-2 (I-12) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | B4-26-9 (H-19)
B4-25-3 (I-13) | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | B4-27-4 (G-14)
B4-25-4 (I-14) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | B4-27-5 (G-15)
B4-25-5 (I-15) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B4-36-9 (AG-20)
B4-25-6 (I-16) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | B4-27-7 (G-17)
Rack S-15 | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | OFF | B4-27-8 (G-18)
Rack S-13 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | B4-27-9 (G-19)
[10 empty] | 총합: | 4.84 | 0 | 0
6-DaHall 1-PDU-01 |  | PDU : SEL1 - 6-1 - A1 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 21.6 | 21.2 | 16.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A1-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 1.95 |  |  |  | O | ON | G1101(A)
A1-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 2.28 |  |  | O | ON | G1103(A)
A1-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 2.95 |  | O | ON | A1-35-3(AG-13)
A1-1-4 (AF-16) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 4.83 |  |  |  | O | ON | A1-35-4(AG-14)
A1-1-5 (AF-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 5.89 |  |  | O | ON | A1-35-5(AG-15)
A1-1-6 (AF-14) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 6.93 |  | O | ON | A1-35-6(AG-16)
A1-1-7 (AF-13) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 4.67 |  |  |  | O | ON | A1-35-7(AG-17)
A1-1-8 (AF-12) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 4.73 |  |  | O | ON | A1-35-8 (AG-18)
A1-1-9 (AF-11) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A1-16-4 (R-14)
#A1-1-3 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | A1-16-5 (R-15)
#A1-1-7 | O | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | A1-16-6 (R-16)
#A1-35-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A1-16-7 (R-17)
6-1-A1-30-25 | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | A1-16-8 (R-18)
A1-13-1 (AA-11) | O | ON |  | 2.24 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | A1-16-9 (R-19)
A1-13-2 (AA-12) | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | OFF | #A1-13-4
A1-13-3 (AA-13) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | OFF | #A1-16-4
A1-13-4 (AA-14) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | X | OFF | A1-4-1
A1-13-5 (AA-15) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0.28 |  | O | ON | G1102(A)
A1-13-6 (AA-16) | O | ON | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | X | OFF | G1102 하부(미사용)
A1-13-7 (AA-17) | O | ON |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | A1-35-3(2)(위치 불명)
B209 / (AA-18) | O | ON |  |  | 0.64 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 3.62 |  | O | ON | B411
A1-13-9 (B410) | O | ON | 2.78 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B211 | A1-30-44 를 B211에 포설 예정('23.05월초)
A1-16-1 (R-11) | O | ON |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0.55 |  |  | O | ON | 신규 BMS(6F TPS실) Rack
A1-16-2 (R-12) | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | A1-4-8 (AC-12)
B210 / (AA-19) | O | OFF | 3.14 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | ON | FMS 6층 전원
[10 empty] | 총합: | 17.37 | 15.69 | 14.42
6-DaHall 1-PDU-02 |  | PDU : SEL1 - 6-1 - B1 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 19.2 | 18.8 | 21.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B1-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 1.47 |  |  |  | O | ON | G1101 (B)
B1-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 1.78 |  |  | O | ON | G1103 (B)
B1-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 4.93 |  | O | ON | B1-35-3(AG-13)
B1-1-4 (AF-16) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 3.32 |  |  |  | O | ON | B1-35-4(AG-14)
B1-1-5 (AF-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 5.63 |  |  | O | ON | B1-35-5(AG-15)
B1-1-6 (AF-14) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 8.9 |  | O | ON | B1-35-6(AG-16)
B1-1-7 (AF-13) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 6.23 |  |  |  | O | ON | B1-35-7(AG-17)
B1-1-8 (AF-12) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 4.81 |  |  | O | ON | B1-35-8 (AG-18)
B1-1-9 (AF-11) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | X | OFF | 6-1-B1-30-18
#B1-2-3 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | B1-16-5 (R-15)
#B1-2-7 | O | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | B1-16-6 (R-16)
#B1-3-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | B1-16-7 (R-17)
6-1-B1-30-25 | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | B1-16-8 (R-18)
B1-13-1 (AA-11) | O | ON |  | 1.33 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | B1-16-9 (R-19)
B1-13-2 (AA-12) | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 3.16 |  | O | OFF | B210 / (AA-19) | B1-30-30 사용예정
B1-13-3 (AA-13) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | OFF | #B1-16-7
B1-13-4 (AA-14) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B1-16-4 (R-14)
B1-13-5 (AA-15) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 1.05 |  | O | ON | G1102 (B)
B1-13-6 (AA-16) | O | ON | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | G1102 하부(도어락&CCTV)
B1-13-7 (AA-17) | O | ON |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | B1-35-3(2)(위치 불명)
B209 / (AA-18) | O | ON |  |  | 0.48 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 3.76 |  | O | ON | B411
B1-13-9 (B410) | O | ON | 3.3 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B211 | B1-30-44 를 B211에 포설 예정('23.05월초)
B1-16-1 (R-11) | O | ON |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | X | OFF | B1-4-7
B1-16-2 (R-12) | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B1-4-8 (AC-12)
| X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 14.32 | 13.55 | 22.28
6-DaHall 1-PDU-03 |  | PDU : SEL1 - 6-1 - A2 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 20.7 | 21.3 | 10.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A2-2-1 | O | ON | 2.74 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | X | OFF | A2-3-1
A2-2-2 | O | ON |  | 2.14 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | X | OFF | A2-3-2
A2-2-3 | O | ON |  |  | 0.88 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | X | OFF | A2-3-3
A2-2-4 | O | ON | 3.73 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | X | OFF | A2-3-4
A2-2-5 | O | ON |  | 2.82 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | X | OFF | A2-3-5
A2-2-6 | O | ON |  |  | 1.4 | `` | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | X | OFF | A2-3-6
A2-2-7 | O | ON | 3.05 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | X | OFF | A2-3-7
A2-2-8 | O | ON |  | 3.88 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A2-3-8 (AD-12)
A2-2-9 | O | ON |  |  | 2.03 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A2-3-9 (AD-11)
A2-5-1 | X | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | A2-6-8
A2-5-2 | X | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | A2-7-1 (V-17)
A2-5-3 | X | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A2-7-2 (V-17)
A2-5-4 | X | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | A2-7-3 (V-16)
A2-5-5 | X | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | A2-7-4 (V-15)
A2-5-6 | X | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | A2-7-5 (V-14)
A2-5-7 | X | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | A2-7-6 (V-13)
A2-5-8 (AB-12) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | A2-7-7 (V-12)
A2-5-9 (AB-11) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | A2-7-8 (V-11)
A2-6-1 | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | A2-8-1 (V-16)
A2-6-2 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | A2-8-2 (W-17)
A2-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | ON | A2-8-3 (W-16)
A2-6-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | ON | A2-8-4 (W-15)
A2-6-5 | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | ON | A2-8-5 (W-14)
A2-6-6 | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | A2-8-6 (W-13)
손혈관인식시스템 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 9.52 | 8.84 | 4.31
6-DaHall 1-PDU-04 |  | PDU : SEL1 - 6-1 - B2 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 18.6 | 29.1 | 14.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B2-2-1 | O | ON | 2.25 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | X | OFF | B2-3-1
B2-2-2 | O | ON |  | 2.65 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | X | OFF | B2-3-2
B2-2-3 | O | ON |  |  | 0.85 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | X | OFF | B2-3-3
B2-2-4 | O | ON | 3.97 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | X | OFF | B2-3-4
B2-2-5 | O | ON |  | 3.27 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | X | OFF | B2-3-5
B2-2-6 | O | ON |  |  | 2.05 | `` | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | X | OFF | B2-3-6
B2-2-7 | O | ON | 1.37 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | X | OFF | B2-3-7
B2-2-8 | O | ON |  | 3.61 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B2-3-8 (AD-12)
B2-2-9 | O | ON |  |  | 1.82 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B2-3-9 (AD-11)
B2-5-1 | X | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | B2-6-8
B2-5-2 | X | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | B2-7-1 (V-17)
B2-5-3 | X | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | B2-7-2 (V-17)
B2-5-4 | X | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | B2-7-3 (V-16)
B2-5-5 | X | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | B2-7-4 (V-15)
B2-5-6 | X | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | B2-7-5 (V-14)
B2-5-7 | X | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | B2-7-6 (V-13)
B2-5-8 (AB-12) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B2-7-7 (V-12)
B2-5-9 (AB-11) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | B2-7-8 (V-11)
B2-6-1 | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | B2-8-1 (V-16)
B2-6-2 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | B2-8-2 (W-17)
B2-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | ON | B2-8-3 (W-16)
B2-6-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | ON | B2-8-4 (W-15)
B2-6-5 | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | ON | B2-8-5 (W-14)
B2-6-6 | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B2-8-6 (W-13)
| X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 7.59 | 9.53 | 4.72
6-DaHall 1-PDU-05 |  | PDU : SEL1 - 6-1 - A3 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 19.5 | 43.6 | 27 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A5-8-7 (W-12) | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 11.01 |  |  | O | ON | A5-15-1 (T-11)
A5-8-8 (W-11) | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 5.03 |  | O | ON | A5-15-2 (T-12)
A5-9-1 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0.71 |  |  |  | O | ON | A5-15-3 (T-13)
A5-9-2 (X-17) | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 2.42 |  |  | O | ON | A5-15-4 (T-14)
A5-9-3 (X-16) | O | ON |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 1 |  | O | ON | A5-15-5 (T-15)
A5-9-4 (X-15) | O | ON | 1.72 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 1.38 |  |  |  | O | ON | A5-15-6 (T-16)
A5-9-5 (X-14) | O | ON |  | 1.99 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 4.76 |  |  | O | ON | A5-15-7 (T-17)
A5-9-6 (X-13) | O | ON |  |  | 3.55 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 3.19 |  | O | ON | A5-15-8 (T-18)
A5-9-7 (X-12) | O | ON | 0.87 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | A5-15-9
A5-9-8 (X-11) | O | ON |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | ON | A5-17-1 (Q-11)
A5-10-1 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | A5-17-2 (Q-12)
A807(A5-10-2) | O | ON | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | A5-17-3 (Q-13)
A5-10-3 (A806 - 1) | O | ON |  | 3.28 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | A5-17-4 (Q-14)
A5-10-4 (A806 - 2) | O | ON |  |  | 3.63 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | A5-17-5 (Q-15)
A5-10-5 (Y-14) | O | ON | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | A5-17-6 (Q-16)
A5-10-6 (Y-13) | O | ON |  | 1.52 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | A5-17-7 (Q-17)
A5-10-7 (Y-12) | O | ON |  |  | 1.11 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | A5-17-8 (Q-18)
A5-10-8 (Y-11) | O | ON | 0.67 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | A5-17-9 (Q-19)
A5-14-1 (U-10) | O | ON |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | A5-18-1 (P-11)
A5-14-2 (U-11) | O | ON |  |  | 2.09 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A5-18-2 (P-12)
A5-14-3 (U-12) | O | ON | 1.26 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | A5-18-3 (P-13)
A5-14-4 (U-13) | O | ON |  | 5.67 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | A5-18-4 (P-14)
A5-14-5 (U-14) | O | ON |  |  | 4.74 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | A5-18-5 (P-15)
6-1-A3-47 | O | ON | 2.54 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | ON | A5-16-3 (R-13)
A5-14-7 (U-16) | O | ON |  | 7.55 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | ON | A5-4-9 (AC-11)
6-1-A3-51 | O | ON |  |  | 2.05 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | A5-6-7
6-1-A3-53 | O | ON | 2.04 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 4.17 |  |  |  | O | ON | A5-15-5(2) (T-15)
[10 empty] | 총합: | 15.36 | 38.2 | 26.39
6-DaHall 1-PDU-06 |  | PDU : SEL1 - 6-1 - B3 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 12.5 | 37.1 | 24.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B5-8-7 (W-12) | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 9.9 |  |  | O | ON | B5-15-1 (T-11)
B5-8-8 (W-11) | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 3.88 |  | O | ON | B5-15-2 (T-12)
B5-9-1 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0.69 |  |  |  | O | ON | B5-15-3 (T-13)
B5-9-2 | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 3.16 |  |  | O | ON | B5-15-4 (T-14)
B5-9-3 | O | ON |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0.54 |  | O | ON | B5-15-5 (T-15)
B5-9-4 (X-15) | O | ON | 1.89 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | B5-15-6 (T-16)
B5-9-5 (X-14) | O | ON |  | 3.42 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 3.15 |  |  | O | ON | B5-15-7 (T-17)
B5-9-6 (X-13) | O | ON |  |  | 3.1 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 3.81 |  | O | ON | B5-15-8 (T-18)
B5-9-7 (X-12) | O | ON | 0.82 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | B5-15-9
B5-9-8 (X-11) | O | ON |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | ON | B5-17-1 (Q-11)
B5-10-1 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | B5-17-2 (Q-12)
A807(B5-10-2) | O | ON | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | B5-17-3 (Q-13)
B5-10-3 (A806 - 1) | O | ON |  | 3.53 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | B5-17-4 (Q-14)
B5-10-4 (A806 - 2) | O | ON |  |  | 2.91 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | B5-17-5 (Q-15)
B5-10-5 (Y-14) | O | ON | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | B5-17-6 (Q-16)
B5-10-6 (Y-13) | O | ON |  | 0.38 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | B5-17-7 (Q-17)
B5-10-7 (Y-12) | O | ON |  |  | 1.18 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | B5-17-8 (Q-18)
B5-10-8 (Y-11) | O | ON | 0.39 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | B5-17-9 (Q-19)
A5-14-1 (U-10) | O | ON |  | 0.98 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | B5-18-1 (P-11)
A5-14-2 (U-11) | O | ON |  |  | 1.9 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | B5-18-2 (P-12)
A5-14-3 (U-12) | O | ON | 0.33 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | B5-18-3 (P-13)
A5-14-4 (U-13) | O | ON |  | 4.8 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | B5-18-4 (P-14)
A5-14-5 (U-14) | O | ON |  |  | 4.84 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | B5-18-5 (P-15)
6-1-B3-47 | O | ON | 2.32 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | ON | B5-16-3 (R-13)
A5-14-7 (U-16) | O | ON |  | 1.29 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | ON | B5-4-9 (AC-11)
6-1-B3-51 | O | ON |  |  | 2.62 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | B5-6-7
6-1-B3-53 | O | ON | 0.56 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 2.34 |  |  |  | O | ON | B5-15-5(2) (T-15)
[10 empty] | 총합: | 9.34 | 30.61 | 24.78
6-DaHall 1-PDU-07 |  | PDU : SEL1 - 6-1 - A4 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
#A6-4-4 | O | OFF |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | A6-4-1
#A6-4-7 | O | OFF |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | A6-4-2
#A6-5-4 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | A6-4-3
#A6-5-7 | O | OFF |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | ON | A6-4-4 (AC-16)
#A6-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | ON | A6-4-5 (AC-15)
#A6-6-6 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | A6-4-6 (AC-14)
#A6-7-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | ON | A6-4-7 (AC-13)
#A6-7-6 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | A6-5-1
#A6-8-3 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | A6-5-2
#A6-8-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | A6-5-3
#A6-9-3 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | A6-5-4 (AB-16)
#A6-9-6 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | A6-5-5 (AB-15)
#A6-10-3 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | A6-5-6 (AB-14)
#A6-10-6 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | A6-5-7 (AB-13)
#A6-14-4 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | OFF | A6-2-1
#A6-14-7 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | OFF | A6-2-2
#A6-15-4 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | OFF | A6-2-3
#A6-15-7 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | A6-2-4 (AE-16)
#A6-17-4 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | A6-2-5 (AE-15)
#A6-17-7 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A6-2-6 (AE-14)
A6-8-8(1) | O | ON | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | A6-2-7 (AE-13)
A6-8-7(1) | O | ON |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | A6-2-8 (AE-12)
A6-8-6(1) | O | ON |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | A6-2-9 (AE-11)
불량 | X | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | A6-3-1
A6-3-7 (AD-13) | O | ON |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | A6-3-2
A6-3-6 (AD-14) | O | ON |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | A6-3-3
A6-3-5 (AD-15) | O | ON | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | ON | A6-3-4 (AD-16)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-08 |  | PDU : SEL1 - 6-1 - B4 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
#B6-28-3 | X | OFF |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | B6-4-1
#B6-28-6 | X | OFF |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | B6-4-2
#B6-29-3 | X | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | B6-4-3
#B6-29-6 | X | OFF |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | ON | B6-4-4 (AC-16)
#B6-30-3 | X | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | ON | B6-4-5 (AC-15)
#B6-30-6 | X | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | B6-4-6 (AC-14)
#B6-31-3 | X | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | ON | B6-4-7 (AC-13)
#B6-31-6 | X | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | B6-5-1
#B6-32-3 | X | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | B6-5-2
#B6-32-6 | X | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | B6-5-3
#B6-33-3 | X | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | B6-5-4 (AB-16)
#B6-33-6 | X | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | B6-5-5 (AB-15)
| X | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | B6-5-6 (AB-14)
| X | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | B6-5-7 (AB-13)
| X | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | OFF | B6-2-1
| X | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | OFF | B6-2-2
| X | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | OFF | B6-2-3
| X | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | B6-2-4 (AE-16)
| X | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | B6-2-5 (AE-15)
| X | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | B6-2-6 (AE-14)
| X | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | B6-2-7 (AE-13)
B6-8-8(1) | O | ON |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | B6-2-8 (AE-12)
B6-8-7(1) | O | ON |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | B6-2-9 (AE-11)
B6-8-6(1) | O | ON | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | B6-3-1
B6-3-7 (AD-13) | O | ON |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | B6-3-2
B6-3-6 (AD-14) | O | ON |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | B6-3-3
B6-3-5 (AD-15) | O | ON | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | ON | B6-3-4 (AD-16)
[10 empty] | 총합: | 0 | 0 | 0
| IDC | 296.58

## 6F_current (hidden)
6F | A(전류)
6-DaHall 1-PDU-01-01 | [branch#001] [A] current
6-DaHall 1-PDU-01-02 | [branch#002] [A] current
6-DaHall 1-PDU-01-03 | [branch#003] [A] current
6-DaHall 1-PDU-01-04 | [branch#004] [A] current
6-DaHall 1-PDU-01-05 | [branch#005] [A] current
6-DaHall 1-PDU-01-06 | [branch#006] [A] current
6-DaHall 1-PDU-01-07 | [branch#007] [A] current
6-DaHall 1-PDU-01-08 | [branch#008] [A] current
6-DaHall 1-PDU-01-09 | [branch#009] [A] current
6-DaHall 1-PDU-01-10 | [branch#010] [A] current
6-DaHall 1-PDU-01-11 | [branch#011] [A] current
6-DaHall 1-PDU-01-12 | [branch#012] [A] current
6-DaHall 1-PDU-01-13 | [branch#013] [A] current
6-DaHall 1-PDU-01-14 | [branch#014] [A] current
6-DaHall 1-PDU-01-15 | [branch#015] [A] current
6-DaHall 1-PDU-01-16 | [branch#016] [A] current
6-DaHall 1-PDU-01-17 | [branch#017] [A] current
6-DaHall 1-PDU-01-18 | [branch#018] [A] current
6-DaHall 1-PDU-01-19 | [branch#019] [A] current
6-DaHall 1-PDU-01-20 | [branch#020] [A] current
6-DaHall 1-PDU-01-21 | [branch#021] [A] current
6-DaHall 1-PDU-01-22 | [branch#022] [A] current
6-DaHall 1-PDU-01-23 | [branch#023] [A] current
6-DaHall 1-PDU-01-24 | [branch#024] [A] current
6-DaHall 1-PDU-01-25 | [branch#025] [A] current
6-DaHall 1-PDU-01-26 | [branch#026] [A] current
6-DaHall 1-PDU-01-27 | [branch#027] [A] current
6-DaHall 1-PDU-01-28 | [branch#028] [A] current
6-DaHall 1-PDU-01-29 | [branch#029] [A] current
6-DaHall 1-PDU-01-30 | [branch#030] [A] current
6-DaHall 1-PDU-01-31 | [branch#031] [A] current
6-DaHall 1-PDU-01-32 | [branch#032] [A] current
6-DaHall 1-PDU-01-33 | [branch#033] [A] current
6-DaHall 1-PDU-01-34 | [branch#034] [A] current
6-DaHall 1-PDU-01-35 | [branch#035] [A] current
6-DaHall 1-PDU-01-36 | [branch#036] [A] current
6-DaHall 1-PDU-01-37 | [branch#037] [A] current
6-DaHall 1-PDU-01-38 | [branch#038] [A] current
6-DaHall 1-PDU-01-39 | [branch#039] [A] current
6-DaHall 1-PDU-01-40 | [branch#040] [A] current
6-DaHall 1-PDU-01-41 | [branch#041] [A] current
6-DaHall 1-PDU-01-42 | [branch#042] [A] current
6-DaHall 1-PDU-01-43 | [branch#043] [A] current
6-DaHall 1-PDU-01-44 | [branch#044] [A] current
6-DaHall 1-PDU-01-45 | [branch#045] [A] current
6-DaHall 1-PDU-01-46 | [branch#046] [A] current
6-DaHall 1-PDU-01-47 | [branch#047] [A] current
6-DaHall 1-PDU-01-48 | [branch#048] [A] current
6-DaHall 1-PDU-01-49 | [branch#049] [A] current
6-DaHall 1-PDU-01-50 | [branch#050] [A] current
6-DaHall 1-PDU-02-01 | [branch#001] [A] current
6-DaHall 1-PDU-02-02 | [branch#002] [A] current
6-DaHall 1-PDU-02-03 | [branch#003] [A] current
6-DaHall 1-PDU-02-04 | [branch#004] [A] current
6-DaHall 1-PDU-02-05 | [branch#005] [A] current
6-DaHall 1-PDU-02-06 | [branch#006] [A] current
6-DaHall 1-PDU-02-07 | [branch#007] [A] current
6-DaHall 1-PDU-02-08 | [branch#008] [A] current
6-DaHall 1-PDU-02-09 | [branch#009] [A] current
6-DaHall 1-PDU-02-10 | [branch#010] [A] current
6-DaHall 1-PDU-02-11 | [branch#011] [A] current
6-DaHall 1-PDU-02-12 | [branch#012] [A] current
6-DaHall 1-PDU-02-13 | [branch#013] [A] current
6-DaHall 1-PDU-02-14 | [branch#014] [A] current
6-DaHall 1-PDU-02-15 | [branch#015] [A] current
6-DaHall 1-PDU-02-16 | [branch#016] [A] current
6-DaHall 1-PDU-02-17 | [branch#017] [A] current
6-DaHall 1-PDU-02-18 | [branch#018] [A] current
6-DaHall 1-PDU-02-19 | [branch#019] [A] current
6-DaHall 1-PDU-02-20 | [branch#020] [A] current
6-DaHall 1-PDU-02-21 | [branch#021] [A] current
6-DaHall 1-PDU-02-22 | [branch#022] [A] current
6-DaHall 1-PDU-02-23 | [branch#023] [A] current
6-DaHall 1-PDU-02-24 | [branch#024] [A] current
6-DaHall 1-PDU-02-25 | [branch#025] [A] current
6-DaHall 1-PDU-02-26 | [branch#026] [A] current
6-DaHall 1-PDU-02-27 | [branch#027] [A] current
6-DaHall 1-PDU-02-28 | [branch#028] [A] current
6-DaHall 1-PDU-02-29 | [branch#029] [A] current
6-DaHall 1-PDU-02-30 | [branch#030] [A] current
6-DaHall 1-PDU-02-31 | [branch#031] [A] current
6-DaHall 1-PDU-02-32 | [branch#032] [A] current
6-DaHall 1-PDU-02-33 | [branch#033] [A] current
6-DaHall 1-PDU-02-34 | [branch#034] [A] current
6-DaHall 1-PDU-02-35 | [branch#035] [A] current
6-DaHall 1-PDU-02-36 | [branch#036] [A] current
6-DaHall 1-PDU-02-37 | [branch#037] [A] current
6-DaHall 1-PDU-02-38 | [branch#038] [A] current
6-DaHall 1-PDU-02-39 | [branch#039] [A] current
6-DaHall 1-PDU-02-40 | [branch#040] [A] current
6-DaHall 1-PDU-02-41 | [branch#041] [A] current
6-DaHall 1-PDU-02-42 | [branch#042] [A] current
6-DaHall 1-PDU-02-43 | [branch#043] [A] current
6-DaHall 1-PDU-02-44 | [branch#044] [A] current
6-DaHall 1-PDU-02-45 | [branch#045] [A] current
6-DaHall 1-PDU-02-46 | [branch#046] [A] current
6-DaHall 1-PDU-02-47 | [branch#047] [A] current
6-DaHall 1-PDU-02-48 | [branch#048] [A] current
6-DaHall 1-PDU-02-49 | [branch#049] [A] current
6-DaHall 1-PDU-02-50 | [branch#050] [A] current
6-DaHall 1-PDU-03-01 | [branch#001] [A] current
6-DaHall 1-PDU-03-02 | [branch#002] [A] current
6-DaHall 1-PDU-03-03 | [branch#003] [A] current
6-DaHall 1-PDU-03-04 | [branch#004] [A] current
6-DaHall 1-PDU-03-05 | [branch#005] [A] current
6-DaHall 1-PDU-03-06 | [branch#006] [A] current
6-DaHall 1-PDU-03-07 | [branch#007] [A] current
6-DaHall 1-PDU-03-08 | [branch#008] [A] current
6-DaHall 1-PDU-03-09 | [branch#009] [A] current
6-DaHall 1-PDU-03-10 | [branch#010] [A] current
6-DaHall 1-PDU-03-11 | [branch#011] [A] current
6-DaHall 1-PDU-03-12 | [branch#012] [A] current
6-DaHall 1-PDU-03-13 | [branch#013] [A] current
6-DaHall 1-PDU-03-14 | [branch#014] [A] current
6-DaHall 1-PDU-03-15 | [branch#015] [A] current
6-DaHall 1-PDU-03-16 | [branch#016] [A] current
6-DaHall 1-PDU-03-17 | [branch#017] [A] current
6-DaHall 1-PDU-03-18 | [branch#018] [A] current
6-DaHall 1-PDU-03-19 | [branch#019] [A] current
6-DaHall 1-PDU-03-20 | [branch#020] [A] current
6-DaHall 1-PDU-03-21 | [branch#021] [A] current
6-DaHall 1-PDU-03-22 | [branch#022] [A] current
6-DaHall 1-PDU-03-23 | [branch#023] [A] current
6-DaHall 1-PDU-03-24 | [branch#024] [A] current
6-DaHall 1-PDU-03-25 | [branch#025] [A] current
6-DaHall 1-PDU-03-26 | [branch#026] [A] current
6-DaHall 1-PDU-03-27 | [branch#027] [A] current
6-DaHall 1-PDU-03-28 | [branch#028] [A] current
6-DaHall 1-PDU-03-29 | [branch#029] [A] current
6-DaHall 1-PDU-03-30 | [branch#030] [A] current
6-DaHall 1-PDU-03-31 | [branch#031] [A] current
6-DaHall 1-PDU-03-32 | [branch#032] [A] current
6-DaHall 1-PDU-03-33 | [branch#033] [A] current
6-DaHall 1-PDU-03-34 | [branch#034] [A] current
6-DaHall 1-PDU-03-35 | [branch#035] [A] current
6-DaHall 1-PDU-03-36 | [branch#036] [A] current
6-DaHall 1-PDU-03-37 | [branch#037] [A] current
6-DaHall 1-PDU-03-38 | [branch#038] [A] current
6-DaHall 1-PDU-03-39 | [branch#039] [A] current
6-DaHall 1-PDU-03-40 | [branch#040] [A] current
6-DaHall 1-PDU-03-41 | [branch#041] [A] current
6-DaHall 1-PDU-03-42 | [branch#042] [A] current
6-DaHall 1-PDU-03-43 | [branch#043] [A] current
6-DaHall 1-PDU-03-44 | [branch#044] [A] current
6-DaHall 1-PDU-03-45 | [branch#045] [A] current
6-DaHall 1-PDU-03-46 | [branch#046] [A] current
6-DaHall 1-PDU-03-47 | [branch#047] [A] current
6-DaHall 1-PDU-03-48 | [branch#048] [A] current
6-DaHall 1-PDU-03-49 | [branch#049] [A] current
6-DaHall 1-PDU-03-50 | [branch#050] [A] current
6-DaHall 1-PDU-04-01 | [branch#001] [A] current
6-DaHall 1-PDU-04-02 | [branch#002] [A] current
6-DaHall 1-PDU-04-03 | [branch#003] [A] current
6-DaHall 1-PDU-04-04 | [branch#004] [A] current
6-DaHall 1-PDU-04-05 | [branch#005] [A] current
6-DaHall 1-PDU-04-06 | [branch#006] [A] current
6-DaHall 1-PDU-04-07 | [branch#007] [A] current
6-DaHall 1-PDU-04-08 | [branch#008] [A] current
6-DaHall 1-PDU-04-09 | [branch#009] [A] current
6-DaHall 1-PDU-04-10 | [branch#010] [A] current
6-DaHall 1-PDU-04-11 | [branch#011] [A] current
6-DaHall 1-PDU-04-12 | [branch#012] [A] current
6-DaHall 1-PDU-04-13 | [branch#013] [A] current
6-DaHall 1-PDU-04-14 | [branch#014] [A] current
6-DaHall 1-PDU-04-15 | [branch#015] [A] current
6-DaHall 1-PDU-04-16 | [branch#016] [A] current
6-DaHall 1-PDU-04-17 | [branch#017] [A] current
6-DaHall 1-PDU-04-18 | [branch#018] [A] current
6-DaHall 1-PDU-04-19 | [branch#019] [A] current
6-DaHall 1-PDU-04-20 | [branch#020] [A] current
6-DaHall 1-PDU-04-21 | [branch#021] [A] current
6-DaHall 1-PDU-04-22 | [branch#022] [A] current
6-DaHall 1-PDU-04-23 | [branch#023] [A] current
6-DaHall 1-PDU-04-24 | [branch#024] [A] current
6-DaHall 1-PDU-04-25 | [branch#025] [A] current
6-DaHall 1-PDU-04-26 | [branch#026] [A] current
6-DaHall 1-PDU-04-27 | [branch#027] [A] current
6-DaHall 1-PDU-04-28 | [branch#028] [A] current
6-DaHall 1-PDU-04-29 | [branch#029] [A] current
6-DaHall 1-PDU-04-30 | [branch#030] [A] current
6-DaHall 1-PDU-04-31 | [branch#031] [A] current
6-DaHall 1-PDU-04-32 | [branch#032] [A] current
6-DaHall 1-PDU-04-33 | [branch#033] [A] current
6-DaHall 1-PDU-04-34 | [branch#034] [A] current
6-DaHall 1-PDU-04-35 | [branch#035] [A] current
6-DaHall 1-PDU-04-36 | [branch#036] [A] current
6-DaHall 1-PDU-04-37 | [branch#037] [A] current
6-DaHall 1-PDU-04-38 | [branch#038] [A] current
6-DaHall 1-PDU-04-39 | [branch#039] [A] current
6-DaHall 1-PDU-04-40 | [branch#040] [A] current
6-DaHall 1-PDU-04-41 | [branch#041] [A] current
6-DaHall 1-PDU-04-42 | [branch#042] [A] current
6-DaHall 1-PDU-04-43 | [branch#043] [A] current
6-DaHall 1-PDU-04-44 | [branch#044] [A] current
6-DaHall 1-PDU-04-45 | [branch#045] [A] current
6-DaHall 1-PDU-04-46 | [branch#046] [A] current
6-DaHall 1-PDU-04-47 | [branch#047] [A] current
6-DaHall 1-PDU-04-48 | [branch#048] [A] current
6-DaHall 1-PDU-04-49 | [branch#049] [A] current
6-DaHall 1-PDU-04-50 | [branch#050] [A] current
6-DaHall 1-PDU-05-01 | [branch#001] [A] current
6-DaHall 1-PDU-05-02 | [branch#002] [A] current
6-DaHall 1-PDU-05-03 | [branch#003] [A] current
6-DaHall 1-PDU-05-04 | [branch#004] [A] current
6-DaHall 1-PDU-05-05 | [branch#005] [A] current
6-DaHall 1-PDU-05-06 | [branch#006] [A] current
6-DaHall 1-PDU-05-07 | [branch#007] [A] current
6-DaHall 1-PDU-05-08 | [branch#008] [A] current
6-DaHall 1-PDU-05-09 | [branch#009] [A] current
6-DaHall 1-PDU-05-10 | [branch#010] [A] current
6-DaHall 1-PDU-05-11 | [branch#011] [A] current
6-DaHall 1-PDU-05-12 | [branch#012] [A] current
6-DaHall 1-PDU-05-13 | [branch#013] [A] current
6-DaHall 1-PDU-05-14 | [branch#014] [A] current
6-DaHall 1-PDU-05-15 | [branch#015] [A] current
6-DaHall 1-PDU-05-16 | [branch#016] [A] current
6-DaHall 1-PDU-05-17 | [branch#017] [A] current
6-DaHall 1-PDU-05-18 | [branch#018] [A] current
6-DaHall 1-PDU-05-19 | [branch#019] [A] current
6-DaHall 1-PDU-05-20 | [branch#020] [A] current
6-DaHall 1-PDU-05-21 | [branch#021] [A] current
6-DaHall 1-PDU-05-22 | [branch#022] [A] current
6-DaHall 1-PDU-05-23 | [branch#023] [A] current
6-DaHall 1-PDU-05-24 | [branch#024] [A] current
6-DaHall 1-PDU-05-25 | [branch#025] [A] current
6-DaHall 1-PDU-05-26 | [branch#026] [A] current
6-DaHall 1-PDU-05-27 | [branch#027] [A] current
6-DaHall 1-PDU-05-28 | [branch#028] [A] current
6-DaHall 1-PDU-05-29 | [branch#029] [A] current
6-DaHall 1-PDU-05-30 | [branch#030] [A] current
6-DaHall 1-PDU-05-31 | [branch#031] [A] current
6-DaHall 1-PDU-05-32 | [branch#032] [A] current
6-DaHall 1-PDU-05-33 | [branch#033] [A] current
6-DaHall 1-PDU-05-34 | [branch#034] [A] current
6-DaHall 1-PDU-05-35 | [branch#035] [A] current
6-DaHall 1-PDU-05-36 | [branch#036] [A] current
6-DaHall 1-PDU-05-37 | [branch#037] [A] current
6-DaHall 1-PDU-05-38 | [branch#038] [A] current
6-DaHall 1-PDU-05-39 | [branch#039] [A] current
6-DaHall 1-PDU-05-40 | [branch#040] [A] current
6-DaHall 1-PDU-05-41 | [branch#041] [A] current
6-DaHall 1-PDU-05-42 | [branch#042] [A] current
6-DaHall 1-PDU-05-43 | [branch#043] [A] current
6-DaHall 1-PDU-05-44 | [branch#044] [A] current
6-DaHall 1-PDU-05-45 | [branch#045] [A] current
6-DaHall 1-PDU-05-46 | [branch#046] [A] current
6-DaHall 1-PDU-05-47 | [branch#047] [A] current
6-DaHall 1-PDU-05-48 | [branch#048] [A] current
6-DaHall 1-PDU-05-49 | [branch#049] [A] current
6-DaHall 1-PDU-05-50 | [branch#050] [A] current
6-DaHall 1-PDU-05-51 | [branch#051] [A] current
6-DaHall 1-PDU-05-52 | [branch#052] [A] current
6-DaHall 1-PDU-05-53 | [branch#053] [A] current
6-DaHall 1-PDU-05-54 | [branch#054] [A] current
6-DaHall 1-PDU-06-01 | [branch#001] [A] current
6-DaHall 1-PDU-06-02 | [branch#002] [A] current
6-DaHall 1-PDU-06-03 | [branch#003] [A] current
6-DaHall 1-PDU-06-04 | [branch#004] [A] current
6-DaHall 1-PDU-06-05 | [branch#005] [A] current
6-DaHall 1-PDU-06-06 | [branch#006] [A] current
6-DaHall 1-PDU-06-07 | [branch#007] [A] current
6-DaHall 1-PDU-06-08 | [branch#008] [A] current
6-DaHall 1-PDU-06-09 | [branch#009] [A] current
6-DaHall 1-PDU-06-10 | [branch#010] [A] current
6-DaHall 1-PDU-06-11 | [branch#011] [A] current
6-DaHall 1-PDU-06-12 | [branch#012] [A] current
6-DaHall 1-PDU-06-13 | [branch#013] [A] current
6-DaHall 1-PDU-06-14 | [branch#014] [A] current
6-DaHall 1-PDU-06-15 | [branch#015] [A] current
6-DaHall 1-PDU-06-16 | [branch#016] [A] current
6-DaHall 1-PDU-06-17 | [branch#017] [A] current
6-DaHall 1-PDU-06-18 | [branch#018] [A] current
6-DaHall 1-PDU-06-19 | [branch#019] [A] current
6-DaHall 1-PDU-06-20 | [branch#020] [A] current
6-DaHall 1-PDU-06-21 | [branch#021] [A] current
6-DaHall 1-PDU-06-22 | [branch#022] [A] current
6-DaHall 1-PDU-06-23 | [branch#023] [A] current
6-DaHall 1-PDU-06-24 | [branch#024] [A] current
6-DaHall 1-PDU-06-25 | [branch#025] [A] current
6-DaHall 1-PDU-06-26 | [branch#026] [A] current
6-DaHall 1-PDU-06-27 | [branch#027] [A] current
6-DaHall 1-PDU-06-28 | [branch#028] [A] current
6-DaHall 1-PDU-06-29 | [branch#029] [A] current
6-DaHall 1-PDU-06-30 | [branch#030] [A] current
6-DaHall 1-PDU-06-31 | [branch#031] [A] current
6-DaHall 1-PDU-06-32 | [branch#032] [A] current
6-DaHall 1-PDU-06-33 | [branch#033] [A] current
6-DaHall 1-PDU-06-34 | [branch#034] [A] current
6-DaHall 1-PDU-06-35 | [branch#035] [A] current
6-DaHall 1-PDU-06-36 | [branch#036] [A] current
6-DaHall 1-PDU-06-37 | [branch#037] [A] current
6-DaHall 1-PDU-06-38 | [branch#038] [A] current
6-DaHall 1-PDU-06-39 | [branch#039] [A] current
6-DaHall 1-PDU-06-40 | [branch#040] [A] current
6-DaHall 1-PDU-06-41 | [branch#041] [A] current
6-DaHall 1-PDU-06-42 | [branch#042] [A] current
6-DaHall 1-PDU-06-43 | [branch#043] [A] current
6-DaHall 1-PDU-06-44 | [branch#044] [A] current
6-DaHall 1-PDU-06-45 | [branch#045] [A] current
6-DaHall 1-PDU-06-46 | [branch#046] [A] current
6-DaHall 1-PDU-06-47 | [branch#047] [A] current
6-DaHall 1-PDU-06-48 | [branch#048] [A] current
6-DaHall 1-PDU-06-49 | [branch#049] [A] current
6-DaHall 1-PDU-06-50 | [branch#050] [A] current
6-DaHall 1-PDU-06-51 | [branch#051] [A] current
6-DaHall 1-PDU-06-52 | [branch#052] [A] current
6-DaHall 1-PDU-06-53 | [branch#053] [A] current
6-DaHall 1-PDU-06-54 | [branch#054] [A] current
6-DaHall 1-PDU-07-01 | [branch#001] [A] current
6-DaHall 1-PDU-07-02 | [branch#002] [A] current
6-DaHall 1-PDU-07-03 | [branch#003] [A] current
6-DaHall 1-PDU-07-04 | [branch#004] [A] current
6-DaHall 1-PDU-07-05 | [branch#005] [A] current
6-DaHall 1-PDU-07-06 | [branch#006] [A] current
6-DaHall 1-PDU-07-07 | [branch#007] [A] current
6-DaHall 1-PDU-07-08 | [branch#008] [A] current
6-DaHall 1-PDU-07-09 | [branch#009] [A] current
6-DaHall 1-PDU-07-10 | [branch#010] [A] current
6-DaHall 1-PDU-07-11 | [branch#011] [A] current
6-DaHall 1-PDU-07-12 | [branch#012] [A] current
6-DaHall 1-PDU-07-13 | [branch#013] [A] current
6-DaHall 1-PDU-07-14 | [branch#014] [A] current
6-DaHall 1-PDU-07-15 | [branch#015] [A] current
6-DaHall 1-PDU-07-16 | [branch#016] [A] current
6-DaHall 1-PDU-07-17 | [branch#017] [A] current
6-DaHall 1-PDU-07-18 | [branch#018] [A] current
6-DaHall 1-PDU-07-19 | [branch#019] [A] current
6-DaHall 1-PDU-07-20 | [branch#020] [A] current
6-DaHall 1-PDU-07-21 | [branch#021] [A] current
6-DaHall 1-PDU-07-22 | [branch#022] [A] current
6-DaHall 1-PDU-07-23 | [branch#023] [A] current
6-DaHall 1-PDU-07-24 | [branch#024] [A] current
6-DaHall 1-PDU-07-25 | [branch#025] [A] current
6-DaHall 1-PDU-07-26 | [branch#026] [A] current
6-DaHall 1-PDU-07-27 | [branch#027] [A] current
6-DaHall 1-PDU-07-28 | [branch#028] [A] current
6-DaHall 1-PDU-07-29 | [branch#029] [A] current
6-DaHall 1-PDU-07-30 | [branch#030] [A] current
6-DaHall 1-PDU-07-31 | [branch#031] [A] current
6-DaHall 1-PDU-07-32 | [branch#032] [A] current
6-DaHall 1-PDU-07-33 | [branch#033] [A] current
6-DaHall 1-PDU-07-34 | [branch#034] [A] current
6-DaHall 1-PDU-07-35 | [branch#035] [A] current
6-DaHall 1-PDU-07-36 | [branch#036] [A] current
6-DaHall 1-PDU-07-37 | [branch#037] [A] current
6-DaHall 1-PDU-07-38 | [branch#038] [A] current
6-DaHall 1-PDU-07-39 | [branch#039] [A] current
6-DaHall 1-PDU-07-40 | [branch#040] [A] current
6-DaHall 1-PDU-07-41 | [branch#041] [A] current
6-DaHall 1-PDU-07-42 | [branch#042] [A] current
6-DaHall 1-PDU-07-43 | [branch#043] [A] current
6-DaHall 1-PDU-07-44 | [branch#044] [A] current
6-DaHall 1-PDU-07-45 | [branch#045] [A] current
6-DaHall 1-PDU-07-46 | [branch#046] [A] current
6-DaHall 1-PDU-07-47 | [branch#047] [A] current
6-DaHall 1-PDU-07-48 | [branch#048] [A] current
6-DaHall 1-PDU-07-49 | [branch#049] [A] current
6-DaHall 1-PDU-07-50 | [branch#050] [A] current
6-DaHall 1-PDU-07-51 | [branch#051] [A] current
6-DaHall 1-PDU-07-52 | [branch#052] [A] current
6-DaHall 1-PDU-07-53 | [branch#053] [A] current
6-DaHall 1-PDU-07-54 | [branch#054] [A] current
6-DaHall 1-PDU-08-01 | [branch#001] [A] current
6-DaHall 1-PDU-08-02 | [branch#002] [A] current
6-DaHall 1-PDU-08-03 | [branch#003] [A] current
6-DaHall 1-PDU-08-04 | [branch#004] [A] current
6-DaHall 1-PDU-08-05 | [branch#005] [A] current
6-DaHall 1-PDU-08-06 | [branch#006] [A] current
6-DaHall 1-PDU-08-07 | [branch#007] [A] current
6-DaHall 1-PDU-08-08 | [branch#008] [A] current
6-DaHall 1-PDU-08-09 | [branch#009] [A] current
6-DaHall 1-PDU-08-10 | [branch#010] [A] current
6-DaHall 1-PDU-08-11 | [branch#011] [A] current
6-DaHall 1-PDU-08-12 | [branch#012] [A] current
6-DaHall 1-PDU-08-13 | [branch#013] [A] current
6-DaHall 1-PDU-08-14 | [branch#014] [A] current
6-DaHall 1-PDU-08-15 | [branch#015] [A] current
6-DaHall 1-PDU-08-16 | [branch#016] [A] current
6-DaHall 1-PDU-08-17 | [branch#017] [A] current
6-DaHall 1-PDU-08-18 | [branch#018] [A] current
6-DaHall 1-PDU-08-19 | [branch#019] [A] current
6-DaHall 1-PDU-08-20 | [branch#020] [A] current
6-DaHall 1-PDU-08-21 | [branch#021] [A] current
6-DaHall 1-PDU-08-22 | [branch#022] [A] current
6-DaHall 1-PDU-08-23 | [branch#023] [A] current
6-DaHall 1-PDU-08-24 | [branch#024] [A] current
6-DaHall 1-PDU-08-25 | [branch#025] [A] current
6-DaHall 1-PDU-08-26 | [branch#026] [A] current
6-DaHall 1-PDU-08-27 | [branch#027] [A] current
6-DaHall 1-PDU-08-28 | [branch#028] [A] current
6-DaHall 1-PDU-08-29 | [branch#029] [A] current
6-DaHall 1-PDU-08-30 | [branch#030] [A] current
6-DaHall 1-PDU-08-31 | [branch#031] [A] current
6-DaHall 1-PDU-08-32 | [branch#032] [A] current
6-DaHall 1-PDU-08-33 | [branch#033] [A] current
6-DaHall 1-PDU-08-34 | [branch#034] [A] current
6-DaHall 1-PDU-08-35 | [branch#035] [A] current
6-DaHall 1-PDU-08-36 | [branch#036] [A] current
6-DaHall 1-PDU-08-37 | [branch#037] [A] current
6-DaHall 1-PDU-08-38 | [branch#038] [A] current
6-DaHall 1-PDU-08-39 | [branch#039] [A] current
6-DaHall 1-PDU-08-40 | [branch#040] [A] current
6-DaHall 1-PDU-08-41 | [branch#041] [A] current
6-DaHall 1-PDU-08-42 | [branch#042] [A] current
6-DaHall 1-PDU-08-43 | [branch#043] [A] current
6-DaHall 1-PDU-08-44 | [branch#044] [A] current
6-DaHall 1-PDU-08-45 | [branch#045] [A] current
6-DaHall 1-PDU-08-46 | [branch#046] [A] current
6-DaHall 1-PDU-08-47 | [branch#047] [A] current
6-DaHall 1-PDU-08-48 | [branch#048] [A] current
6-DaHall 1-PDU-08-49 | [branch#049] [A] current
6-DaHall 1-PDU-08-50 | [branch#050] [A] current
6-DaHall 1-PDU-08-51 | [branch#051] [A] current
6-DaHall 1-PDU-08-52 | [branch#052] [A] current
6-DaHall 1-PDU-08-53 | [branch#053] [A] current
6-DaHall 1-PDU-08-54 | [branch#054] [A] current
6-DaHall 1-PDU-09-01 | [branch#001] [A] current
6-DaHall 1-PDU-09-02 | [branch#002] [A] current
6-DaHall 1-PDU-09-03 | [branch#003] [A] current
6-DaHall 1-PDU-09-04 | [branch#004] [A] current
6-DaHall 1-PDU-09-05 | [branch#005] [A] current
6-DaHall 1-PDU-09-06 | [branch#006] [A] current
6-DaHall 1-PDU-09-07 | [branch#007] [A] current
6-DaHall 1-PDU-09-08 | [branch#008] [A] current
6-DaHall 1-PDU-09-09 | [branch#009] [A] current
6-DaHall 1-PDU-09-10 | [branch#010] [A] current
6-DaHall 1-PDU-09-11 | [branch#011] [A] current
6-DaHall 1-PDU-09-12 | [branch#012] [A] current
6-DaHall 1-PDU-09-13 | [branch#013] [A] current
6-DaHall 1-PDU-09-14 | [branch#014] [A] current
6-DaHall 1-PDU-09-15 | [branch#015] [A] current
6-DaHall 1-PDU-09-16 | [branch#016] [A] current
6-DaHall 1-PDU-09-17 | [branch#017] [A] current
6-DaHall 1-PDU-09-18 | [branch#018] [A] current
6-DaHall 1-PDU-09-19 | [branch#019] [A] current
6-DaHall 1-PDU-09-20 | [branch#020] [A] current
6-DaHall 1-PDU-09-21 | [branch#021] [A] current
6-DaHall 1-PDU-09-22 | [branch#022] [A] current
6-DaHall 1-PDU-09-23 | [branch#023] [A] current
6-DaHall 1-PDU-09-24 | [branch#024] [A] current
6-DaHall 1-PDU-09-25 | [branch#025] [A] current
6-DaHall 1-PDU-09-26 | [branch#026] [A] current
6-DaHall 1-PDU-09-27 | [branch#027] [A] current
6-DaHall 1-PDU-09-28 | [branch#028] [A] current
6-DaHall 1-PDU-09-29 | [branch#029] [A] current
6-DaHall 1-PDU-09-30 | [branch#030] [A] current
6-DaHall 1-PDU-09-31 | [branch#031] [A] current
6-DaHall 1-PDU-09-32 | [branch#032] [A] current
6-DaHall 1-PDU-09-33 | [branch#033] [A] current
6-DaHall 1-PDU-09-34 | [branch#034] [A] current
6-DaHall 1-PDU-09-35 | [branch#035] [A] current
6-DaHall 1-PDU-09-36 | [branch#036] [A] current
6-DaHall 1-PDU-09-37 | [branch#037] [A] current
6-DaHall 1-PDU-09-38 | [branch#038] [A] current
6-DaHall 1-PDU-09-39 | [branch#039] [A] current
6-DaHall 1-PDU-09-40 | [branch#040] [A] current
6-DaHall 1-PDU-09-41 | [branch#041] [A] current
6-DaHall 1-PDU-09-42 | [branch#042] [A] current
6-DaHall 1-PDU-09-43 | [branch#043] [A] current
6-DaHall 1-PDU-09-44 | [branch#044] [A] current
6-DaHall 1-PDU-09-45 | [branch#045] [A] current
6-DaHall 1-PDU-09-46 | [branch#046] [A] current
6-DaHall 1-PDU-09-47 | [branch#047] [A] current
6-DaHall 1-PDU-09-48 | [branch#048] [A] current
6-DaHall 1-PDU-09-49 | [branch#049] [A] current
6-DaHall 1-PDU-09-50 | [branch#050] [A] current
6-DaHall 1-PDU-10-01 | [branch#001] [A] current
6-DaHall 1-PDU-10-02 | [branch#002] [A] current
6-DaHall 1-PDU-10-03 | [branch#003] [A] current
6-DaHall 1-PDU-10-04 | [branch#004] [A] current
6-DaHall 1-PDU-10-05 | [branch#005] [A] current
6-DaHall 1-PDU-10-06 | [branch#006] [A] current
6-DaHall 1-PDU-10-07 | [branch#007] [A] current
6-DaHall 1-PDU-10-08 | [branch#008] [A] current
6-DaHall 1-PDU-10-09 | [branch#009] [A] current
6-DaHall 1-PDU-10-10 | [branch#010] [A] current
6-DaHall 1-PDU-10-11 | [branch#011] [A] current
6-DaHall 1-PDU-10-12 | [branch#012] [A] current
6-DaHall 1-PDU-10-13 | [branch#013] [A] current
6-DaHall 1-PDU-10-14 | [branch#014] [A] current
6-DaHall 1-PDU-10-15 | [branch#015] [A] current
6-DaHall 1-PDU-10-16 | [branch#016] [A] current
6-DaHall 1-PDU-10-17 | [branch#017] [A] current
6-DaHall 1-PDU-10-18 | [branch#018] [A] current
6-DaHall 1-PDU-10-19 | [branch#019] [A] current
6-DaHall 1-PDU-10-20 | [branch#020] [A] current
6-DaHall 1-PDU-10-21 | [branch#021] [A] current
6-DaHall 1-PDU-10-22 | [branch#022] [A] current
6-DaHall 1-PDU-10-23 | [branch#023] [A] current
6-DaHall 1-PDU-10-24 | [branch#024] [A] current
6-DaHall 1-PDU-10-25 | [branch#025] [A] current
6-DaHall 1-PDU-10-26 | [branch#026] [A] current
6-DaHall 1-PDU-10-27 | [branch#027] [A] current
6-DaHall 1-PDU-10-28 | [branch#028] [A] current
6-DaHall 1-PDU-10-29 | [branch#029] [A] current
6-DaHall 1-PDU-10-30 | [branch#030] [A] current
6-DaHall 1-PDU-10-31 | [branch#031] [A] current
6-DaHall 1-PDU-10-32 | [branch#032] [A] current
6-DaHall 1-PDU-10-33 | [branch#033] [A] current
6-DaHall 1-PDU-10-34 | [branch#034] [A] current
6-DaHall 1-PDU-10-35 | [branch#035] [A] current
6-DaHall 1-PDU-10-36 | [branch#036] [A] current
6-DaHall 1-PDU-10-37 | [branch#037] [A] current
6-DaHall 1-PDU-10-38 | [branch#038] [A] current
6-DaHall 1-PDU-10-39 | [branch#039] [A] current
6-DaHall 1-PDU-10-40 | [branch#040] [A] current
6-DaHall 1-PDU-10-41 | [branch#041] [A] current
6-DaHall 1-PDU-10-42 | [branch#042] [A] current
6-DaHall 1-PDU-10-43 | [branch#043] [A] current
6-DaHall 1-PDU-10-44 | [branch#044] [A] current
6-DaHall 1-PDU-10-45 | [branch#045] [A] current
6-DaHall 1-PDU-10-46 | [branch#046] [A] current
6-DaHall 1-PDU-10-47 | [branch#047] [A] current
6-DaHall 1-PDU-10-48 | [branch#048] [A] current
6-DaHall 1-PDU-10-49 | [branch#049] [A] current
6-DaHall 1-PDU-10-50 | [branch#050] [A] current
6-DaHall 1-PDU-11-01 | [branch#001] [A] current
6-DaHall 1-PDU-11-02 | [branch#002] [A] current
6-DaHall 1-PDU-11-03 | [branch#003] [A] current
6-DaHall 1-PDU-11-04 | [branch#004] [A] current
6-DaHall 1-PDU-11-05 | [branch#005] [A] current
6-DaHall 1-PDU-11-06 | [branch#006] [A] current
6-DaHall 1-PDU-11-07 | [branch#007] [A] current
6-DaHall 1-PDU-11-08 | [branch#008] [A] current
6-DaHall 1-PDU-11-09 | [branch#009] [A] current
6-DaHall 1-PDU-11-10 | [branch#010] [A] current
6-DaHall 1-PDU-11-11 | [branch#011] [A] current
6-DaHall 1-PDU-11-12 | [branch#012] [A] current
6-DaHall 1-PDU-11-13 | [branch#013] [A] current
6-DaHall 1-PDU-11-14 | [branch#014] [A] current
6-DaHall 1-PDU-11-15 | [branch#015] [A] current
6-DaHall 1-PDU-11-16 | [branch#016] [A] current
6-DaHall 1-PDU-11-17 | [branch#017] [A] current
6-DaHall 1-PDU-11-18 | [branch#018] [A] current
6-DaHall 1-PDU-11-19 | [branch#019] [A] current
6-DaHall 1-PDU-11-20 | [branch#020] [A] current
6-DaHall 1-PDU-11-21 | [branch#021] [A] current
6-DaHall 1-PDU-11-22 | [branch#022] [A] current
6-DaHall 1-PDU-11-23 | [branch#023] [A] current
6-DaHall 1-PDU-11-24 | [branch#024] [A] current
6-DaHall 1-PDU-11-25 | [branch#025] [A] current
6-DaHall 1-PDU-11-26 | [branch#026] [A] current
6-DaHall 1-PDU-11-27 | [branch#027] [A] current
6-DaHall 1-PDU-11-28 | [branch#028] [A] current
6-DaHall 1-PDU-11-29 | [branch#029] [A] current
6-DaHall 1-PDU-11-30 | [branch#030] [A] current
6-DaHall 1-PDU-11-31 | [branch#031] [A] current
6-DaHall 1-PDU-11-32 | [branch#032] [A] current
6-DaHall 1-PDU-11-33 | [branch#033] [A] current
6-DaHall 1-PDU-11-34 | [branch#034] [A] current
6-DaHall 1-PDU-11-35 | [branch#035] [A] current
6-DaHall 1-PDU-11-36 | [branch#036] [A] current
6-DaHall 1-PDU-11-37 | [branch#037] [A] current
6-DaHall 1-PDU-11-38 | [branch#038] [A] current
6-DaHall 1-PDU-11-39 | [branch#039] [A] current
6-DaHall 1-PDU-11-40 | [branch#040] [A] current
6-DaHall 1-PDU-11-41 | [branch#041] [A] current
6-DaHall 1-PDU-11-42 | [branch#042] [A] current
6-DaHall 1-PDU-11-43 | [branch#043] [A] current
6-DaHall 1-PDU-11-44 | [branch#044] [A] current
6-DaHall 1-PDU-11-45 | [branch#045] [A] current
6-DaHall 1-PDU-11-46 | [branch#046] [A] current
6-DaHall 1-PDU-11-47 | [branch#047] [A] current
6-DaHall 1-PDU-11-48 | [branch#048] [A] current
6-DaHall 1-PDU-11-49 | [branch#049] [A] current
6-DaHall 1-PDU-11-50 | [branch#050] [A] current
6-DaHall 1-PDU-12-01 | [branch#001] [A] current
6-DaHall 1-PDU-12-02 | [branch#002] [A] current
6-DaHall 1-PDU-12-03 | [branch#003] [A] current
6-DaHall 1-PDU-12-04 | [branch#004] [A] current
6-DaHall 1-PDU-12-05 | [branch#005] [A] current
6-DaHall 1-PDU-12-06 | [branch#006] [A] current
6-DaHall 1-PDU-12-07 | [branch#007] [A] current
6-DaHall 1-PDU-12-08 | [branch#008] [A] current
6-DaHall 1-PDU-12-09 | [branch#009] [A] current
6-DaHall 1-PDU-12-10 | [branch#010] [A] current
6-DaHall 1-PDU-12-11 | [branch#011] [A] current
6-DaHall 1-PDU-12-12 | [branch#012] [A] current
6-DaHall 1-PDU-12-13 | [branch#013] [A] current
6-DaHall 1-PDU-12-14 | [branch#014] [A] current
6-DaHall 1-PDU-12-15 | [branch#015] [A] current
6-DaHall 1-PDU-12-16 | [branch#016] [A] current
6-DaHall 1-PDU-12-17 | [branch#017] [A] current
6-DaHall 1-PDU-12-18 | [branch#018] [A] current
6-DaHall 1-PDU-12-19 | [branch#019] [A] current
6-DaHall 1-PDU-12-20 | [branch#020] [A] current
6-DaHall 1-PDU-12-21 | [branch#021] [A] current
6-DaHall 1-PDU-12-22 | [branch#022] [A] current
6-DaHall 1-PDU-12-23 | [branch#023] [A] current
6-DaHall 1-PDU-12-24 | [branch#024] [A] current
6-DaHall 1-PDU-12-25 | [branch#025] [A] current
6-DaHall 1-PDU-12-26 | [branch#026] [A] current
6-DaHall 1-PDU-12-27 | [branch#027] [A] current
6-DaHall 1-PDU-12-28 | [branch#028] [A] current
6-DaHall 1-PDU-12-29 | [branch#029] [A] current
6-DaHall 1-PDU-12-30 | [branch#030] [A] current
6-DaHall 1-PDU-12-31 | [branch#031] [A] current
6-DaHall 1-PDU-12-32 | [branch#032] [A] current
6-DaHall 1-PDU-12-33 | [branch#033] [A] current
6-DaHall 1-PDU-12-34 | [branch#034] [A] current
6-DaHall 1-PDU-12-35 | [branch#035] [A] current
6-DaHall 1-PDU-12-36 | [branch#036] [A] current
6-DaHall 1-PDU-12-37 | [branch#037] [A] current
6-DaHall 1-PDU-12-38 | [branch#038] [A] current
6-DaHall 1-PDU-12-39 | [branch#039] [A] current
6-DaHall 1-PDU-12-40 | [branch#040] [A] current
6-DaHall 1-PDU-12-41 | [branch#041] [A] current
6-DaHall 1-PDU-12-42 | [branch#042] [A] current
6-DaHall 1-PDU-12-43 | [branch#043] [A] current
6-DaHall 1-PDU-12-44 | [branch#044] [A] current
6-DaHall 1-PDU-12-45 | [branch#045] [A] current
6-DaHall 1-PDU-12-46 | [branch#046] [A] current
6-DaHall 1-PDU-12-47 | [branch#047] [A] current
6-DaHall 1-PDU-12-48 | [branch#048] [A] current
6-DaHall 1-PDU-12-49 | [branch#049] [A] current
6-DaHall 1-PDU-12-50 | [branch#050] [A] current
6-DaHall 1-PDU-13-01 | [branch#001] [A] current
6-DaHall 1-PDU-13-02 | [branch#002] [A] current
6-DaHall 1-PDU-13-03 | [branch#003] [A] current
6-DaHall 1-PDU-13-04 | [branch#004] [A] current
6-DaHall 1-PDU-13-05 | [branch#005] [A] current
6-DaHall 1-PDU-13-06 | [branch#006] [A] current
6-DaHall 1-PDU-13-07 | [branch#007] [A] current
6-DaHall 1-PDU-13-08 | [branch#008] [A] current
6-DaHall 1-PDU-13-09 | [branch#009] [A] current
6-DaHall 1-PDU-13-10 | [branch#010] [A] current
6-DaHall 1-PDU-13-11 | [branch#011] [A] current
6-DaHall 1-PDU-13-12 | [branch#012] [A] current
6-DaHall 1-PDU-13-13 | [branch#013] [A] current
6-DaHall 1-PDU-13-14 | [branch#014] [A] current
6-DaHall 1-PDU-13-15 | [branch#015] [A] current
6-DaHall 1-PDU-13-16 | [branch#016] [A] current
6-DaHall 1-PDU-13-17 | [branch#017] [A] current
6-DaHall 1-PDU-13-18 | [branch#018] [A] current
6-DaHall 1-PDU-13-19 | [branch#019] [A] current
6-DaHall 1-PDU-13-20 | [branch#020] [A] current
6-DaHall 1-PDU-13-21 | [branch#021] [A] current
6-DaHall 1-PDU-13-22 | [branch#022] [A] current
6-DaHall 1-PDU-13-23 | [branch#023] [A] current
6-DaHall 1-PDU-13-24 | [branch#024] [A] current
6-DaHall 1-PDU-13-25 | [branch#025] [A] current
6-DaHall 1-PDU-13-26 | [branch#026] [A] current
6-DaHall 1-PDU-13-27 | [branch#027] [A] current
6-DaHall 1-PDU-13-28 | [branch#028] [A] current
6-DaHall 1-PDU-13-29 | [branch#029] [A] current
6-DaHall 1-PDU-13-30 | [branch#030] [A] current
6-DaHall 1-PDU-13-31 | [branch#031] [A] current
6-DaHall 1-PDU-13-32 | [branch#032] [A] current
6-DaHall 1-PDU-13-33 | [branch#033] [A] current
6-DaHall 1-PDU-13-34 | [branch#034] [A] current
6-DaHall 1-PDU-13-35 | [branch#035] [A] current
6-DaHall 1-PDU-13-36 | [branch#036] [A] current
6-DaHall 1-PDU-13-37 | [branch#037] [A] current
6-DaHall 1-PDU-13-38 | [branch#038] [A] current
6-DaHall 1-PDU-13-39 | [branch#039] [A] current
6-DaHall 1-PDU-13-40 | [branch#040] [A] current
6-DaHall 1-PDU-13-41 | [branch#041] [A] current
6-DaHall 1-PDU-13-42 | [branch#042] [A] current
6-DaHall 1-PDU-13-43 | [branch#043] [A] current
6-DaHall 1-PDU-13-44 | [branch#044] [A] current
6-DaHall 1-PDU-13-45 | [branch#045] [A] current
6-DaHall 1-PDU-13-46 | [branch#046] [A] current
6-DaHall 1-PDU-13-47 | [branch#047] [A] current
6-DaHall 1-PDU-13-48 | [branch#048] [A] current
6-DaHall 1-PDU-13-49 | [branch#049] [A] current
6-DaHall 1-PDU-13-50 | [branch#050] [A] current
6-DaHall 1-PDU-13-51 | [branch#051] [A] current
6-DaHall 1-PDU-13-52 | [branch#052] [A] current
6-DaHall 1-PDU-13-53 | [branch#053] [A] current
6-DaHall 1-PDU-13-54 | [branch#054] [A] current
6-DaHall 1-PDU-14-01 | [branch#001] [A] current
6-DaHall 1-PDU-14-02 | [branch#002] [A] current
6-DaHall 1-PDU-14-03 | [branch#003] [A] current
6-DaHall 1-PDU-14-04 | [branch#004] [A] current
6-DaHall 1-PDU-14-05 | [branch#005] [A] current
6-DaHall 1-PDU-14-06 | [branch#006] [A] current
6-DaHall 1-PDU-14-07 | [branch#007] [A] current
6-DaHall 1-PDU-14-08 | [branch#008] [A] current
6-DaHall 1-PDU-14-09 | [branch#009] [A] current
6-DaHall 1-PDU-14-10 | [branch#010] [A] current
6-DaHall 1-PDU-14-11 | [branch#011] [A] current
6-DaHall 1-PDU-14-12 | [branch#012] [A] current
6-DaHall 1-PDU-14-13 | [branch#013] [A] current
6-DaHall 1-PDU-14-14 | [branch#014] [A] current
6-DaHall 1-PDU-14-15 | [branch#015] [A] current
6-DaHall 1-PDU-14-16 | [branch#016] [A] current
6-DaHall 1-PDU-14-17 | [branch#017] [A] current
6-DaHall 1-PDU-14-18 | [branch#018] [A] current
6-DaHall 1-PDU-14-19 | [branch#019] [A] current
6-DaHall 1-PDU-14-20 | [branch#020] [A] current
6-DaHall 1-PDU-14-21 | [branch#021] [A] current
6-DaHall 1-PDU-14-22 | [branch#022] [A] current
6-DaHall 1-PDU-14-23 | [branch#023] [A] current
6-DaHall 1-PDU-14-24 | [branch#024] [A] current
6-DaHall 1-PDU-14-25 | [branch#025] [A] current
6-DaHall 1-PDU-14-26 | [branch#026] [A] current
6-DaHall 1-PDU-14-27 | [branch#027] [A] current
6-DaHall 1-PDU-14-28 | [branch#028] [A] current
6-DaHall 1-PDU-14-29 | [branch#029] [A] current
6-DaHall 1-PDU-14-30 | [branch#030] [A] current
6-DaHall 1-PDU-14-31 | [branch#031] [A] current
6-DaHall 1-PDU-14-32 | [branch#032] [A] current
6-DaHall 1-PDU-14-33 | [branch#033] [A] current
6-DaHall 1-PDU-14-34 | [branch#034] [A] current
6-DaHall 1-PDU-14-35 | [branch#035] [A] current
6-DaHall 1-PDU-14-36 | [branch#036] [A] current
6-DaHall 1-PDU-14-37 | [branch#037] [A] current
6-DaHall 1-PDU-14-38 | [branch#038] [A] current
6-DaHall 1-PDU-14-39 | [branch#039] [A] current
6-DaHall 1-PDU-14-40 | [branch#040] [A] current
6-DaHall 1-PDU-14-41 | [branch#041] [A] current
6-DaHall 1-PDU-14-42 | [branch#042] [A] current
6-DaHall 1-PDU-14-43 | [branch#043] [A] current
6-DaHall 1-PDU-14-44 | [branch#044] [A] current
6-DaHall 1-PDU-14-45 | [branch#045] [A] current
6-DaHall 1-PDU-14-46 | [branch#046] [A] current
6-DaHall 1-PDU-14-47 | [branch#047] [A] current
6-DaHall 1-PDU-14-48 | [branch#048] [A] current
6-DaHall 1-PDU-14-49 | [branch#049] [A] current
6-DaHall 1-PDU-14-50 | [branch#050] [A] current
6-DaHall 1-PDU-14-51 | [branch#051] [A] current
6-DaHall 1-PDU-14-52 | [branch#052] [A] current
6-DaHall 1-PDU-14-53 | [branch#053] [A] current
6-DaHall 1-PDU-14-54 | [branch#054] [A] current
6-DaHall 1-CEP-05-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
6-DaHall 1-CEP-05-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
6-DaHall 1-CEP-05-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
6-DaHall 1-CEP-05-04 | [branch#004] [R] I1 | [branch#004] [S] I2 | [branch#004] [T] I3
6-DaHall 1-CEP-05-05 | [branch#005] [R] I1 | [branch#005] [S] I2 | [branch#005] [T] I3
6-DaHall 1-CEP-05-06 | [branch#006] [R] I1 | [branch#006] [S] I2 | [branch#006] [T] I3
6-DaHall 1-CEP-05-07 | [branch#007] [R] I1 | [branch#007] [S] I2 | [branch#007] [T] I3
6-DaHall 1-CEP-05-08 | [branch#008] [R] I1 | [branch#008] [S] I2 | [branch#008] [T] I3
6-DaHall 1-CEP-05-09 | [branch#009] [R] I1 | [branch#009] [S] I2 | [branch#009] [T] I3
6-DaHall 1-CEP-05-10 | [branch#010] [R] I1 | [branch#010] [S] I2 | [branch#010] [T] I3
6-DaHall 1-CEP-05-11 | [branch#011] [R] I1 | [branch#011] [S] I2 | [branch#011] [T] I3
6-DaHall 1-CEP-05-12 | [branch#012] [A] current
6-DaHall 1-CEP-05-13 | [branch#013] [A] current
6-DaHall 1-CEP-05-14 | [branch#014] [A] current
6-DaHall 1-CEP-05-15 | [branch#015] [A] current
6-DaHall 1-CEP-05-16 | [branch#016] [A] current
6-DaHall 1-CEP-05-17 | [branch#017] [A] current

## 6층_부하량(월간_MAX)
Date : 2024-01-01 ~ 2024-01-31
6-DaHall 1-CEP-05 | [7 empty] | Main CB 4P 350A
[10 empty] | MAIN 계측값 : | 2.3 | 2.1 | 2.9 | <- 실측값 |  |  | 5-DaHall 1-EH-01
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
5-DaHall 1-CEP-06 | O | ON | 58.76 | 59.71 | 58.23 |  | 4P 150A | #01
| X | OFF | 사 | 용 | 금 | 지 | 4P 50A | #02 | #03 | 4P 50A | 0 | 0 | 0 |  | X | OFF
5-DaHall 1-CRAC-14 (CF CRAC #02) | O | ON | 0 | 0 | 0 |  | 4P 50A | #04 | #05 | 4P 50A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 50A | #06 | #07 | 4P 50A | 0 | 0 | 0 |  | O | OFF | 급배기휀
| X | OFF | 0 | 0 | 0 |  | 4P 50A | #08 | #09 | 4P 50A | 0 | 0 | 0 |  | X | OFF
spare | X | OFF | 0 | 0 | 0 |  | 4P 50A | #10 | #11 | 4P 100A | 54.47 | 61.14 | 63.87 |  | O | ON | 8층 냉방분전반
| O | OFF | 0 |  |  |  | 2P 30A | #12 | #13 | 2P 30A | 0 |  |  |  | O | OFF
| O | OFF |  | 0 |  |  | 2P 30A | #14 | #15 | 2P 50A |  | 15.22 |  |  | O | ON | 7-DaHall 1-EH (7층 가습기 Main)
| O | OFF |  |  | 0 |  | 2P 30A | #16 | #17 | 2P 50A |  |  | 22.31 |  | O | ON | 6-DaHall 1-EH (6층 가습기 Main)
|  | 6층 사무실 | 37.53 | [6 empty] | 총합: | 113.23 | 136.07 | 144.41 | 0
[11 empty] | 393.71 | 37.53 | 9.532%
6-DaHall 1-PDU-13 |  | PDU : SEL1 - 6-1 - A7 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A7-18-6 | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | DE운용실 사무#1 A7-30-8
A7-18-7 | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | DE 출입통제Desk A7-31-1
A7-18-8 | O | ON | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | 6F DE 가청경보 PNL
A7-18-9 | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | OFF | A7-31-3
A7-28-1 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-4
A7-28-2 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | OFF | A7-31-5
A7-28-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | OFF | A7-31-6
A7-28-4 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-7
A7-28-5 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | A7-31-8
A7-28-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | #A7-28-3
A7-28-7 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | OFF | #A7-28-6
A7-28-8 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | OFF | #A7-29-3
A7-29-1 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | OFF | #A7-29-6
A7-29-2 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | A7-21-4(3) (M-14)
A7-29-3 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | A7-21-3(3) (M-13)
A7-29-4 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | A7-21-3(2) (M-13)
A7-29-5 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | A7-21-4(2) (M-14)
A7-29-6 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | OFF | A7-26-8(2)
A7-29-7 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | OFF | A7-26-9(2)
A7-29-8 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A7-28-9 (6층 인터넷장비)
A7-30-1 | O | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | OFF | A7-29-9
A7-30-2 | O | OFF |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | OFF | A7-30-9
A7-30-3 | O | OFF |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-9
A7-30-4 | O | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | A7-27-6
A7-30-5 | O | OFF |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | A7-26-6
A7-30-6 | O | OFF |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | ON | A4-19-1 (O-11)
A7-30-7 | O | OFF | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | OFF | A4-27-9 (G-19)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-14 |  | PDU : SEL1 - 6-1 - B7 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B7-18-6 | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | DE운용실 감시모니터 B7-30-8
B7-18-7 | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | DE운용실 사무#2 B7-31-1
B7-18-8 | O | ON | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-2
B7-18-9 | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | OFF | B7-31-3
B7-28-1 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-4
B7-28-2 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-5
B7-28-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | OFF | B7-31-6
B7-28-4 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-7
B7-28-5 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-8
B7-28-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | ON | B7-32-1 (사무실)
B7-28-7 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | OFF | B7-32-2 (사무실)
B7-28-8 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | OFF | B7-32-3 (사무실)
B7-29-1 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | OFF | B7-32-4 (사무실)
B7-29-2 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | B7-21-4(3) (M-14)
B7-29-3 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | B7-21-3(3) (M-13)
B7-29-4 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | B7-21-4(2) (M-13)
B7-29-5 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | B7-21-3(2) (M-14)
B7-29-6 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | OFF | B7-26-8(2)
B7-29-7 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | OFF | B7-26-9(2)
B7-29-8 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | OFF | B7-28-9
B7-30-1 | O | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | OFF | B7-29-9
B7-30-2 | O | OFF |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | OFF | B7-30-9
B7-30-3 | O | OFF |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-9
B7-30-4 | O | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | B7-26-6
B7-30-5 | O | OFF |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | B7-27-6
B7-30-6 | O | OFF |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | ON | B4-19-1 (O-11)
B7-30-7 | O | OFF | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | OFF | A4-27-8
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-09 |  | PDU : SEL1 - 6-1 - A5 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A3-21-1 (M-11) | O | ON | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | ON | A3-22-1 (L-11)
A3-21-2 (M-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | ON | A3-22-2 (L-12)
A3-21-3 (M-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | ON | A3-22-3 (L-13)
A3-21-4 (M-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | ON | A3-22-4 (L-14)
A3-21-5 (M-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | A3-22-5 (L-15)
A3-21-6 (M-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | A3-22-6 (L-16)
A3-21-7 (M-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | A3-22-7 (L-17)
A3-21-8 (M-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A3-22-8 (L-18)
A3-21-9 (M-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A3-22-9 (L-19)
#A3-19-4 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | A3-23-1 (K-11)
#A3-19-7 | O | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | A3-23-2 (K-12)
#A3-36-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A3-23-3 (K-13)
#A3-36-6 | O | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | A3-23-4 (K-14)
#A3-23-4 (K-14) | O | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | A3-23-5 (K-15)
#A3-23-7 (K-17) | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | A3-23-6 (K-16)
B4-19-7 (O-17) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | A3-23-7 / 6F-K-17
#A3-24-7 | O | OFF |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | A3-23-8 / 6F-K-18)
A3-24-8 (J-18) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | ON | A3-23-9 / 6F-K-19
A3-24-9 (J-19) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-1 (J-11)
#A3-25-4 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | A3-24-2 (J-12)
#A3-26-4 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | A3-24-3 (J-13)
#A3-27-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-4 (J-14)
A3-27-1 (G-11) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | A3-24-5 (J-15)
A3-27-2 (G-12) | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | OFF | A3-24-6 (J-16)
A3-27-3 (G-13) | O | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-7 (J-17)
[10 empty] | 총합: | 0 | 0 | 0 | 0
6-DaHall 1-PDU-10 |  | PDU : SEL1 - 6-1 - B5 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B3-21-1 (M-11) | O | ON | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | ON | B3-22-1 (L-11)
B3-21-2 (M-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | ON | B3-22-2 (L-12)
B3-21-3 (M-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | ON | B3-22-3 (L-13)
B3-21-4 (M-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | ON | B3-22-4 (L-14)
B3-21-5 (M-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | B3-22-5 (L-15)
B3-21-6 (M-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | B3-22-6 (L-16)
B3-21-7 (M-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | B3-22-7 (L-17)
B3-21-8 (M-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B3-22-8 (L-18)
B3-21-9 (M-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B3-22-9 (L-19)
#B3-20-4 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | B3-23-1 (K-11)
#B3-20-7 (N-17) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | B3-23-2 (K-12)
#B3-21-4 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B3-24-6 (J-16)
#B3-21-7 | O | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | B3-23-4 (K-14)
#B3-22-4 | O | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | B3-23-5 (K-15)
#B3-22-7 | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | B3-23-6 (K-16)
#B3-25-7 | O | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | B3-23-7 / 6F-K-17
#B3-26-7 | O | OFF |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B3-23-8 / 6F-K-18
B3-24-8 (J-18) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | ON | B3-23-9 / 6F-K-19
B3-24-9 (J-19) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-1 (J-11)
#B3-27-7 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | B3-24-2 (J-12)
B3-27-1 (G-11) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | B3-24-3 (J-13)
B3-27-2 (G-12) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-4 (J-14)
B3-27-3 (G-13) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | B3-24-5 (J-15)
spare | X | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B3-23-3 (K-13)
spare | X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-7 (J-17)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-11 |  | PDU : SEL1 - 6-1 - A6 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 5.1 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | OFF | A4-20-1 (N-11)
A4-19-2 (O-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | OFF | A4-20-2 (N-12)
A4-19-3 (O-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | OFF | A4-20-3 (N-13)
A4-19-4 (O-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | OFF | A4-20-4 (N-14)
A4-19-5 (O-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | A4-20-5 (N-15)
A4-19-6 (O-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | A4-20-6 (N-16)
A4-19-7 (O-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | A4-20-7 (N-17)
A4-19-8 (O-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A4-20-8 (N-18)
A4-19-9 (O-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A4-20-9 (N-19)
A4-36-1 (AG-19) | O | ON | 6.15 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | A4-25-9 (I-19)
A4-36-2 (S-10) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-1 (H-11)
A4-36-3 (S-11) | O | ON |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-2 (H-12)
A4-36-4 (S-12) | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | OFF | A4-26-3 (H-13)
A4-36-5 (S-13) | O | ON |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-4 (H-14)
A4-36-6 (S-14) | O | ON |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-5 (H-15)
A4-36-7 (S-15) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | X | OFF
A4-36-8 (S-16) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-7 (H-17)
A4-25-1 (I-11) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-8 (H-18)
A4-25-2 (I-12) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | A4-26-9 (H-19)
A4-25-3 (I-13) | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | A4-27-4 (G-14)
A4-25-4 (I-14) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | A4-27-5 (G-15)
A4-25-5 (I-15) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | A4-36-9 (AG-20)
A4-25-6 (I-16) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | A4-27-7 (G-17)
Rack S-15 | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | X | OFF
Rack S-13 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 6.15 | 0 | 0
6-DaHall 1-PDU-12 |  | PDU : SEL1 - 6-1 - B6 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 5.1 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-1 (N-11)
B4-19-2 (O-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B4-20-2 (N-12)
B4-19-3 (O-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | OFF | B4-20-3 (N-13)
B4-19-4 (O-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-4 (N-14)
B4-19-5 (O-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | B4-20-5 (N-15)
B4-19-6 (O-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | B4-20-6 (N-16)
#A3-24-4 | O | OFF | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-7 (N-17)
B4-19-8 (O-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B4-20-8 (N-18)
B4-19-9 (O-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B4-20-9 (N-19)
B4-36-1 (AG-19) | O | ON | 6.04 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | B4-25-9 (I-19)
B4-36-2 (S-10) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-1 (H-11)
B4-36-3 (S-11) | O | ON |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-2 (H-12)
B4-36-4 (S-12) | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B4-26-3 (H-13)
B4-36-5 (S-13) | O | ON |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-4 (H-14)
B4-36-6 (S-14) | O | ON |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-5 (H-15)
B4-36-7 (S-15) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | X | OFF
B4-36-8 (S-16) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-7 (H-17)
B4-25-1 (I-11) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-8 (H-18)
B4-25-2 (I-12) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | B4-26-9 (H-19)
B4-25-3 (I-13) | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | B4-27-4 (G-14)
B4-25-4 (I-14) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | B4-27-5 (G-15)
B4-25-5 (I-15) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B4-36-9 (AG-20)
B4-25-6 (I-16) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | B4-27-7 (G-17)
Rack S-15 | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | OFF | B4-27-8 (G-18)
Rack S-13 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | B4-27-9 (G-19)
[10 empty] | 총합: | 6.04 | 0 | 0
6-DaHall 1-PDU-01 |  | PDU : SEL1 - 6-1 - A1 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 21.6 | 21.2 | 16.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A1-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 2 |  |  |  | O | ON | G1101(A)
A1-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 8.94 |  |  | O | ON | G1103(A)
A1-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 3.16 |  | O | ON | A1-35-3(AG-13)
A1-1-4 (AF-16) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 4.97 |  |  |  | O | ON | A1-35-4(AG-14)
A1-1-5 (AF-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 8.89 |  |  | O | ON | A1-35-5(AG-15)
A1-1-6 (AF-14) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 8.31 |  | O | ON | A1-35-6(AG-16)
A1-1-7 (AF-13) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 6.61 |  |  |  | O | ON | A1-35-7(AG-17)
A1-1-8 (AF-12) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 6.84 |  |  | O | ON | A1-35-8 (AG-18)
A1-1-9 (AF-11) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A1-16-4 (R-14)
#A1-1-3 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | A1-16-5 (R-15)
#A1-1-7 | O | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | A1-16-6 (R-16)
#A1-35-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A1-16-7 (R-17)
6-1-A1-30-25 | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | A1-16-8 (R-18)
A1-13-1 (AA-11) | O | ON |  | 2.29 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | A1-16-9 (R-19)
A1-13-2 (AA-12) | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | OFF | #A1-13-4
A1-13-3 (AA-13) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | OFF | #A1-16-4
A1-13-4 (AA-14) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | X | OFF | A1-4-1
A1-13-5 (AA-15) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 2.78 |  | O | ON | G1102(A)
A1-13-6 (AA-16) | O | ON | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | X | OFF | G1102 하부(미사용)
A1-13-7 (AA-17) | O | ON |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | A1-35-3(2)(위치 불명)
B209 / (AA-18) | O | ON |  |  | 1.03 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 4.52 |  | O | ON | B411
A1-13-9 (B410) | O | ON | 5.6 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B211 | A1-30-44 를 B211에 포설 예정('23.05월초)
A1-16-1 (R-11) | O | ON |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0.66 |  |  | O | ON | 신규 BMS(6F TPS실) Rack
A1-16-2 (R-12) | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | A1-4-8 (AC-12)
B210 / (AA-19) | O | OFF | 10.24 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | ON | FMS 6층 전원
[10 empty] | 총합: | 29.42 | 27.62 | 19.8
6-DaHall 1-PDU-02 |  | PDU : SEL1 - 6-1 - B1 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 19.2 | 18.8 | 21.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B1-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 1.5 |  |  |  | O | ON | G1101 (B)
B1-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 7.19 |  |  | O | ON | G1103 (B)
B1-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 5.31 |  | O | ON | B1-35-3(AG-13)
B1-1-4 (AF-16) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 3.46 |  |  |  | O | ON | B1-35-4(AG-14)
B1-1-5 (AF-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 8.75 |  |  | O | ON | B1-35-5(AG-15)
B1-1-6 (AF-14) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 10.46 |  | O | ON | B1-35-6(AG-16)
B1-1-7 (AF-13) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 8.49 |  |  |  | O | ON | B1-35-7(AG-17)
B1-1-8 (AF-12) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 5.49 |  |  | O | ON | B1-35-8 (AG-18)
B1-1-9 (AF-11) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | X | OFF | 6-1-B1-30-18
#B1-2-3 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | B1-16-5 (R-15)
#B1-2-7 | O | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | B1-16-6 (R-16)
#B1-3-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | B1-16-7 (R-17)
6-1-B1-30-25 | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | B1-16-8 (R-18)
B1-13-1 (AA-11) | O | ON |  | 1.37 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | B1-16-9 (R-19)
B1-13-2 (AA-12) | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 10.32 |  | O | OFF | B210 / (AA-19) | B1-30-30 사용예정
B1-13-3 (AA-13) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | OFF | #B1-16-7
B1-13-4 (AA-14) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B1-16-4 (R-14)
B1-13-5 (AA-15) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 3.57 |  | O | ON | G1102 (B)
B1-13-6 (AA-16) | O | ON | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | G1102 하부(도어락&CCTV)
B1-13-7 (AA-17) | O | ON |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | B1-35-3(2)(위치 불명)
B209 / (AA-18) | O | ON |  |  | 0.8 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 4.55 |  | O | ON | B411
B1-13-9 (B410) | O | ON | 6.12 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B211 | B1-30-44 를 B211에 포설 예정('23.05월초)
B1-16-1 (R-11) | O | ON |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | X | OFF | B1-4-7
B1-16-2 (R-12) | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B1-4-8 (AC-12)
| X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 19.57 | 22.8 | 35.01
6-DaHall 1-PDU-03 |  | PDU : SEL1 - 6-1 - A2 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 20.7 | 21.3 | 10.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A2-2-1 | O | ON | 7.67 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | X | OFF | A2-3-1
A2-2-2 | O | ON |  | 6.74 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | X | OFF | A2-3-2
A2-2-3 | O | ON |  |  | 0.94 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | X | OFF | A2-3-3
A2-2-4 | O | ON | 4.2 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | X | OFF | A2-3-4
A2-2-5 | O | ON |  | 3.56 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | X | OFF | A2-3-5
A2-2-6 | O | ON |  |  | 4.27 | `` | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | X | OFF | A2-3-6
A2-2-7 | O | ON | 6.95 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | X | OFF | A2-3-7
A2-2-8 | O | ON |  | 4.31 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A2-3-8 (AD-12)
A2-2-9 | O | ON |  |  | 2.12 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A2-3-9 (AD-11)
A2-5-1 | X | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | A2-6-8
A2-5-2 | X | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | A2-7-1 (V-17)
A2-5-3 | X | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A2-7-2 (V-17)
A2-5-4 | X | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | A2-7-3 (V-16)
A2-5-5 | X | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | A2-7-4 (V-15)
A2-5-6 | X | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | A2-7-5 (V-14)
A2-5-7 | X | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | A2-7-6 (V-13)
A2-5-8 (AB-12) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | A2-7-7 (V-12)
A2-5-9 (AB-11) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | A2-7-8 (V-11)
A2-6-1 | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | A2-8-1 (V-16)
A2-6-2 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | A2-8-2 (W-17)
A2-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | ON | A2-8-3 (W-16)
A2-6-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | ON | A2-8-4 (W-15)
A2-6-5 | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | ON | A2-8-5 (W-14)
A2-6-6 | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | A2-8-6 (W-13)
손혈관인식시스템 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 18.82 | 14.61 | 7.33
6-DaHall 1-PDU-04 |  | PDU : SEL1 - 6-1 - B2 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 18.6 | 29.1 | 14.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B2-2-1 | O | ON | 6.64 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | X | OFF | B2-3-1
B2-2-2 | O | ON |  | 7.45 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | X | OFF | B2-3-2
B2-2-3 | O | ON |  |  | 1.5 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | X | OFF | B2-3-3
B2-2-4 | O | ON | 4.36 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | X | OFF | B2-3-4
B2-2-5 | O | ON |  | 4.07 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | X | OFF | B2-3-5
B2-2-6 | O | ON |  |  | 4.94 | `` | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | X | OFF | B2-3-6
B2-2-7 | O | ON | 5.41 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | X | OFF | B2-3-7
B2-2-8 | O | ON |  | 3.98 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B2-3-8 (AD-12)
B2-2-9 | O | ON |  |  | 1.91 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B2-3-9 (AD-11)
B2-5-1 | X | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | B2-6-8
B2-5-2 | X | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | B2-7-1 (V-17)
B2-5-3 | X | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | B2-7-2 (V-17)
B2-5-4 | X | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | B2-7-3 (V-16)
B2-5-5 | X | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | B2-7-4 (V-15)
B2-5-6 | X | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | B2-7-5 (V-14)
B2-5-7 | X | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | B2-7-6 (V-13)
B2-5-8 (AB-12) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B2-7-7 (V-12)
B2-5-9 (AB-11) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | B2-7-8 (V-11)
B2-6-1 | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | B2-8-1 (V-16)
B2-6-2 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | B2-8-2 (W-17)
B2-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | ON | B2-8-3 (W-16)
B2-6-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | ON | B2-8-4 (W-15)
B2-6-5 | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | ON | B2-8-5 (W-14)
B2-6-6 | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B2-8-6 (W-13)
| X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 16.41 | 15.5 | 8.35
6-DaHall 1-PDU-05 |  | PDU : SEL1 - 6-1 - A3 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 19.5 | 43.6 | 27 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A5-8-7 (W-12) | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 13.13 |  |  | O | ON | A5-15-1 (T-11)
A5-8-8 (W-11) | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 5.65 |  | O | ON | A5-15-2 (T-12)
A5-9-1 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0.72 |  |  |  | O | ON | A5-15-3 (T-13)
A5-9-2 (X-17) | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 3.83 |  |  | O | ON | A5-15-4 (T-14)
A5-9-3 (X-16) | O | ON |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 1.08 |  | O | ON | A5-15-5 (T-15)
A5-9-4 (X-15) | O | ON | 2.35 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 1.48 |  |  |  | O | ON | A5-15-6 (T-16)
A5-9-5 (X-14) | O | ON |  | 2.16 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 5.56 |  |  | O | ON | A5-15-7 (T-17)
A5-9-6 (X-13) | O | ON |  |  | 3.93 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 3.71 |  | O | ON | A5-15-8 (T-18)
A5-9-7 (X-12) | O | ON | 1.13 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | A5-15-9
A5-9-8 (X-11) | O | ON |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | ON | A5-17-1 (Q-11)
A5-10-1 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | A5-17-2 (Q-12)
A807(A5-10-2) | O | ON | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | A5-17-3 (Q-13)
A5-10-3 (A806 - 1) | O | ON |  | 12.11 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | A5-17-4 (Q-14)
A5-10-4 (A806 - 2) | O | ON |  |  | 5.5 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | A5-17-5 (Q-15)
A5-10-5 (Y-14) | O | ON | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | A5-17-6 (Q-16)
A5-10-6 (Y-13) | O | ON |  | 1.63 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | A5-17-7 (Q-17)
A5-10-7 (Y-12) | O | ON |  |  | 1.13 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | A5-17-8 (Q-18)
A5-10-8 (Y-11) | O | ON | 0.68 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | A5-17-9 (Q-19)
A5-14-1 (U-10) | O | ON |  | 8.43 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | A5-18-1 (P-11)
A5-14-2 (U-11) | O | ON |  |  | 2.2 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A5-18-2 (P-12)
A5-14-3 (U-12) | O | ON | 2.15 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | A5-18-3 (P-13)
A5-14-4 (U-13) | O | ON |  | 6.33 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | A5-18-4 (P-14)
A5-14-5 (U-14) | O | ON |  |  | 5.42 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | A5-18-5 (P-15)
6-1-A3-47 | O | ON | 5.11 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | ON | A5-16-3 (R-13)
A5-14-7 (U-16) | O | ON |  | 9.14 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | ON | A5-4-9 (AC-11)
6-1-A3-51 | O | ON |  |  | 5.08 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | A5-6-7
6-1-A3-53 | O | ON | 6.63 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 4.5 |  |  |  | O | ON | A5-15-5(2) (T-15)
[10 empty] | 총합: | 24.75 | 62.32 | 33.7
6-DaHall 1-PDU-06 |  | PDU : SEL1 - 6-1 - B3 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 12.5 | 37.1 | 24.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B5-8-7 (W-12) | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 11.95 |  |  | O | ON | B5-15-1 (T-11)
B5-8-8 (W-11) | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 4.54 |  | O | ON | B5-15-2 (T-12)
B5-9-1 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0.72 |  |  |  | O | ON | B5-15-3 (T-13)
B5-9-2 | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 4.53 |  |  | O | ON | B5-15-4 (T-14)
B5-9-3 | O | ON |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0.55 |  | O | ON | B5-15-5 (T-15)
B5-9-4 (X-15) | O | ON | 1.93 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | B5-15-6 (T-16)
B5-9-5 (X-14) | O | ON |  | 3.86 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 3.53 |  |  | O | ON | B5-15-7 (T-17)
B5-9-6 (X-13) | O | ON |  |  | 3.4 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 4.58 |  | O | ON | B5-15-8 (T-18)
B5-9-7 (X-12) | O | ON | 1.03 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | B5-15-9
B5-9-8 (X-11) | O | ON |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | ON | B5-17-1 (Q-11)
B5-10-1 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | B5-17-2 (Q-12)
A807(B5-10-2) | O | ON | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | B5-17-3 (Q-13)
B5-10-3 (A806 - 1) | O | ON |  | 7.95 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | B5-17-4 (Q-14)
B5-10-4 (A806 - 2) | O | ON |  |  | 7.03 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | B5-17-5 (Q-15)
B5-10-5 (Y-14) | O | ON | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | B5-17-6 (Q-16)
B5-10-6 (Y-13) | O | ON |  | 0.39 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | B5-17-7 (Q-17)
B5-10-7 (Y-12) | O | ON |  |  | 1.2 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | B5-17-8 (Q-18)
B5-10-8 (Y-11) | O | ON | 0.39 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | B5-17-9 (Q-19)
A5-14-1 (U-10) | O | ON |  | 10.92 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | B5-18-1 (P-11)
A5-14-2 (U-11) | O | ON |  |  | 2.12 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | B5-18-2 (P-12)
A5-14-3 (U-12) | O | ON | 1.23 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | B5-18-3 (P-13)
A5-14-4 (U-13) | O | ON |  | 5.49 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | B5-18-4 (P-14)
A5-14-5 (U-14) | O | ON |  |  | 5.45 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | B5-18-5 (P-15)
6-1-B3-47 | O | ON | 4.91 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | ON | B5-16-3 (R-13)
A5-14-7 (U-16) | O | ON |  | 1.51 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | ON | B5-4-9 (AC-11)
6-1-B3-51 | O | ON |  |  | 5.68 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | B5-6-7
6-1-B3-53 | O | ON | 0.9 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 2.71 |  |  |  | O | ON | B5-15-5(2) (T-15)
[10 empty] | 총합: | 13.82 | 50.13 | 34.55
6-DaHall 1-PDU-07 |  | PDU : SEL1 - 6-1 - A4 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
#A6-4-4 | O | OFF |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | A6-4-1
#A6-4-7 | O | OFF |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | A6-4-2
#A6-5-4 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | A6-4-3
#A6-5-7 | O | OFF |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | ON | A6-4-4 (AC-16)
#A6-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | ON | A6-4-5 (AC-15)
#A6-6-6 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | A6-4-6 (AC-14)
#A6-7-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | ON | A6-4-7 (AC-13)
#A6-7-6 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | A6-5-1
#A6-8-3 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | A6-5-2
#A6-8-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | A6-5-3
#A6-9-3 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | A6-5-4 (AB-16)
#A6-9-6 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | A6-5-5 (AB-15)
#A6-10-3 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | A6-5-6 (AB-14)
#A6-10-6 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | A6-5-7 (AB-13)
#A6-14-4 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | OFF | A6-2-1
#A6-14-7 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | OFF | A6-2-2
#A6-15-4 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | OFF | A6-2-3
#A6-15-7 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | A6-2-4 (AE-16)
#A6-17-4 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | A6-2-5 (AE-15)
#A6-17-7 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A6-2-6 (AE-14)
A6-8-8(1) | O | ON | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | A6-2-7 (AE-13)
A6-8-7(1) | O | ON |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | A6-2-8 (AE-12)
A6-8-6(1) | O | ON |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | A6-2-9 (AE-11)
불량 | X | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | A6-3-1
A6-3-7 (AD-13) | O | ON |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | A6-3-2
A6-3-6 (AD-14) | O | ON |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | A6-3-3
A6-3-5 (AD-15) | O | ON | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | ON | A6-3-4 (AD-16)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-08 |  | PDU : SEL1 - 6-1 - B4 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
#B6-28-3 | X | OFF |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | B6-4-1
#B6-28-6 | X | OFF |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | B6-4-2
#B6-29-3 | X | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | B6-4-3
#B6-29-6 | X | OFF |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | ON | B6-4-4 (AC-16)
#B6-30-3 | X | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | ON | B6-4-5 (AC-15)
#B6-30-6 | X | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | B6-4-6 (AC-14)
#B6-31-3 | X | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | ON | B6-4-7 (AC-13)
#B6-31-6 | X | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | B6-5-1
#B6-32-3 | X | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | B6-5-2
#B6-32-6 | X | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | B6-5-3
#B6-33-3 | X | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | B6-5-4 (AB-16)
#B6-33-6 | X | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | B6-5-5 (AB-15)
| X | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | B6-5-6 (AB-14)
| X | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | B6-5-7 (AB-13)
| X | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | OFF | B6-2-1
| X | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | OFF | B6-2-2
| X | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | OFF | B6-2-3
| X | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | B6-2-4 (AE-16)
| X | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | B6-2-5 (AE-15)
| X | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | B6-2-6 (AE-14)
| X | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | B6-2-7 (AE-13)
B6-8-8(1) | O | ON |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | B6-2-8 (AE-12)
B6-8-7(1) | O | ON |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | B6-2-9 (AE-11)
B6-8-6(1) | O | ON | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | B6-3-1
B6-3-7 (AD-13) | O | ON |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | B6-3-2
B6-3-6 (AD-14) | O | ON |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | B6-3-3
B6-3-5 (AD-15) | O | ON | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | ON | B6-3-4 (AD-16)
[10 empty] | 총합: | 0 | 0 | 0
| IDC | 466.7

## 6층_부하량(월간_AVG)
Date : 2024-01-01 ~ 2024-01-31
6-DaHall 1-CEP-05 | [7 empty] | Main CB 4P 350A
[10 empty] | MAIN 계측값 : | 2.3 | 2.1 | 2.9 | <- 실측값 |  |  | 5-DaHall 1-EH-01
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
5-DaHall 1-CEP-06 | O | ON | 0.25451 | 0.78783 | 0.70159 |  | 4P 150A | #01
| X | OFF | 사 | 용 | 금 | 지 | 4P 50A | #02 | #03 | 4P 50A | 0 | 0 | 0 |  | X | OFF
5-DaHall 1-CRAC-14 (CF CRAC #02) | O | ON | 0 | 0 | 0 |  | 4P 50A | #04 | #05 | 4P 50A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 50A | #06 | #07 | 4P 50A | 0 | 0 | 0 |  | O | OFF | 급배기휀
| X | OFF | 0 | 0 | 0 |  | 4P 50A | #08 | #09 | 4P 50A | 0 | 0 | 0 |  | X | OFF
spare | X | OFF | 0 | 0 | 0 |  | 4P 50A | #10 | #11 | 4P 100A | 6.4556 | 11.9344 | 12.1109 |  | O | ON | 8층 냉방분전반
| O | OFF | 0 |  |  |  | 2P 30A | #12 | #13 | 2P 30A | 0 |  |  |  | O | OFF
| O | OFF |  | 0 |  |  | 2P 30A | #14 | #15 | 2P 50A |  | 9.9254 |  |  | O | ON | 7-DaHall 1-EH (7층 가습기 Main)
| O | OFF |  |  | 0 |  | 2P 30A | #16 | #17 | 2P 50A |  |  | 9.5847 |  | O | ON | 6-DaHall 1-EH (6층 가습기 Main)
|  | 6층 사무실 | 19.51 | [6 empty] | 총합: | 6.7102 | 22.6476 | 22.3972 | 0
[11 empty] | 51.7549 | 19.51 | 37.7%
6-DaHall 1-PDU-13 |  | PDU : SEL1 - 6-1 - A7 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A7-18-6 | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | DE운용실 사무#1 A7-30-8
A7-18-7 | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | DE 출입통제Desk A7-31-1
A7-18-8 | O | ON | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | 6F DE 가청경보 PNL
A7-18-9 | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | OFF | A7-31-3
A7-28-1 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-4
A7-28-2 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | OFF | A7-31-5
A7-28-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | OFF | A7-31-6
A7-28-4 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-7
A7-28-5 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | A7-31-8
A7-28-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | #A7-28-3
A7-28-7 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | OFF | #A7-28-6
A7-28-8 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | OFF | #A7-29-3
A7-29-1 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | OFF | #A7-29-6
A7-29-2 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | A7-21-4(3) (M-14)
A7-29-3 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | A7-21-3(3) (M-13)
A7-29-4 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | A7-21-3(2) (M-13)
A7-29-5 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | A7-21-4(2) (M-14)
A7-29-6 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | OFF | A7-26-8(2)
A7-29-7 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | OFF | A7-26-9(2)
A7-29-8 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A7-28-9 (6층 인터넷장비)
A7-30-1 | O | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | OFF | A7-29-9
A7-30-2 | O | OFF |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | OFF | A7-30-9
A7-30-3 | O | OFF |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-9
A7-30-4 | O | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | A7-27-6
A7-30-5 | O | OFF |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | A7-26-6
A7-30-6 | O | OFF |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | ON | A4-19-1 (O-11)
A7-30-7 | O | OFF | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | OFF | A4-27-9 (G-19)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-14 |  | PDU : SEL1 - 6-1 - B7 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B7-18-6 | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | DE운용실 감시모니터 B7-30-8
B7-18-7 | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | DE운용실 사무#2 B7-31-1
B7-18-8 | O | ON | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-2
B7-18-9 | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | OFF | B7-31-3
B7-28-1 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-4
B7-28-2 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-5
B7-28-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | OFF | B7-31-6
B7-28-4 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-7
B7-28-5 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-8
B7-28-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | ON | B7-32-1 (사무실)
B7-28-7 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | OFF | B7-32-2 (사무실)
B7-28-8 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | OFF | B7-32-3 (사무실)
B7-29-1 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | OFF | B7-32-4 (사무실)
B7-29-2 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | B7-21-4(3) (M-14)
B7-29-3 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | B7-21-3(3) (M-13)
B7-29-4 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | B7-21-4(2) (M-13)
B7-29-5 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | B7-21-3(2) (M-14)
B7-29-6 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | OFF | B7-26-8(2)
B7-29-7 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | OFF | B7-26-9(2)
B7-29-8 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | OFF | B7-28-9
B7-30-1 | O | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | OFF | B7-29-9
B7-30-2 | O | OFF |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | OFF | B7-30-9
B7-30-3 | O | OFF |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-9
B7-30-4 | O | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | B7-26-6
B7-30-5 | O | OFF |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | B7-27-6
B7-30-6 | O | OFF |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | ON | B4-19-1 (O-11)
B7-30-7 | O | OFF | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | OFF | A4-27-8
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-09 |  | PDU : SEL1 - 6-1 - A5 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A3-21-1 (M-11) | O | ON | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | ON | A3-22-1 (L-11)
A3-21-2 (M-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | ON | A3-22-2 (L-12)
A3-21-3 (M-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | ON | A3-22-3 (L-13)
A3-21-4 (M-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | ON | A3-22-4 (L-14)
A3-21-5 (M-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | A3-22-5 (L-15)
A3-21-6 (M-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | A3-22-6 (L-16)
A3-21-7 (M-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | A3-22-7 (L-17)
A3-21-8 (M-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A3-22-8 (L-18)
A3-21-9 (M-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A3-22-9 (L-19)
#A3-19-4 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | A3-23-1 (K-11)
#A3-19-7 | O | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | A3-23-2 (K-12)
#A3-36-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A3-23-3 (K-13)
#A3-36-6 | O | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | A3-23-4 (K-14)
#A3-23-4 (K-14) | O | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | A3-23-5 (K-15)
#A3-23-7 (K-17) | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | A3-23-6 (K-16)
B4-19-7 (O-17) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | A3-23-7 / 6F-K-17
#A3-24-7 | O | OFF |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | A3-23-8 / 6F-K-18)
A3-24-8 (J-18) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | ON | A3-23-9 / 6F-K-19
A3-24-9 (J-19) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-1 (J-11)
#A3-25-4 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | A3-24-2 (J-12)
#A3-26-4 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | A3-24-3 (J-13)
#A3-27-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-4 (J-14)
A3-27-1 (G-11) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | A3-24-5 (J-15)
A3-27-2 (G-12) | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | OFF | A3-24-6 (J-16)
A3-27-3 (G-13) | O | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-7 (J-17)
[10 empty] | 총합: | 0 | 0 | 0 | 0
6-DaHall 1-PDU-10 |  | PDU : SEL1 - 6-1 - B5 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B3-21-1 (M-11) | O | ON | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | ON | B3-22-1 (L-11)
B3-21-2 (M-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | ON | B3-22-2 (L-12)
B3-21-3 (M-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | ON | B3-22-3 (L-13)
B3-21-4 (M-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | ON | B3-22-4 (L-14)
B3-21-5 (M-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | B3-22-5 (L-15)
B3-21-6 (M-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | B3-22-6 (L-16)
B3-21-7 (M-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | B3-22-7 (L-17)
B3-21-8 (M-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B3-22-8 (L-18)
B3-21-9 (M-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B3-22-9 (L-19)
#B3-20-4 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | B3-23-1 (K-11)
#B3-20-7 (N-17) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | B3-23-2 (K-12)
#B3-21-4 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B3-24-6 (J-16)
#B3-21-7 | O | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | B3-23-4 (K-14)
#B3-22-4 | O | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | B3-23-5 (K-15)
#B3-22-7 | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | B3-23-6 (K-16)
#B3-25-7 | O | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | B3-23-7 / 6F-K-17
#B3-26-7 | O | OFF |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B3-23-8 / 6F-K-18
B3-24-8 (J-18) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | ON | B3-23-9 / 6F-K-19
B3-24-9 (J-19) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-1 (J-11)
#B3-27-7 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | B3-24-2 (J-12)
B3-27-1 (G-11) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | B3-24-3 (J-13)
B3-27-2 (G-12) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-4 (J-14)
B3-27-3 (G-13) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | B3-24-5 (J-15)
spare | X | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B3-23-3 (K-13)
spare | X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-7 (J-17)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-11 |  | PDU : SEL1 - 6-1 - A6 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 5.1 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | OFF | A4-20-1 (N-11)
A4-19-2 (O-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | OFF | A4-20-2 (N-12)
A4-19-3 (O-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | OFF | A4-20-3 (N-13)
A4-19-4 (O-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | OFF | A4-20-4 (N-14)
A4-19-5 (O-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | A4-20-5 (N-15)
A4-19-6 (O-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | A4-20-6 (N-16)
A4-19-7 (O-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | A4-20-7 (N-17)
A4-19-8 (O-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A4-20-8 (N-18)
A4-19-9 (O-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A4-20-9 (N-19)
A4-36-1 (AG-19) | O | ON | 5.355 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | A4-25-9 (I-19)
A4-36-2 (S-10) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-1 (H-11)
A4-36-3 (S-11) | O | ON |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-2 (H-12)
A4-36-4 (S-12) | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | OFF | A4-26-3 (H-13)
A4-36-5 (S-13) | O | ON |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-4 (H-14)
A4-36-6 (S-14) | O | ON |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-5 (H-15)
A4-36-7 (S-15) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | X | OFF
A4-36-8 (S-16) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-7 (H-17)
A4-25-1 (I-11) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-8 (H-18)
A4-25-2 (I-12) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | A4-26-9 (H-19)
A4-25-3 (I-13) | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | A4-27-4 (G-14)
A4-25-4 (I-14) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | A4-27-5 (G-15)
A4-25-5 (I-15) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | A4-36-9 (AG-20)
A4-25-6 (I-16) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | A4-27-7 (G-17)
Rack S-15 | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | X | OFF
Rack S-13 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 5.355 | 0 | 0
6-DaHall 1-PDU-12 |  | PDU : SEL1 - 6-1 - B6 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 5.1 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-1 (N-11)
B4-19-2 (O-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B4-20-2 (N-12)
B4-19-3 (O-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | OFF | B4-20-3 (N-13)
B4-19-4 (O-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-4 (N-14)
B4-19-5 (O-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | B4-20-5 (N-15)
B4-19-6 (O-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | B4-20-6 (N-16)
#A3-24-4 | O | OFF | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-7 (N-17)
B4-19-8 (O-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B4-20-8 (N-18)
B4-19-9 (O-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B4-20-9 (N-19)
B4-36-1 (AG-19) | O | ON | 5.2948 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | B4-25-9 (I-19)
B4-36-2 (S-10) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-1 (H-11)
B4-36-3 (S-11) | O | ON |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-2 (H-12)
B4-36-4 (S-12) | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B4-26-3 (H-13)
B4-36-5 (S-13) | O | ON |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-4 (H-14)
B4-36-6 (S-14) | O | ON |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-5 (H-15)
B4-36-7 (S-15) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | X | OFF
B4-36-8 (S-16) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-7 (H-17)
B4-25-1 (I-11) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-8 (H-18)
B4-25-2 (I-12) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | B4-26-9 (H-19)
B4-25-3 (I-13) | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | B4-27-4 (G-14)
B4-25-4 (I-14) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | B4-27-5 (G-15)
B4-25-5 (I-15) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B4-36-9 (AG-20)
B4-25-6 (I-16) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | B4-27-7 (G-17)
Rack S-15 | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | OFF | B4-27-8 (G-18)
Rack S-13 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | B4-27-9 (G-19)
[10 empty] | 총합: | 5.2948 | 0 | 0
6-DaHall 1-PDU-01 |  | PDU : SEL1 - 6-1 - A1 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 21.6 | 21.2 | 16.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A1-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 1.9684 |  |  |  | O | ON | G1101(A)
A1-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 3.5632 |  |  | O | ON | G1103(A)
A1-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 3.0188 |  | O | ON | A1-35-3(AG-13)
A1-1-4 (AF-16) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 4.8658 |  |  |  | O | ON | A1-35-4(AG-14)
A1-1-5 (AF-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 7.4314 |  |  | O | ON | A1-35-5(AG-15)
A1-1-6 (AF-14) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 7.4215 |  | O | ON | A1-35-6(AG-16)
A1-1-7 (AF-13) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 5.4139 |  |  |  | O | ON | A1-35-7(AG-17)
A1-1-8 (AF-12) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 5.6209 |  |  | O | ON | A1-35-8 (AG-18)
A1-1-9 (AF-11) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A1-16-4 (R-14)
#A1-1-3 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | A1-16-5 (R-15)
#A1-1-7 | O | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | A1-16-6 (R-16)
#A1-35-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A1-16-7 (R-17)
6-1-A1-30-25 | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | A1-16-8 (R-18)
A1-13-1 (AA-11) | O | ON |  | 2.2737 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | A1-16-9 (R-19)
A1-13-2 (AA-12) | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | OFF | #A1-13-4
A1-13-3 (AA-13) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | OFF | #A1-16-4
A1-13-4 (AA-14) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | X | OFF | A1-4-1
A1-13-5 (AA-15) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0.95324 |  | O | ON | G1102(A)
A1-13-6 (AA-16) | O | ON | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | X | OFF | G1102 하부(미사용)
A1-13-7 (AA-17) | O | ON |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | A1-35-3(2)(위치 불명)
B209 / (AA-18) | O | ON |  |  | 0.82312 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 3.9927 |  | O | ON | B411
A1-13-9 (B410) | O | ON | 3.7276 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B211 | A1-30-44 를 B211에 포설 예정('23.05월초)
A1-16-1 (R-11) | O | ON |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0.55708 |  |  | O | ON | 신규 BMS(6F TPS실) Rack
A1-16-2 (R-12) | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | A1-4-8 (AC-12)
B210 / (AA-19) | O | OFF | 8.1177 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | ON | FMS 6층 전원
[10 empty] | 총합: | 24.0934 | 19.4463 | 16.2093
6-DaHall 1-PDU-02 |  | PDU : SEL1 - 6-1 - B1 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 19.2 | 18.8 | 21.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B1-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 1.4818 |  |  |  | O | ON | G1101 (B)
B1-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 2.5643 |  |  | O | ON | G1103 (B)
B1-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 5.0794 |  | O | ON | B1-35-3(AG-13)
B1-1-4 (AF-16) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 3.3518 |  |  |  | O | ON | B1-35-4(AG-14)
B1-1-5 (AF-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 7.1668 |  |  | O | ON | B1-35-5(AG-15)
B1-1-6 (AF-14) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 9.4983 |  | O | ON | B1-35-6(AG-16)
B1-1-7 (AF-13) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 7.2019 |  |  |  | O | ON | B1-35-7(AG-17)
B1-1-8 (AF-12) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 5.1897 |  |  | O | ON | B1-35-8 (AG-18)
B1-1-9 (AF-11) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | X | OFF | 6-1-B1-30-18
#B1-2-3 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | B1-16-5 (R-15)
#B1-2-7 | O | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | B1-16-6 (R-16)
#B1-3-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | B1-16-7 (R-17)
6-1-B1-30-25 | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | B1-16-8 (R-18)
B1-13-1 (AA-11) | O | ON |  | 1.3432 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | B1-16-9 (R-19)
B1-13-2 (AA-12) | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 8.0599 |  | O | OFF | B210 / (AA-19) | B1-30-30 사용예정
B1-13-3 (AA-13) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | OFF | #B1-16-7
B1-13-4 (AA-14) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B1-16-4 (R-14)
B1-13-5 (AA-15) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 1.393 |  | O | ON | G1102 (B)
B1-13-6 (AA-16) | O | ON | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | G1102 하부(도어락&CCTV)
B1-13-7 (AA-17) | O | ON |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | B1-35-3(2)(위치 불명)
B209 / (AA-18) | O | ON |  |  | 0.62934 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 4.105 |  | O | ON | B411
B1-13-9 (B410) | O | ON | 3.7623 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B211 | B1-30-44 를 B211에 포설 예정('23.05월초)
B1-16-1 (R-11) | O | ON |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | X | OFF | B1-4-7
B1-16-2 (R-12) | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B1-4-8 (AC-12)
| X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 15.7978 | 16.264 | 28.7649
6-DaHall 1-PDU-03 |  | PDU : SEL1 - 6-1 - A2 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 20.7 | 21.3 | 10.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A2-2-1 | O | ON | 5.0595 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | X | OFF | A2-3-1
A2-2-2 | O | ON |  | 4.2526 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | X | OFF | A2-3-2
A2-2-3 | O | ON |  |  | 0.90176 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | X | OFF | A2-3-3
A2-2-4 | O | ON | 3.8382 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | X | OFF | A2-3-4
A2-2-5 | O | ON |  | 2.9847 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | X | OFF | A2-3-5
A2-2-6 | O | ON |  |  | 3.1839 | `` | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | X | OFF | A2-3-6
A2-2-7 | O | ON | 4.4701 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | X | OFF | A2-3-7
A2-2-8 | O | ON |  | 4.0322 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A2-3-8 (AD-12)
A2-2-9 | O | ON |  |  | 2.0482 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A2-3-9 (AD-11)
A2-5-1 | X | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | A2-6-8
A2-5-2 | X | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | A2-7-1 (V-17)
A2-5-3 | X | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A2-7-2 (V-17)
A2-5-4 | X | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | A2-7-3 (V-16)
A2-5-5 | X | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | A2-7-4 (V-15)
A2-5-6 | X | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | A2-7-5 (V-14)
A2-5-7 | X | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | A2-7-6 (V-13)
A2-5-8 (AB-12) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | A2-7-7 (V-12)
A2-5-9 (AB-11) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | A2-7-8 (V-11)
A2-6-1 | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | A2-8-1 (V-16)
A2-6-2 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | A2-8-2 (W-17)
A2-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | ON | A2-8-3 (W-16)
A2-6-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | ON | A2-8-4 (W-15)
A2-6-5 | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | ON | A2-8-5 (W-14)
A2-6-6 | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | A2-8-6 (W-13)
손혈관인식시스템 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 13.3678 | 11.2695 | 6.1338
6-DaHall 1-PDU-04 |  | PDU : SEL1 - 6-1 - B2 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 18.6 | 29.1 | 14.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B2-2-1 | O | ON | 4.0983 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | X | OFF | B2-3-1
B2-2-2 | O | ON |  | 4.8921 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | X | OFF | B2-3-2
B2-2-3 | O | ON |  |  | 1.1937 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | X | OFF | B2-3-3
B2-2-4 | O | ON | 4.0589 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | X | OFF | B2-3-4
B2-2-5 | O | ON |  | 3.4325 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | X | OFF | B2-3-5
B2-2-6 | O | ON |  |  | 3.8195 | `` | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | X | OFF | B2-3-6
B2-2-7 | O | ON | 2.8435 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | X | OFF | B2-3-7
B2-2-8 | O | ON |  | 3.7444 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B2-3-8 (AD-12)
B2-2-9 | O | ON |  |  | 1.8518 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B2-3-9 (AD-11)
B2-5-1 | X | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | B2-6-8
B2-5-2 | X | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | B2-7-1 (V-17)
B2-5-3 | X | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | B2-7-2 (V-17)
B2-5-4 | X | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | B2-7-3 (V-16)
B2-5-5 | X | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | B2-7-4 (V-15)
B2-5-6 | X | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | B2-7-5 (V-14)
B2-5-7 | X | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | B2-7-6 (V-13)
B2-5-8 (AB-12) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B2-7-7 (V-12)
B2-5-9 (AB-11) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | B2-7-8 (V-11)
B2-6-1 | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | B2-8-1 (V-16)
B2-6-2 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | B2-8-2 (W-17)
B2-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | ON | B2-8-3 (W-16)
B2-6-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | ON | B2-8-4 (W-15)
B2-6-5 | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | ON | B2-8-5 (W-14)
B2-6-6 | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B2-8-6 (W-13)
| X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 11.0007 | 12.069 | 6.865
6-DaHall 1-PDU-05 |  | PDU : SEL1 - 6-1 - A3 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 19.5 | 43.6 | 27 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A5-8-7 (W-12) | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 11.5171 |  |  | O | ON | A5-15-1 (T-11)
A5-8-8 (W-11) | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 5.2189 |  | O | ON | A5-15-2 (T-12)
A5-9-1 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0.71 |  |  |  | O | ON | A5-15-3 (T-13)
A5-9-2 (X-17) | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 2.7817 |  |  | O | ON | A5-15-4 (T-14)
A5-9-3 (X-16) | O | ON |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 1.007 |  | O | ON | A5-15-5 (T-15)
A5-9-4 (X-15) | O | ON | 1.81 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 1.4167 |  |  |  | O | ON | A5-15-6 (T-16)
A5-9-5 (X-14) | O | ON |  | 2.0275 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 4.9341 |  |  | O | ON | A5-15-7 (T-17)
A5-9-6 (X-13) | O | ON |  |  | 3.7039 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 3.3747 |  | O | ON | A5-15-8 (T-18)
A5-9-7 (X-12) | O | ON | 0.95682 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | A5-15-9
A5-9-8 (X-11) | O | ON |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | ON | A5-17-1 (Q-11)
A5-10-1 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | A5-17-2 (Q-12)
A807(A5-10-2) | O | ON | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | A5-17-3 (Q-13)
A5-10-3 (A806 - 1) | O | ON |  | 3.7772 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | A5-17-4 (Q-14)
A5-10-4 (A806 - 2) | O | ON |  |  | 3.8393 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | A5-17-5 (Q-15)
A5-10-5 (Y-14) | O | ON | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | A5-17-6 (Q-16)
A5-10-6 (Y-13) | O | ON |  | 1.5458 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | A5-17-7 (Q-17)
A5-10-7 (Y-12) | O | ON |  |  | 1.1197 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | A5-17-8 (Q-18)
A5-10-8 (Y-11) | O | ON | 0.68 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | A5-17-9 (Q-19)
A5-14-1 (U-10) | O | ON |  | 3.4826 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | A5-18-1 (P-11)
A5-14-2 (U-11) | O | ON |  |  | 2.0972 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A5-18-2 (P-12)
A5-14-3 (U-12) | O | ON | 1.4414 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | A5-18-3 (P-13)
A5-14-4 (U-13) | O | ON |  | 5.7522 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | A5-18-4 (P-14)
A5-14-5 (U-14) | O | ON |  |  | 5.0127 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | A5-18-5 (P-15)
6-1-A3-47 | O | ON | 3.5945 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | ON | A5-16-3 (R-13)
A5-14-7 (U-16) | O | ON |  | 8.1769 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | ON | A5-4-9 (AC-11)
6-1-A3-51 | O | ON |  |  | 3.594 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | A5-6-7
6-1-A3-53 | O | ON | 4.3507 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 4.2693 |  |  |  | O | ON | A5-15-5(2) (T-15)
[10 empty] | 총합: | 19.2294 | 43.9951 | 28.9673
6-DaHall 1-PDU-06 |  | PDU : SEL1 - 6-1 - B3 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 12.5 | 37.1 | 24.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B5-8-7 (W-12) | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 10.4239 |  |  | O | ON | B5-15-1 (T-11)
B5-8-8 (W-11) | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 4.0793 |  | O | ON | B5-15-2 (T-12)
B5-9-1 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0.69123 |  |  |  | O | ON | B5-15-3 (T-13)
B5-9-2 | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 3.4827 |  |  | O | ON | B5-15-4 (T-14)
B5-9-3 | O | ON |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0.54039 |  | O | ON | B5-15-5 (T-15)
B5-9-4 (X-15) | O | ON | 1.9057 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | B5-15-6 (T-16)
B5-9-5 (X-14) | O | ON |  | 3.5289 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 3.2451 |  |  | O | ON | B5-15-7 (T-17)
B5-9-6 (X-13) | O | ON |  |  | 3.177 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 4.0675 |  | O | ON | B5-15-8 (T-18)
B5-9-7 (X-12) | O | ON | 0.91132 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | B5-15-9
B5-9-8 (X-11) | O | ON |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | ON | B5-17-1 (Q-11)
B5-10-1 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | B5-17-2 (Q-12)
A807(B5-10-2) | O | ON | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | B5-17-3 (Q-13)
B5-10-3 (A806 - 1) | O | ON |  | 4.4484 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | B5-17-4 (Q-14)
B5-10-4 (A806 - 2) | O | ON |  |  | 3.1651 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | B5-17-5 (Q-15)
B5-10-5 (Y-14) | O | ON | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | B5-17-6 (Q-16)
B5-10-6 (Y-13) | O | ON |  | 0.38038 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | B5-17-7 (Q-17)
B5-10-7 (Y-12) | O | ON |  |  | 1.18 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | B5-17-8 (Q-18)
B5-10-8 (Y-11) | O | ON | 0.39 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | B5-17-9 (Q-19)
A5-14-1 (U-10) | O | ON |  | 3.5799 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | B5-18-1 (P-11)
A5-14-2 (U-11) | O | ON |  |  | 1.9107 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | B5-18-2 (P-12)
A5-14-3 (U-12) | O | ON | 0.81301 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | B5-18-3 (P-13)
A5-14-4 (U-13) | O | ON |  | 4.891 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | B5-18-4 (P-14)
A5-14-5 (U-14) | O | ON |  |  | 5.1112 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | B5-18-5 (P-15)
6-1-B3-47 | O | ON | 3.2764 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | ON | B5-16-3 (R-13)
A5-14-7 (U-16) | O | ON |  | 1.341 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | ON | B5-4-9 (AC-11)
6-1-B3-51 | O | ON |  |  | 4.159 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | B5-6-7
6-1-B3-53 | O | ON | 0.59047 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 2.4015 |  |  |  | O | ON | B5-15-5(2) (T-15)
[10 empty] | 총합: | 10.9795 | 35.3212 | 27.3902
6-DaHall 1-PDU-07 |  | PDU : SEL1 - 6-1 - A4 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
#A6-4-4 | O | OFF |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | A6-4-1
#A6-4-7 | O | OFF |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | A6-4-2
#A6-5-4 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | A6-4-3
#A6-5-7 | O | OFF |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | ON | A6-4-4 (AC-16)
#A6-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | ON | A6-4-5 (AC-15)
#A6-6-6 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | A6-4-6 (AC-14)
#A6-7-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | ON | A6-4-7 (AC-13)
#A6-7-6 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | A6-5-1
#A6-8-3 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | A6-5-2
#A6-8-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | A6-5-3
#A6-9-3 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | A6-5-4 (AB-16)
#A6-9-6 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | A6-5-5 (AB-15)
#A6-10-3 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | A6-5-6 (AB-14)
#A6-10-6 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | A6-5-7 (AB-13)
#A6-14-4 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | OFF | A6-2-1
#A6-14-7 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | OFF | A6-2-2
#A6-15-4 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | OFF | A6-2-3
#A6-15-7 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | A6-2-4 (AE-16)
#A6-17-4 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | A6-2-5 (AE-15)
#A6-17-7 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A6-2-6 (AE-14)
A6-8-8(1) | O | ON | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | A6-2-7 (AE-13)
A6-8-7(1) | O | ON |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | A6-2-8 (AE-12)
A6-8-6(1) | O | ON |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | A6-2-9 (AE-11)
불량 | X | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | A6-3-1
A6-3-7 (AD-13) | O | ON |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | A6-3-2
A6-3-6 (AD-14) | O | ON |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | A6-3-3
A6-3-5 (AD-15) | O | ON | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | ON | A6-3-4 (AD-16)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-08 |  | PDU : SEL1 - 6-1 - B4 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
#B6-28-3 | X | OFF |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | B6-4-1
#B6-28-6 | X | OFF |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | B6-4-2
#B6-29-3 | X | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | B6-4-3
#B6-29-6 | X | OFF |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | ON | B6-4-4 (AC-16)
#B6-30-3 | X | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | ON | B6-4-5 (AC-15)
#B6-30-6 | X | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | B6-4-6 (AC-14)
#B6-31-3 | X | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | ON | B6-4-7 (AC-13)
#B6-31-6 | X | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | B6-5-1
#B6-32-3 | X | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | B6-5-2
#B6-32-6 | X | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | B6-5-3
#B6-33-3 | X | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | B6-5-4 (AB-16)
#B6-33-6 | X | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | B6-5-5 (AB-15)
| X | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | B6-5-6 (AB-14)
| X | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | B6-5-7 (AB-13)
| X | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | OFF | B6-2-1
| X | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | OFF | B6-2-2
| X | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | OFF | B6-2-3
| X | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | B6-2-4 (AE-16)
| X | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | B6-2-5 (AE-15)
| X | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | B6-2-6 (AE-14)
| X | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | B6-2-7 (AE-13)
B6-8-8(1) | O | ON |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | B6-2-8 (AE-12)
B6-8-7(1) | O | ON |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | B6-2-9 (AE-11)
B6-8-6(1) | O | ON | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | B6-3-1
B6-3-7 (AD-13) | O | ON |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | B6-3-2
B6-3-6 (AD-14) | O | ON |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | B6-3-3
B6-3-5 (AD-15) | O | ON | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | ON | B6-3-4 (AD-16)
[10 empty] | 총합: | 0 | 0 | 0
| IDC | 357.8141

## 5층_부하량(월간_MIN)
Date : 2024-01-01 ~ 2024-01-31
5-DaHall 1-CEP-05 | [8 empty] | Main CB 4P 350A
[12 empty] | MAIN 계측값 : | 62.2 | 67 | 61.8 | <- 실측값 |  |  | -1
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
5-DaHall 1-CRAC-16 보조 5F-2호기(구글) | O | ON | 0 | 0 | 0 |  | 4P 50A | #01 | . | . | #02 | 4P 50A | 0 | 0 | 0 |  | O | ON | 5-DaHall 1-CRAC-15 보조 5F-1호기(구글)
5-DaHall 1-CRAC-01 LG CRAC #01 | O | ON | 0 | 0 | 0 |  | 4P 50A | #03 | . | . | #04 | 4P 50A | 0 | 0 | 0 |  | O | ON | 5-DaHall 1-CRAC-02 LG CRAC #02
5-DaHall 1-CRAC-03 LG CRAC #03 | O | ON | 0 | 0 | 0 |  | 4P 50A | #05 | . | . | #06 | 4P 50A | 0 | 0 | 0 |  | O | ON | 5-DaHall 1-CRAC-04 LG CRAC #04
5-DaHall 1-CRAC-05 LG CRAC #05 | O | ON | 0 | 0 | 0 |  | 4P 50A | #07 | . | . | #08 | 4P 50A | 0 | 0 | 0 |  | O | ON | 5-DaHall 1-CRAC-06 LG CRAC #06
5-DaHall 1-CRAC-07 LG CRAC #07 | O | ON | 0 | 0 | 0 |  | 4P 50A | #09 | . | . | #10 | 4P 50A | 0 | 0 | 0 |  | O | ON | 5-DaHall 1-CRAC-08 LG CRAC #08
5-DaHall 1-CRAC-09 LG CRAC #09 | O | ON | 0 | 0 | 0 |  | 4P 50A | #11 | . | . | #12 | 4P 50A | 0 | 0 | 0 |  | O | ON | 5-DaHall 1-CRAC-13 CF CRAC #01
spare | X | OFF | 0 |  |  |  | 2P 30A | #13 | . | . | #14 | 2P 30A | 0 |  |  |  | X | OFF | spare
spare | X | OFF |  | 0 |  |  | 2P 30A | #15 | . | . | #16 | 2P 50A |  | 0 |  |  | O | ON | 5-DaHall 1-EH (5층 가습기 Main)
spare | X | OFF |  |  | 0 |  | 2P 30A | #17 | . | . | #18 | 2P 50A |  |  | 5.85 |  | O | ON | 4-DaHall 1-EH (4층 가습기 Main)
[12 empty] | 합계: | 0 | 0 | 5.85
5-DaHall 1-CEP-06 | [8 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 0.7 | 0 | 0.7 | <- 실측값
[10 empty] | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
[10 empty] | . | #01 | 4P 60A | 0.24 | 0 | 0.24 |  | O | ON | LG CRAC #10 (수냉식)
[10 empty] | . | #02 | 4P 60A | 0.24 | 0 | 0.24 |  | O | ON | LG CRAC #11 (수냉식)
[10 empty] | . | #03 | 4P 60A | 0.24 | 0 | 0.23 |  | O | ON | LG CRAC #12 (수냉식)
[10 empty] | . | #04 | 4P 60A | 0 | 0 | 0 |  | X | OFF | spare
[12 empty] | 합계: | 0.72 | 0 | 0.71
5-DaHall 1-PDU-01 |  | PDU : SEL1 - 5-1 - A1 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 34.6 | 37.8 | 27.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0.57 | 0.72 |  | O | ON | 보다폰정류기-A
1A-1-1 | O | ON | 0 |  |  |  | 2P 30A | #01 | CF상면 |  | #02 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-21 / 1A-2-11
1A-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | CF상면 | 구글202-A | #04 | 2P 30A |  | 0 |  |  | O | ON | 1A-2-12
1A-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | CF상면 | 구글201-A | #06 | 2P 30A |  |  | 1.52 |  | O | ON | 1A-2-13
1A-1-4 | O | OFF | 0 |  |  |  | 2P 30A | #07 | CF상면 |  | #08 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-24 / 1A-2-14
G1101 (1A-1-5) | O | ON |  | 9.36 |  |  | 2P 30A | #09 | cloudflare | 구글 시스템박스 | #10 | 2P 30A |  | 0 |  |  | O | ON | 1A-2-15
G1102 (1A-1-6) | O | ON |  |  | 7.99 |  | 2P 30A | #11 | cloudflare | 철거필요 | #12 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-1
G1103 (1A-1-7) | O | ON | 9.85 |  |  |  | 2P 30A | #13 | cloudflare | 철거필요 | #14 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-2
G1104 (1A-1-8) | O | ON |  | 0 |  |  | 2P 30A | #15 | cloudflare | 철거필요 | #16 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-3
G1105 (1A-1-9) | O | ON |  |  | 0 |  | 2P 30A | #17 | cloudflare | 철거필요 | #18 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-4
1A-1-10 | O | ON | 1.03 |  |  |  | 2P 30A | #19 | 구글104-A | 철거필요 | #20 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-5
1A-1-11 | O | ON |  | 1.38 |  |  | 2P 30A | #21 | 구글103-A | 철거필요 | #22 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-6
1A-1-12 | O | ON |  |  | 1.48 |  | 2P 30A | #23 | 구글102-A | 철거필요 | #24 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-7
1A-1-13 | O | ON | 0 |  |  |  | 2P 30A | #25 | 구글101-A | 철거필요 | #26 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-8
1A-1-14 | O | OFF |  | 0 |  |  | 2P 30A | #27 |  | 철거필요 | #28 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-9
1A-1-15 | O | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | O | OFF | 5F-P-20 / 1A-3-10
G1201 (1A-2-1) | O | ON | 8.93 |  |  |  | 2P 30A | #31 | cloudflare |  | #32 | 2P 30A | 0 |  |  |  | O | OFF | 5F-P-21 / 1A-3-11
G1202 (1A-2-2) | O | ON |  | 7.39 |  |  | 2P 30A | #33 | cloudflare |  | #34 | 2P 30A |  | 0 |  |  | O | OFF | 5F-P-22 / 1A-3-12
G1203 (1A-2-3) | O | ON |  |  | 8.93 |  | 2P 30A | #35 | cloudflare |  | #36 | 2P 30A |  |  | 0 |  | O | OFF | 5F-P-23 / 1A-3-13
G1204 (1A-2-4) | O | ON | 6.8 |  |  |  | 2P 30A | #37 | cloudflare |  | #38 | 2P 30A | 0 |  |  |  | O | OFF | 5F-P-24 / 1A-3-14
G1205 (1A-2-5) | O | ON |  | 8.81 |  |  | 2P 30A | #39 | cloudflare | ?? | #40 | 2P 30A |  | 0 |  |  | X | OFF
1A-2-6 | O | OFF |  |  | 0 |  | 2P 30A | #41 | CF상면 | 보다폰 케이지 안쪽 | #42 | 2P 30A |  |  | 0 |  | O | OFF | 1A-4-1
1A-2-7 | O | OFF | 0 |  |  |  | 2P 30A | #43 | CF상면 | 보다폰 케이지 안쪽 | #44 | 2P 30A | 0 |  |  |  | O | OFF | 1A-4-2
1A-2-8 | O | OFF |  | 0 |  |  | 2P 30A | #45 | CF상면 | 보다폰 케이지 안쪽 | #46 | 2P 30A |  | 0.61 |  |  | O | ON | 1A-4-3
1A-2-9 | O | OFF |  |  | 0 |  | 2P 30A | #47 | CF상면 | Vodafone | #48 | 2P 30A |  |  | 1.1 |  | O | ON | VF Rack#1-상
5F-Q-20 | O | OFF | 0 |  |  |  | 2P 30A | #49 |  | Vodafone | #50 | 2P 30A | 0 |  |  |  | O | ON | VF Rack#2-상
[12 empty] | 합계: | 26.61 | 28.12 | 21.74
5-DaHall 1-PDU-02 |  | PDU : SEL1 - 5-1 - B1 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 34.6 | 35.2 | 26.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0.65 | 0.72 |  | O | ON | 보다폰정류기-B
1B-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | CF상면 |  | #02 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-21 / 1B-2-11
1B-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | CF상면 | 구글202-A | #04 | 2P 30A |  | 0 |  |  | O | ON | 1B-2-12
1B-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | CF상면 | 구글201-A | #06 | 2P 30A |  |  | 1.25 |  | O | ON | 1B-2-13
1B-1-4 | O | OFF | 0 |  |  |  | 2P 30A | #07 | CF상면 |  | #08 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-24 / 1B-2-14
G1101 (1B-1-5) | O | ON |  | 7.84 |  |  | 2P 30A | #09 | cloudflare | 구글Cage 지문인식기 | #10 | 2P 30A |  | 0 |  |  | O | ON | 1B-2-15
G1102 (1B-1-6) | O | ON |  |  | 9.25 |  | 2P 30A | #11 | cloudflare |  | #12 | 2P 30A |  |  | 0 |  | O | OFF | 1B-3-1
G1103 (1B-1-7) | O | ON | 7.97 |  |  |  | 2P 30A | #13 | cloudflare |  | #14 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-2
G1104 (1B-1-8) | O | ON |  | 0 |  |  | 2P 30A | #15 | cloudflare |  | #16 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-3
G1105 (1B-1-9) | O | ON |  |  | 0 |  | 2P 30A | #17 | cloudflare |  | #18 | 2P 30A |  |  | 0 |  | O | ON | 1B-3-4
1B-1-10 | O | ON | 0 |  |  |  | 2P 30A | #19 | 구글104-A |  | #20 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-5
1B-1-11 | O | ON |  | 1.53 |  |  | 2P 30A | #21 | 구글103-A |  | #22 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-6
1B-1-12 | O | ON |  |  | 1.26 |  | 2P 30A | #23 | 구글102-A |  | #24 | 2P 30A |  |  | 0 |  | O | ON | 1B-3-7
1B-1-13 | O | ON | 0 |  |  |  | 2P 30A | #25 | 구글101-A |  | #26 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-8
1B-1-14 | O | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-9
1B-1-15 | O | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | O | ON | 5F-P-20 / 1B-3-10
G1201 (1A-2-1) | O | ON | 9.59 |  |  |  | 2P 30A | #31 | cloudflare |  | #32 | 2P 30A | 0 |  |  |  | O | ON | 5F-P-21 / 1B-3-11
G1202 (1B-2-2) | O | ON |  | 8.63 |  |  | 2P 30A | #33 | cloudflare |  | #34 | 2P 30A |  | 0 |  |  | O | ON | 5F-P-22 / 1B-3-12
G1203 (1B-2-3) | O | ON |  |  | 7.25 |  | 2P 30A | #35 | cloudflare |  | #36 | 2P 30A |  |  | 0 |  | O | ON | 5F-P-23 / 1B-3-13
G1204 (1B-2-4) | O | ON | 7.7 |  |  |  | 2P 30A | #37 | cloudflare |  | #38 | 2P 30A | 0 |  |  |  | O | ON | 5F-P-24 / 1B-3-14
G1205 (1B-2-5) | O | ON |  | 6.93 |  |  | 2P 30A | #39 | cloudflare |  | #40 | 2P 30A |  | 0 |  |  | O | OFF | 5F-P-25 / 1B-3-15
1B-2-6 | O | OFF |  |  | 0 |  | 2P 30A | #41 | CF상면 | ?? | #42 | 2P 30A |  |  | 0 |  | O | OFF | 1B-7-1(2)
1B-2-7 | O | OFF | 0 |  |  |  | 2P 30A | #43 | CF상면 |  | #44 | 2P 30A | 0 |  |  |  | O | OFF | 1B-4-2
1B-2-8 | O | OFF |  | 0 |  |  | 2P 30A | #45 | CF상면 | 보다폰 케이지 안쪽 | #46 | 2P 30A |  | 0.61 |  |  | O | ON | 1B-4-3
1B-2-9 | O | OFF |  |  | 0 |  | 2P 30A | #47 | CF상면 | Vodafone | #48 | 2P 30A |  |  | 0.53 |  | O | ON | VF Rack#1-하
5F-Q-20 | O | OFF | 0 |  |  |  | 2P 30A | #49 |  | Vodafone | #50 | 2P 30A | 0 |  |  |  | O | ON | VF Rack#2-하
[12 empty] | 합계: | 25.26 | 26.19 | 20.26
5-DaHall 1-PDU-03 |  | PDU : SEL1 - 5-1 - A2 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 26.8 | 15.9 | 18 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0 | 0 |  | X | OFF
5F-O-16 / 2A-4-6 | O | ON | 0 |  |  |  | 2P 30A | #01 |  | KG이니시스 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B221 (R13)-1
5F-O-17 / 2A-4-7 | O | ON |  | 0 |  |  | 2P 30A | #03 |  | KG이니시스 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B221 (R13)-2
5F-O-18 | O | ON |  |  | 0 |  | 2P 30A | #05 |  | KG이니시스 | #06 | 2P 30A |  |  | 0.53 |  | O | ON | B222 (R14)-1
5F-O-19 | O | ON | 0 |  |  |  | 2P 30A | #07 |  | KG이니시스 | #08 | 2P 30A | 1.27 |  |  |  | O | ON | B222 (R14)-2
5F-O-20 | O | ON |  | 0 |  |  | 2P 30A | #09 |  | KG이니시스 | #10 | 2P 30A |  | 2.05 |  |  | O | ON | B316 (R15)-1
5F-O-21 | O | ON |  |  | 0 |  | 2P 30A | #11 |  | KG이니시스 | #12 | 2P 30A |  |  | 1.73 |  | O | ON | B316 (R15)-2
5F-O-22 | O | ON | 0 |  |  |  | 2P 30A | #13 |  | KG이니시스 | #14 | 2P 30A | 0.34 |  |  |  | O | ON | B317 (R16)-1
5F-O-23 | O | ON |  | 0 |  |  | 2P 30A | #15 |  | KG이니시스 | #16 | 2P 30A |  | 3.74 |  |  | O | ON | B318 (R17)-1
5F-O-24 | O | ON |  |  | 0 |  | 2P 30A | #17 |  | KG이니시스 | #18 | 2P 30A |  |  | 0.84 |  | O | ON | B319 (R18)
2A-7-2(2) | X | OFF | 0 |  |  |  | 2P 30A | #19 | ?? | KG이니시스 | #20 | 2P 30A | 2.73 |  |  |  | O | ON | B320 (R19)
2A-5-1 | O | OFF |  | 0 |  |  | 2P 30A | #21 | 보다폰상면 | KG이니시스 | #22 | 2P 30A |  | 2.75 |  |  | O | ON | B321 (R20)
2A-5-2 | O | ON |  |  | 0 |  | 2P 30A | #23 | 보다폰상면 | KG이니시스 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B322 (R21)
2A-5-3 | O | ON | 0 |  |  |  | 2P 30A | #25 | 보다폰상면 | KG이니시스 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B416 (R22)
2A-5-4 | O | ON |  | 0 |  |  | 2P 30A | #27 | 보다폰상면 | KG이니시스 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B417 (R23)
2A-5-5 | O | ON |  |  | 0 |  | 2P 30A | #29 |  | KG이니시스 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B418 (R24)
5-1-A2-31 | X | OFF | 0 |  |  |  | 2P 30A | #31 |  | KG이니시스 | #32 | 2P 30A | 2.46 |  |  |  | O | ON | B116 (R12)
5-1-A2-33 | X | OFF |  | 0 |  |  | 2P 30A | #33 |  | KG이니시스 | #34 | 2P 30A |  | 2.14 |  |  | O | ON | B117 (R11)
5-1-A2-35 | X | OFF |  |  | 0 |  | 2P 30A | #35 |  | KG이니시스 | #36 | 2P 30A |  |  | 2.15 |  | O | ON | B118 (R10)
B317 (R16)-2 | O | ON | 2.59 |  |  |  | 2P 30A | #37 | KG이니시스 | KG이니시스 | #38 | 2P 30A | 2.32 |  |  |  | O | ON | B119 (R9)
B318 (R17)-2 | O | ON |  | 1.66 |  |  | 2P 30A | #39 | KG이니시스 | KG이니시스 | #40 | 2P 30A |  | 1.35 |  |  | O | ON | B120 (R8)
B221 (R13)-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | KG이니시스 | KG이니시스 | #42 | 2P 30A |  |  | 1.77 |  | O | ON | B121 (R7)
B222 (R14)-3 | O | ON | 2.18 |  |  |  | 2P 30A | #43 | KG이니시스 | KG이니시스 | #44 | 2P 30A | 2.83 |  |  |  | O | ON | B122 (R6)
B316 (R15)-3 | O | ON |  | 0 |  |  | 2P 30A | #45 | KG이니시스 | KG이니시스 | #46 | 2P 30A |  | 2.82 |  |  | O | ON | B216 (R5)
B219 (R2) | O | ON |  |  | 3.95 |  | 2P 30A | #47 | KG이니시스 | KG이니시스 | #48 | 2P 30A |  |  | 3.39 |  | O | ON | B217 (R4)
B220 (R1) | O | ON | 5.59 |  |  |  | 2P 30A | #49 | KG이니시스 | KG이니시스 | #50 | 2P 30A | 3.81 |  |  |  | O | ON | B218 (R3)
[12 empty] | 합계: | 26.12 | 16.51 | 14.36
5-DaHall 1-PDU-04 |  | PDU : SEL1 - 5-1 - B2 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 25.1 | 15.5 | 18.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| O | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0 | 0 |  | O | OFF
5F-O-16 / 2B-4-6 | O | ON | 0 |  |  |  | 2P 30A | #01 | 철거가능 | KG이니시스 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B221 (R13)-1
5F-O-17 / 2B-4-7 | O | ON |  | 0 |  |  | 2P 30A | #03 | 철거가능 | KG이니시스 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B221 (R13)-2
5F-O-18 | O | ON |  |  | 0 |  | 2P 30A | #05 | 철거가능 | KG이니시스 | #06 | 2P 30A |  |  | 0.53 |  | O | ON | B222 (R14)-1
5F-O-19 | O | ON | 0 |  |  |  | 2P 30A | #07 | 철거가능 | KG이니시스 | #08 | 2P 30A | 1.57 |  |  |  | O | ON | B222 (R14)-2
5F-O-20 | O | ON |  | 0 |  |  | 2P 30A | #09 | 철거가능 | KG이니시스 | #10 | 2P 30A |  | 1.94 |  |  | O | ON | B316 (R15)-1
5F-O-21 | O | ON |  |  | 0 |  | 2P 30A | #11 | 철거가능 | KG이니시스 | #12 | 2P 30A |  |  | 1.78 |  | O | ON | B316 (R15)-2
5F-O-22 | O | ON | 0 |  |  |  | 2P 30A | #13 | 철거가능 | KG이니시스 | #14 | 2P 30A | 0.4 |  |  |  | O | ON | B317 (R16)-1
5F-O-23 | O | ON |  | 0 |  |  | 2P 30A | #15 | 철거가능 | KG이니시스 | #16 | 2P 30A |  | 3.67 |  |  | O | ON | B318 (R17)-1
5F-O-24 | O | ON |  |  | 0 |  | 2P 30A | #17 | 철거가능 | KG이니시스 | #18 | 2P 30A |  |  | 0.85 |  | O | ON | B319 (R18)
2B-7-2(2) | O | OFF | 0 |  |  |  | 2P 30A | #19 | ?? | KG이니시스 | #20 | 2P 30A | 1.78 |  |  |  | O | ON | B320 (R19)
2B-5-1 | O | OFF |  | 0 |  |  | 2P 30A | #21 | 보다폰상면 | KG이니시스 | #22 | 2P 30A |  | 2.99 |  |  | O | ON | B321 (R20)
2B-5-2 | O | ON |  |  | 0 |  | 2P 30A | #23 | 보다폰상면 | KG이니시스 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B322 (R21)
2B-5-3 | O | ON | 0 |  |  |  | 2P 30A | #25 | 보다폰상면 | KG이니시스 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B416 (R22)
2B-5-4 | O | ON |  | 0 |  |  | 2P 30A | #27 | 보다폰상면 | KG이니시스 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B417 (R23)
2B-5-5 | O | ON |  |  | 0 |  | 2P 30A | #29 | 철거필요 | KG이니시스 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B418 (R24)
| X | OFF | 0 |  |  |  | 2P 30A | #31 | 철거필요 | KG이니시스 | #32 | 2P 30A | 0.26 |  |  |  | O | ON | B116 (R12)
| X | OFF |  | 0 |  |  | 2P 30A | #33 | 철거필요 | KG이니시스 | #34 | 2P 30A |  | 0.28 |  |  | O | ON | B117 (R11)
| X | OFF |  |  | 0 |  | 2P 30A | #35 | 철거가능 | KG이니시스 | #36 | 2P 30A |  |  | 2.27 |  | O | ON | B118 (R10)
B317 (R16)-2 | O | ON | 3.21 |  |  |  | 2P 30A | #37 | KG이니시스 | KG이니시스 | #38 | 2P 30A | 2.46 |  |  |  | O | ON | B119 (R9)
B318 (R17)-2 | O | ON |  | 1.1 |  |  | 2P 30A | #39 | KG이니시스 | KG이니시스 | #40 | 2P 30A |  | 1.43 |  |  | O | ON | B120 (R8)
B221 (R13)-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | KG이니시스 | KG이니시스 | #42 | 2P 30A |  |  | 1.57 |  | O | ON | B121 (R7)
B222 (R14)-3 | O | ON | 2.27 |  |  |  | 2P 30A | #43 | KG이니시스 | KG이니시스 | #44 | 2P 30A | 2.25 |  |  |  | O | ON | B122 (R6)
B316 (R15)-3 | O | ON |  | 0 |  |  | 2P 30A | #45 | KG이니시스 | KG이니시스 | #46 | 2P 30A |  | 2.29 |  |  | O | ON | B216 (R5)
B219 (R2) | O | ON |  |  | 4.29 |  | 2P 30A | #47 | KG이니시스 | KG이니시스 | #48 | 2P 30A |  |  | 2.94 |  | O | ON | B217 (R4)
B220 (R1) | O | ON | 5.3 |  |  |  | 2P 30A | #49 | KG이니시스 | KG이니시스 | #50 | 2P 30A | 3.62 |  |  |  | O | ON | B218 (R3)
[12 empty] | 합계: | 23.12 | 13.7 | 14.23
PDU6B-1T |  | PDU : | [6 empty] | Main CB 4P 150A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A |  |  |  |  | X | OFF
1T-1-3 | O | OFF |  |  |  |  | 3P 30A | #03 | CF상면 | . | #04 | 3P 30A |  |  |  |  | O | OFF | 1T-4-3
1T-1-6 | O | OFF |  |  |  |  | 3P 30A | #05 | CF상면 | . | #06 | 3P 30A |  |  |  |  | O | OFF | 1T-4-6
1T-1A9 | O | OFF |  |  |  |  | 3P 30A | #07 | . | . | #08 | 3P 30A |  |  |  |  | O | OFF | 1T-4-9
1T-1-12 | O | OFF |  |  |  |  | 3P 30A | #09 | Google상면 | . | #10 | 3P 30A |  |  |  |  | O | OFF | 1T-4-12
1T-2-3 | O | OFF |  |  |  |  | 3P 30A | #11 | CF상면 | . | #12 | 3P 20A |  |  |  |  | O | OFF | 1T-5-3
1T-2-6 | O | OFF |  |  |  |  | 3P 20A | #13 | . | . | #14 | 3P 20A |  |  |  |  | O | OFF | 1T-5-6
1T-2-9 | O | OFF |  |  |  |  | 3P 20A | #15 | . | . | #16 | 3P 20A |  |  |  |  | O | OFF | 1T-5-9
1T-2-12 | O | OFF |  |  |  |  | 3P 20A | #17 | Google상면 | . | #18 | 3P 20A |  |  |  |  | O | OFF | 1T-5-12
1T-3-3 | O | OFF |  |  |  |  | 3P 20A | #19 | . | . | #20 | 3P 20A |  |  |  |  | O | OFF | 1T-6-2
1T-3-6 | O | OFF |  |  |  |  | 3P 20A | #21 | . | . | #22 | 3P 20A |  |  |  |  | O | OFF | 1T-6-4
1T-3-9 | O | OFF |  |  |  |  | 3P 20A | #23 | . | . | #24 | 3P 20A |  |  |  |  | X | OFF
1T-3-12 | O | OFF |  |  |  |  | 3P 20A | #25 | . | . | #26 | 3P 20A |  |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-05 |  | PDU : SEL1 - 5-1 - A3 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  | 0 |  | 2P 30A | #01 |  |  | #02 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #03 |  |  | #04 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #13 |  |  | #14 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #19 |  |  | #20 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-2
| X | OFF |  | 0 |  |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-3
| X | OFF |  |  | 0 |  | 2P 30A | #25 |  |  | #26 | 2P 30A |  |  | 0 |  | O | OFF | 3A-12-3T
| X | OFF | 0 |  |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-4
| X | OFF |  | 0 |  |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-5
| X | OFF |  |  | 0 |  | 2P 30A | #31 |  |  | #32 | 2P 30A |  |  | 0 |  | O | OFF | 3A-12-6
| X | OFF | 0 |  |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-7
| X | OFF |  | 0 |  |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-8
| X | OFF |  |  | 0 |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #43 |  |  | #44 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-06 |  | PDU : SEL1 - 5-1 - B3 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  | 0 |  | 2P 30A | #01 |  |  | #02 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #03 |  |  | #04 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #13 |  |  | #14 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #19 |  |  | #20 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A | 0 |  |  |  | O | OFF | 3B-12-2
| X | OFF |  | 0 |  |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  | 0 |  |  | O | OFF | 3B-12-3
| X | OFF |  |  | 0 |  | 2P 30A | #25 |  |  | #26 | 2P 30A |  |  | 0 |  | O | OFF | 3B-12-4
| X | OFF | 0 |  |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A | 0 |  |  |  | O | OFF | 3B-12-5
| X | OFF |  | 0 |  |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  | 0 |  |  | O | OFF | 3B-12-6
| X | OFF |  |  | 0 |  | 2P 30A | #31 |  |  | #32 | 2P 30A |  |  | 0 |  | O | OFF | 3B-12-6T
| X | OFF | 0 |  |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A | 0 |  |  |  | O | OFF | 3B-12-7
| X | OFF |  | 0 |  |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  | 0 |  |  | O | OFF | 3B-12-8
| X | OFF |  |  | 0 |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #43 |  |  | #44 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-07 |  | PDU : SEL1 - 5-1 - A4 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 8.6 | 1.1 | 0.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
9A-1-5 (PCCW) /5F-A-14 | O | ON | 7.64 |  |  |  | 3P 30A | #01 | PCCW | 센츄리링크코리아 | #02 | 3P 30A | 0.99 |  |  |  | O | ON | 9A-1-8 / 5F-A-17
9A-1-6 / 5F-A-15 | O | ON |  | 1.19 |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A |  | 0 |  |  | O | ON | 9A-1-9 / 5F-A-18
9A-1-7 / 5F-A-16 | O | ON |  |  | 0.4 |  | 3P 30A | #05 | PCCW | 세종 인터넷(IES.YSM.S51) | #06 | 3P 30A |  |  | 0.34 |  | O | ON | 9A-1-10 / 5F-A-19
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #09 |  |  | #10 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 8.63 | 1.19 | 0.74
5-DaHall 1-PDU-09 |  | PDU : SEL1 - 5-1 - A5 | [6 empty] | Main CB 4P 200A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #03 |  |  | #04 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #09 |  |  | #10 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #37 |  |  | #38 | 3P 20A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-08 |  | PDU : SEL1 - 5-1 - B4 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 6.5 | 1.4 | 1.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01 | 코로케션 | 센츄리링크코리아 | #02 | 3P 30A | 1.13 |  |  |  | O | ON | 9B-1-8 / 5F-A-17
9B-1-6 / 5F-A-15 | O | ON |  | 1.26 |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A |  | 0 |  |  | O | ON | 9B-1-9 / 5F-A-18
9B-1-7 / 5F-A-16 | O | ON |  |  | 0 |  | 3P 30A | #05 | PCCW | 세종 인터넷(IES.YSM.S51) | #06 | 3P 30A |  |  | 1.33 |  | O | ON | 9B-1-10 / 5F-A-19
9B-1-5 (PCCW)/5F-A-14 | O | ON | 5.28 |  |  |  | 3P 30A | #07 | PCCW |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #09 |  |  | #10 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| O | ON |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 6.41 | 1.26 | 1.33
5-DaHall 1-PDU-10 |  | PDU : SEL1 - 5-1 - B5 | [6 empty] | Main CB 4P 200A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #03 |  |  | #04 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #09 |  |  | #10 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #37 |  |  | #38 | 3P 20A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-11 |  | PDU : SEL1 - 5-1 - A6 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 15.3 | 10.2 | 9.9 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
1A-1-1 / 5F-A-10 | O | ON | 0 |  |  |  | 3P 30A | #03 | 코로케션 |  | #04 | 3P 30A | 0 |  |  |  | O | OFF | A1-3-2
1A-1-2 / 5F-A-11 | O | ON |  | 0 |  |  | 3P 30A | #05 | 코로케션 | 코로케션 | #06 | 3P 30A |  | 1.97 |  |  | O | ON | A1-3-3
1A-1-2(2) | O | ON |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 20A |  |  | 0 |  | O | ON | A1-3-4
1A-1-3 / 5F-A-12 | O | ON | 5.19 |  |  |  | 3P 30A | #09 | PCCW | 코로케션 | #10 | 3P 20A | 0 |  |  |  | O | ON | A1-3-5
1A-1-4 / 5F-A-13 | O | ON |  | 0 |  |  | 3P 30A | #11 | PCCW | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | A1-3-6
1A-1-4(2) / 5F-A-13 (2) | O | ON |  |  | 1.94 |  | 3P 30A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 0 |  | O | ON | A1-3-7
A1-2-1 / 5F-B-10 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 0 |  |  |  | O | ON | A1-3-8
A1-2-2 / 5F-B-11 | O | ON |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 2.39 |  |  | O | ON | A1-3-9
A1-2-3 / 5F-B-12 | O | OFF |  |  | 0 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 2.88 |  | O | ON | A1-3-10
A1-2-4 / 5F-B-13 | O | ON | 2.48 |  |  |  | 3P 20A | #21 | 다코스 |  | #22 | 3P 20A | 0 |  |  |  | O | ON | A807 / 5F-D-16 / A1-4-7(2)
A1-2-5 / A605 (A) | O | ON |  | 4.82 |  |  | 3P 20A | #23 | 이비즈네트웍스 | PCCW | #24 | 3P 20A |  | 0 |  |  | O | ON | A1-5-10(2) / 5F-E-19
A1-2-6 / 5F-B-15 | O | ON |  |  | 0 |  | 3P 20A | #25 | 다코스 & NTT | PCCW | #26 | 3P 20A |  |  | 5.41 |  | O | ON | A1-1-3(2) / 5F-A-12(2)
A1-2-7 / 5F-B-16 | O | ON | 2.55 |  |  |  | 3P 20A | #27 | 제우스네트웍스 |  | #28 | 3P 20A | 5.27 |  |  |  | O | ON | A1-1-8(2) / 5F-A-17 (2)
A1-2-8 / 5F-B-17 | O | ON |  | 0 |  |  | 3P 20A | #29 | COLT |  | #30 | 3P 20A |  | 0 |  |  | O | ON | 5F-D-18 임시
A1-3-1 | O | OFF |  |  | 0 |  | 3P 20A | #31 |  | 코로케션 | #32 | 3P 20A |  |  | 0 |  | O | ON
[12 empty] | 합계: | 15.49 | 9.18 | 10.23
5-DaHall 1-PDU-13 |  | PDU : SEL1 - 5-1 - A7 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 12 | 18.7 | 14.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
A2-2-9 / 5F-B-18 | O | ON | 5.29 |  |  |  | 3P 30A | #03 | 코로케션 | 코로케션 | #04 | 3P 30A | 0 |  |  |  | O | ON | A2-5-4
A2-2-10 / 5F-B-19 | O | ON |  | 3.9 |  |  | 3P 30A | #05 | PCCW | 코로케션 | #06 | 3P 30A |  | 5.81 |  |  | O | ON | A2-5-5
A2-4-1 | O | ON |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 4.05 |  | O | ON | A2-5-6
A2-4-2 | O | ON | 0 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 30A | 0 |  |  |  | O | ON | A2-5-7
A2-4-3 | O | ON |  | 0 |  |  | 3P 20A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | A2-5-8
A2-4-4 | O | ON |  |  | 0.7 |  | 3P 20A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 0 |  | O | ON | A2-5-9
A2-4-5 / 5F-D-14 | O | ON | 0 |  |  |  | 3P 20A | #15 | PCCW | PCCW | #16 | 3P 20A | 3.83 |  |  |  | O | ON | A2-5-10 / 5F-E-19
A2-4-6 / 5F-D-15 | O | ON |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 0 |  |  | O | OFF | A2-6-1
A2-4-7 | O | ON |  |  | 5.1 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 0 |  | O | OFF | A2-6-2
A2-4-8 | O | ON | 3.16 |  |  |  | 3P 20A | #21 | 코로케션 | 코로케션 | #22 | 3P 20A | 0 |  |  |  | O | OFF | A2-6-3
A2-4-9 | O | ON |  | 8.64 |  |  | 3P 20A | #23 | 코로케션 | 코로케션 | #24 | 3P 20A |  | 0 |  |  | O | OFF | A2-6-4
A2-4-10 | O | ON |  |  | 2.46 |  | 3P 20A | #25 | 코로케션 | 코로케션 | #26 | 3P 20A |  |  | 1.79 |  | O | ON | A2-6-5 / F-14
A2-5-1 | O | ON | 0 |  |  |  | 3P 20A | #27 | 코로케션 | 코로케션 | #28 | 3P 20A | 0 |  |  |  | O | OFF | A2-6-6 / F-15
A2-5-2 | O | ON |  | 0 |  |  | 3P 20A | #29 | 코로케션 | 코로케션 | #30 | 3P 20A |  | 0 |  |  | O | OFF | A2-6-7 / F-16
A2-5-3 | O | ON |  |  | 0 |  | 3P 20A | #31 | 코로케션 | 코로케션 | #32 | 3P 20A |  |  | 0 |  | O | ON | A2-6-8 / F-17
[12 empty] | 합계: | 12.28 | 18.35 | 14.1
5-DaHall 1-PDU-15 |  | PDU : SEL1 - 5-1 - A8 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 19.1 | 6.2 | 14.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
AC PDU-3#A | O | ON | 5.97 | 1.24 | 7.84 |  | 3P 50A | #01(3상) | 텔스트라 | 텔스트라 | #02(3상) | 3P 50A | 3.36 | 2.77 | 1.94 |  | O | ON | TO:PDU(A)-3A
| X | OFF | 0 | 0 | 0 |  | 3P 50A | #03(3상) |  | Singtel-1 | #04(3상) | 3P 50A | 0 | 0 | 0 |  | X | OFF | DC정류기A
TRANSDUSER | O | OFF | 0 | 0 | 0 |  | 3P 30A | #05(3상) |  |  | #06(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF | customer con
PUD(A)-3-07 / 5F-B-17 (2) | O | ON | 3.76 |  |  |  | 3P 30A | #07 | COLT |  | #08 | 3P 30A | 4.29 |  |  |  | O | ON | A1007 / 5F-F-16
PUD(A)-3-09 / 5F-B-17 (3) | O | ON |  | 1.74 |  |  | 3P 30A | #09 | COLT |  | #10 | 3P 30A |  | 6.7 |  |  | O | OFF | A1006 / 5F-F-15
A603 / Colt, A-1 (23/08/23 On) | O | ON |  |  | 0 |  | 3P 30A | #11 |  | CMI | #12 | 3P 30A |  |  | 2.3 |  | O | ON | D-15랙(CMI)-A ('21.09.29 투입)
P여(A)-3 싱텔 SKB CWDM A전원 | O | ON | 0.59 |  |  |  | 3P 30A | #13 |  |  | #14 | 3P 30A | 1.56 |  |  |  | O | ON | A603 / Colt, 정류기A (23/08/23 On)
PUD(A)-2-15 | X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
PUD(A)-2-17 | X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
PUD(A)-2-19 | X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
PUD(A)-2-21 | X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
PUD(A)-2-23 | O | ON |  |  | 2.3 |  | 3P 20A | #23 | Singtel-2 |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
DACOM EOS | X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
PUD(A)-2-27 | X | OFF |  | 0 |  |  | 3P 20A | #27 |  | 다코스 & NTT | #28 | 3P 20A |  | 0.71 |  |  | O | ON | A3-2-6(2) / 5F-B-15 (2)
PUD(A)-2-29 | O | ON |  |  | 0.36 |  | 3P 20A | #29 | Singtel-2 |  | #30 | 3P 20A |  |  | 0 |  | X | OFF | TNSI A
[12 empty] | 합계: | 19.53 | 13.16 | 14.74
5-DaHall 1-PDU-12 |  | PDU : SEL1 - 5-1 - B6 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 20.1 | 13.1 | 14 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
1B-1-1 / 5F-A-10 | O | ON | 0 |  |  |  | 3P 30A | #03 | 코로케션 | 코로케션 | #04 | 3P 30A | 1.89 |  |  |  | O | ON | B1-3-3
1B-1-2 / 5F-A-11 | O | ON |  | 0 |  |  | 3P 30A | #05 | PCCW | 코로케션 | #06 | 3P 30A |  | 0 |  |  | O | ON | B1-3-4
| X | OFF |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 0 |  | O | ON | B1-3-5
1B-1-4 / 5F-A-13 | O | ON | 2.92 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 20A | 0 |  |  |  | O | ON | B1-3-6
1B-1-4(2) / 5F-A-13 (2) | O | ON |  | 0 |  |  | 3P 30A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | B1-3-7
B1-2-1 / 5F-B-10 | O | ON |  |  | 0 |  | 3P 20A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 0 |  | O | ON | B1-3-8
B1-2-2 / 5F-B-11 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 5.41 |  |  |  | O | ON | B1-3-9
B1-2-3 / 5F-B-12 | O | OFF |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 3.59 |  |  | O | ON | B1-3-10
B1-2-4 / 5F-B-13 | O | ON |  |  | 2.92 |  | 3P 20A | #19 | 다코스 |  | #20 | 3P 20A |  |  | 0 |  | X | OFF
B1-2-5 / A605 (B) | O | ON | 4.44 |  |  |  | 3P 20A | #21 | 이비즈네트웍스 |  | #22 | 3P 20A | 0 |  |  |  | X | OFF | A807 / 5F-D-16 / B1-4-7(2)
B1-2-6 / 5F-B-15 | O | ON |  | 0 |  |  | 3P 20A | #23 | 다코스 & NTT | PCCW | #24 | 3P 20A |  | 3.46 |  |  | O | ON | B1-5-10(2) / 5F-E-19
B1-2-7 / 5F-B-16 | O | ON |  |  | 3.3 |  | 3P 20A | #25 | 제우스네트웍스 | PCCW | #26 | 3P 20A |  |  | 4.96 |  | O | ON | 1B-1-3 / 5F-A-12
B1-2-8 / 5F-B-17 | O | ON | 0 |  |  |  | 3P 20A | #27 | COLT |  | #28 | 3P 20A | 5.66 |  |  |  | O | ON | B1-1-8(2) / 5F-A-17 (2)
B1-3-1 | O | ON |  | 0 |  |  | 3P 20A | #29 | 코로케션 | PCCW | #30 | 3P 20A |  | 6.46 |  |  | X | ON | B1-1-3(2) / 5F-A-12 (2)
B1-3-2 | O | OFF |  |  | 0 |  | 3P 20A | #31 | 코로케션 | 코로케션 | #32 | 3P 20A |  |  | 2.88 |  | O | ON | B1-2-9 / 5F-B-18
[12 empty] | 합계: | 20.32 | 13.51 | 14.06
5-DaHall 1-PDU-14 |  | PDU : SEL1 - 5-1 - B7 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 13.4 | 11.6 | 7.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
B2-2-10 / 5F-B-19 | O | ON | 1.39 |  |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A | 6.69 |  |  |  | O | ON | B2-5-5
B2-4-1 | O | ON |  | 0 |  |  | 3P 30A | #05 | 코로케션 | 코로케션 | #06 | 3P 30A |  | 2.75 |  |  | O | ON | B2-5-6
B2-4-2 | O | ON |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 0 |  | O | ON | B2-5-7
B2-4-3 | O | OFF | 0 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 30A | 0 |  |  |  | O | ON | B2-5-8
B2-4-4 | O | ON |  | 0 |  |  | 3P 20A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | B2-5-9
B2-4-5 / 5F-D-14 | O | ON |  |  | 1.72 |  | 3P 20A | #13 | PCCW | PCCW | #14 | 3P 20A |  |  | 3.17 |  | O | ON | B2-5-10 / 5F-E-19
B2-4-6 / 5F-D-15 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 0 |  |  |  | O | OFF | B2-6-1
B2-4-7 | O | ON |  | 0.94 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 0 |  |  | O | OFF | B2-6-2
B2-4-8 | O | ON |  |  | 2.18 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 0 |  | O | OFF | B2-6-3
B2-4-9 | O | ON | 3.34 |  |  |  | 3P 20A | #21 | 코로케션 | 코로케션 | #22 | 3P 20A | 0 |  |  |  | O | OFF | B2-6-4
B2-4-10 | O | ON |  | 2.51 |  |  | 3P 20A | #23 | 코로케션 | 코로케션 | #24 | 3P 20A |  | 4.1 |  |  | O | ON | B2-6-5 / F-14
B2-5-1 | O | ON |  |  | 0 |  | 3P 20A | #25 | 코로케션 | 코로케션 | #26 | 3P 20A |  |  | 0 |  | O | OFF | B2-6-6 / F-15
B2-5-2 | O | ON | 0 |  |  |  | 3P 20A | #27 | 코로케션 | 코로케션 | #28 | 3P 20A | 0 |  |  |  | O | OFF | B2-6-7 / F-16
B2-5-3 | O | ON |  | 0 |  |  | 3P 20A | #29 | 코로케션 | 코로케션 | #30 | 3P 20A |  | 0 |  |  | O | ON | B2-6-8 / F-17
B2-5-4 | O | ON |  |  | 0 |  | 3P 20A | #31 | 코로케션 |  | #32 | 3P 20A |  |  | 0 |  | O | ON | FMS 5층 메인전원
[12 empty] | 합계: | 11.42 | 10.3 | 7.07
5-DaHall 1-PDU-16 |  | PDU : SEL1 - 5-1 - B8 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 20.1 | 11.1 | 16 | <- 실측값 |  |  | <- 디스플래이값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
AC PDU-3#B | O | ON | 4.67 | 1.33 | 6.03 |  | 3P 50A | #01(3상) | 텔스트라 | 텔스트라 | #02(3상) | 3P 50A | 3.12 | 3.12 | 1.85 |  | O | ON | TO:PDU(B)-3A
| X | OFF | 0 | 0 | 0 |  | 3P 50A | #03(3상) |  | Singtel-1 | #04(3상) | 3P 50A | 0 | 0 | 0 |  | X | OFF | DC정류기B
TRANSDUSER | X | OFF | 0 | 0 | 0 |  | 3P 30A | #05(3상) |  |  | #06(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF | customer con
PUD(B)-3-07 / 5F-B-17 (2) | O | ON | 3.95 |  |  |  | 3P 30A | #07 | COLT |  | #08 | 3P 30A | 4.86 |  |  |  | O | ON | A1007 / 5F-F-16
PUD(B)-3-09 / 5F-B-17 (3) | O | ON |  | 1.79 |  |  | 3P 30A | #09 | COLT |  | #10 | 3P 30A |  | 0.99 |  |  | X | OFF | A1006 / 5F-F-15
A603 / Colt, B-1 (23/08/23 On) | O | ON |  |  | 0 |  | 3P 30A | #11 |  | CMI | #12 | 3P 30A |  |  | 2.55 |  | O | ON | D-15랙(CMI)-B ('21.09.29 투입)
P여(B)-3 싱텔 SKB CWDM B전원 | O | ON | 1.65 |  |  |  | 3P 30A | #13 |  |  | #14 | 3P 30A | 1.71 |  |  |  | O | ON | A603 / Colt, 정류기B (23/08/23 On)
KT Rack #2 (소형 임시정류기) | O | ON |  | 0.42 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
KT Rack #3 (소형 임시정류기) | O | ON |  |  | 0.39 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
KT Rack #4 (소형 임시정류기) | O | ON | 0 |  |  |  | 3P 20A | #19 |  | 4F BMS | #20 | 3P 20A | 0.59 |  |  |  | O | ON | 신규 BMS(4F TPS실) Rack
텔스트라 CCTV 모니터링PC 및 시스템 박스 | O | ON |  | 0.27 |  |  | 3P 20A | #21 |  | 5F BMS | #22 | 3P 20A |  | 0.58 |  |  | O | ON | 신규 BMS(5F TPS실) Rack
DACOM EOS | O | ON |  |  | 0 |  | 3P 20A | #23 | Singtel-2 | Singtel-2 | #24 | 3P 20A |  |  | 0.58 |  | O | ON | kt mspp 전원
| O | ON | 0.42 |  |  |  | 3P 20A | #25 | Singtel-2 |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
SKB2.5G전용 PDU B3 27 | O | ON |  | 1.48 |  |  | 3P 20A | #27 | Singtel-2 | 다코스 & NTT | #28 | 3P 20A |  | 0.29 |  |  | O | ON | B3-2-6(2) / 5F-B-15 (2)
데이콤 AC전원 | O | ON |  |  | 2.21 |  | 3P 20A | #29 | Singtel-2 | Singtel-2 | #30 | 3P 20A |  |  | 0.48 |  | O | ON | TNSI A
[12 empty] | 합계: | 20.97 | 10.27 | 14.09
PDU(C) | [8 empty] | Main CB 4P 50A
[12 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  |  |  | 3P 50A | #01(3상) |  |  | #02(3상) | 3P 50A |  |  |  |  | X | OFF
라우터룸 System box | O | ON |  |  |  |  | 3P 30A | #03(3상) | Singtel-2 |  | #04(3상) | 3P 30A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  |  |  | X | OFF
SYSTEM BOX | X | OFF |  |  |  |  | 3P 30A | #07 |  | Singtel-2 | #08 | 3P 30A |  |  |  |  | O | ON | SYSTEM BOX
customer con | X | OFF |  |  |  |  | 3P 20A | #09 |  | Singtel-2 | #10 | 3P 20A |  |  |  |  | O | ON | SYSTEM BOX
SYSTEM BOX | O | ON |  |  |  |  | 3P 20A | #11 | Singtel-2 |  | #12 | 3P 20A |  |  |  |  | X | OFF | customer con
| O | OFF |  |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A |  |  |  |  | X | OFF | customer con
M/S 단파 | O | ON |  |  |  |  | 3P 20A | #15 | Singtel-2 |  | #16 | 3P 20A |  |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-17 |  | PDU : SEL1 - 5-1 - A9 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 5.5 | 7.2 | 2.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RT-07 | ○ | ON | 0.59 |  |  |  | 2P 30A | #01 | U08-A-01 | U08-A-02 | #02 | 2P 30A | 0.83 |  |  |  | ○ | ON | RT-08
RT-09 | ○ | ON |  | 0 |  |  | 2P 30A | #03 | U08-A-03 | U08-A-04 | #04 | 2P 30A |  | 0 |  |  | ○ | ON | RT-10
RT-11 | ○ | ON |  |  | 0 |  | 2P 30A | #05 | U08-A-05 | U08-A-06 | #06 | 2P 30A |  |  | 0 |  | ○ | ON | RT-12
RT-13 | ○ | ON | 0 |  |  |  | 2P 30A | #07 | U08-A-07 | U08-A-08 | #08 | 2P 30A | 2.19 |  |  |  | ○ | ON | RT-14
RT-15 | ○ | ON |  | 7.17 |  |  | 2P 30A | #09 | U08-A-09 | U08-A-10 | #10 | 2P 30A |  | 0 |  |  | ○ | ON | RT-16
RT-17 | ○ | ON |  |  | 0.53 |  | 2P 30A | #11 | U08-A-11 | U08-A-12 | #12 | 2P 30A |  |  | 1.11 |  | ○ | ON | RT-18
RT-19 | ○ | ON | 0 |  |  |  | 2P 30A | #13 | U08-A-13 | U08-A-14 | #14 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-01
LSP-02 | ○ | OFF |  | 0 |  |  | 2P 30A | #15 | U08-A-15 | U08-A-16 | #16 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-03
LSP-04 | ○ | ON |  |  | 0.75 |  | 2P 30A | #17 | U08-A-17 | U08-A-18 | #18 | 2P 30A |  |  | 0 |  | ○ | OFF | LSP-05
LSP-06 | ○ | OFF | 0 |  |  |  | 2P 30A | #19 | U08-A-19 | U08-A-20 | #20 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-07
LSP-08 | ○ | OFF |  | 0 |  |  | 2P 30A | #21 | U08-A-21 | U08-A-22 | #22 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-09
LSP-10 | ○ | OFF |  |  | 0 |  | 2P 30A | #23 | U08-A-23 | U08-A-24 | #24 | 2P 30A |  |  | 0 |  | ○ | ON | MT-06
RT-08 정류기 | ○ | ON | 1.81 |  |  |  | 2P 30A | #25 | U08-A-25 |  | #26 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 5.42 | 7.17 | 2.39
5-DaHall 1-PDU-18 |  | PDU : SEL1 - 5-1 - B9 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 4.6 | 5 | 1.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RT-07 | ○ | ON | 0.82 |  |  |  | 2P 30A | #01 | U08-B-01 | U08-B-02 | #02 | 2P 30A | 0.77 |  |  |  | ○ | ON | RT-08
RT-09 | ○ | ON |  | 0 |  |  | 2P 30A | #03 | U08-B-03 | U08-B-04 | #04 | 2P 30A |  | 0 |  |  | ○ | ON | RT-10
RT-11 | ○ | ON |  |  | 0 |  | 2P 30A | #05 | U08-B-05 | U08-B-06 | #06 | 2P 30A |  |  | 0 |  | ○ | ON | RT-12
RT-13 | ○ | ON | 0 |  |  |  | 2P 30A | #07 | U08-B-07 | U08-B-08 | #08 | 2P 30A | 2.14 |  |  |  | ○ | ON | RT-14
RT-15 | ○ | ON |  | 4.96 |  |  | 2P 30A | #09 | U08-B-09 | U08-B-10 | #10 | 2P 30A |  | 0 |  |  | ○ | ON | RT-16
RT-17 | ○ | ON |  |  | 0.41 |  | 2P 30A | #11 | U08-B-11 | U08-B-12 | #12 | 2P 30A |  |  | 0.8 |  | ○ | ON | RT-18
RT-19 | ○ | ON | 0 |  |  |  | 2P 30A | #13 | U08-B-13 | U08-B-14 | #14 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-01
LSP-02 | ○ | OFF |  | 0 |  |  | 2P 30A | #15 | U08-B-15 | U08-B-16 | #16 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-03
LSP-04 | ○ | OFF |  |  | 0 |  | 2P 30A | #17 | U08-B-17 | U08-B-18 | #18 | 2P 30A |  |  | 0 |  | ○ | OFF | LSP-05
LSP-06 | ○ | OFF | 0 |  |  |  | 2P 30A | #19 | U08-B-19 | U08-B-20 | #20 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-07
LSP-08 | ○ | OFF |  | 0 |  |  | 2P 30A | #21 | U08-B-21 | U08-B-22 | #22 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-09
LSP-10 | ○ | OFF |  |  | 0 |  | 2P 30A | #23 | U08-B-23 | U08-B-24 | #24 | 2P 30A |  |  | 0 |  | ○ | ON | 시로코팬
RT-08 정류기 | ○ | ON | 1 |  |  |  | 2P 30A | #25 | U08-B-25 |  | #26 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 4.73 | 4.96 | 1.21
5-DaHall 1-PDU-19 |  | PDU : SEL1 - 5-1 - A10 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 35.1 | 38.9 | 22.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-1 | ○ | ON | 3.8 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 2.85 |  |  |  | ○ | ON | RTX Rack#8, R3-1-1
RTX Rack#2, R1-2-1 | ○ | ON |  | 4.02 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 3.31 |  |  | ○ | ON | RTX Rack#9, R3-2-1
RTX Rack#3, R1-3-1 | ○ | ON |  |  | 0 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 2.78 |  | ○ | ON | NW/Mgmt Rack, R3-3-1
RTX Rack#4, R2-1-1 | ○ | ON | 3.45 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 4.58 |  |  |  | ○ | ON | A40 Rack#1, R4-1-1
RTX Rack#5, R2-2-1 | ○ | ON |  | 3.38 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 4.24 |  |  | ○ | ON | A40 Rack#2, R4-2-1
RTX Rack#6, R2-3-1 | ○ | ON |  |  | 3.96 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 3.98 |  | ○ | ON | NetApp FAS#1, R4-3-1
RTX Rack#7, R2-4-1 | ○ | ON | 3.33 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 1.38 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-1
DGX Rack#1, R5-1-1 | ○ | ON |  | 2.93 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 4.51 |  |  | ○ | OFF | 예비Rack#1, R6-1-1
DGX Rack#2, R5-2-1 | ○ | ON |  |  | 2.7 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 4.48 |  | ○ | OFF | 예비Rack#2, R6-2-1
DGX Rack#3, R5-3-1 | ○ | ON | 1.91 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 5.98 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-1
| X | OFF |  | 0 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 5.76 |  |  | ○ | OFF | 예비Rack#4, R6-4-1
| X | OFF |  |  | 2.28 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 27.28 | 28.15 | 20.18
5-DaHall 1-PDU-20 |  | PDU : SEL1 - 5-1 - B10 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 28.1 | 32.6 | 23.1 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-2 | ○ | ON | 4.82 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 3.34 |  |  |  | ○ | ON | RTX Rack#8, R3-1-2
RTX Rack#2, R1-2-2 | ○ | ON |  | 3.76 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 3.15 |  |  | ○ | ON | RTX Rack#9, R3-2-2
RTX Rack#3, R1-3-2 | ○ | ON |  |  | 0 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 1.81 |  | ○ | ON | NW/Mgmt Rack, R3-3-2
RTX Rack#4, R2-1-2 | ○ | ON | 4.08 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 4.5 |  |  |  | ○ | ON | A40 Rack#1, R4-1-2
RTX Rack#5, R2-2-2 | ○ | ON |  | 3.29 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 4.02 |  |  | ○ | ON | A40 Rack#2, R4-2-2
RTX Rack#6, R2-3-2 | ○ | ON |  |  | 3.34 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 3.88 |  | ○ | ON | NetApp FAS#1, R4-3-2
RTX Rack#7, R2-4-2 | ○ | ON | 3.03 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 1.24 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-2
DGX Rack#1, R5-1-2 | ○ | ON |  | 4.12 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 4.63 |  |  | ○ | OFF | 예비Rack#1, R6-1-2
DGX Rack#2, R5-2-2 | ○ | ON |  |  | 3.16 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 4.34 |  | ○ | OFF | 예비Rack#2, R6-2-2
DGX Rack#3, R5-3-2 | ○ | ON | 2.07 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 0.86 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-2
| X | OFF |  | 0 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 0.58 |  |  | ○ | OFF | 예비Rack#4, R6-4-2
| X | OFF |  |  | 2.15 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 23.94 | 23.55 | 18.68
5-DaHall 1-PDU-21 |  | PDU : SEL1 - 5-1 - A11 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 41.9 | 33.6 | 29.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-3 | ○ | ON | 6.16 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 2.88 |  |  |  | ○ | ON | RTX Rack#8, R3-1-3
RTX Rack#2, R1-2-3 | ○ | ON |  | 5.94 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 3.05 |  |  | ○ | ON | RTX Rack#9, R3-2-3
RTX Rack#3, R1-3-3 | ○ | ON |  |  | 0.58 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 2.51 |  | ○ | ON | NW/Mgmt Rack, R3-3-3
RTX Rack#4, R2-1-3 | ○ | ON | 3.11 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 5.15 |  |  |  | ○ | ON | A40 Rack#1, R4-1-3
RTX Rack#5, R2-2-3 | ○ | ON |  | 3.22 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 4.29 |  |  | ○ | ON | A40 Rack#2, R4-2-3
RTX Rack#6, R2-3-3 | ○ | ON |  |  | 3.12 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 1.25 |  | ○ | ON | NetApp FAS#1, R4-3-3
RTX Rack#7, R2-4-3 | ○ | ON | 3.21 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 1.82 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-3
DGX Rack#1, R5-1-3 | ○ | ON |  | 3.01 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 3.86 |  |  | ○ | OFF | 예비Rack#1, R6-1-3
DGX Rack#2, R5-2-3 | ○ | ON |  |  | 3.15 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 4.15 |  | ○ | OFF | 예비Rack#2, R6-2-3
DGX Rack#3, R5-3-3 | ○ | ON | 2.24 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 5.81 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-3
| X | OFF |  | 0 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 5.71 |  |  | ○ | OFF | 예비Rack#4, R6-4-3
| X | OFF |  |  | 2.34 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 30.38 | 29.08 | 17.1
5-DaHall 1-PDU-22 |  | PDU : SEL1 - 5-1 - B11 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 37 | 27.7 | 24 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-4 | ○ | ON | 6.08 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 2.85 |  |  |  | ○ | ON | RTX Rack#8, R3-1-4
RTX Rack#2, R1-2-4 | ○ | ON |  | 5.67 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 2.9 |  |  | ○ | ON | RTX Rack#9, R3-2-4
RTX Rack#3, R1-3-4 | ○ | ON |  |  | 1.44 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 1.57 |  | ○ | ON | NW/Mgmt Rack, R3-3-4
RTX Rack#4, R2-1-4 | ○ | ON | 3.06 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 5.06 |  |  |  | ○ | ON | A40 Rack#1, R4-1-4
RTX Rack#5, R2-2-4 | ○ | ON |  | 3.32 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 4.53 |  |  | ○ | ON | A40 Rack#2, R4-2-4
RTX Rack#6, R2-3-4 | ○ | ON |  |  | 3.46 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 1.32 |  | ○ | ON | NetApp FAS#1, R4-3-4
RTX Rack#7, R2-4-4 | ○ | ON | 2.82 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 1.84 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-4
DGX Rack#1, R5-1-4 | ○ | ON |  | 3.74 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 4.07 |  |  | ○ | OFF | 예비Rack#1, R6-1-4
DGX Rack#2, R5-2-4 | ○ | ON |  |  | 2.92 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 4.06 |  | ○ | OFF | 예비Rack#2, R6-2-4
DGX Rack#3, R5-3-4 | ○ | ON | 3.41 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 0.59 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-4
| X | OFF |  | 0 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 0.59 |  |  | ○ | OFF | 예비Rack#4, R6-4-4
| X | OFF |  |  | 2.44 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 25.71 | 24.82 | 17.21
5층 TR룸
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
PDU-8 (A) | O | ON | 5.6 | 7.2 | 2.3 | 3.8 | 3P 200A | #08 | Singtel | Singtel | #08 | 3P 200A | 4.6 | 5 | 1.5 | 2.7 | O | ON | PDU-8 (B)
텔스트라 정류기 A1 | O | ON | 8.4 | 19.2 | 9.2 | 10.7 | 3P 30A | #03 | C2C | C2C | #04 | 3P 30A | 8.6 | 8.4 | 9 | 2.1 | O | ON | 텔스트라 정류기 A2
텔스트라 정류기 B1 | O | ON | 11.2 | 8 | 11.6 | 4 | 3P 30A | #05 | C2C | C2C | #06 | 3P 30A | 11.7 | 11.5 | 11.5 | 1.8 | O | ON | 텔스트라 정류기 B2
|  |  | 사용량 | 배분
| IDC |  | 463.76 | 48.39% | [7 empty] | 5-1-A1 | 26.61 | 28.12 | 21.74
| 텔스트라 |  | 43.51 | 4.54% | [7 empty] | 5-1-B1 | 25.26 | 26.19 | 20.26
| 텔스트라 정류기 |  | 128.3 | 13.39% | [7 empty] | 5-1-A2 | 26.12 | 16.51 | 14.36
| singtel PDU-8-A |  | 14.98 | 1.563% | [7 empty] | 6-1-B2 | 23.12 | 13.7 | 14.23
| singtel PDU-8-B |  | 10.9 | 1.137% | =>합계 | 2.7% | [5 empty] | 5-1-A3 | 0 | 0 | 0
| singtel (기타) |  | 10.88 | 1.135% | [7 empty] | 5-1-B3 | 0 | 0 | 0
| LG CNS |  | 286.08 | 29.85% | [7 empty] | 5-1-A4 | 8.63 | 1.19 | 0.74
함계 | IDC |  | 958.41 | 100% | [7 empty] | 5-1-B4 | 6.41 | 1.26 | 1.33
[12 empty] | 5-1-A5 | 0 | 0 | 0
[12 empty] | 5-1-B5 | 0 | 0 | 0
[12 empty] | 5-1-A6 | 15.49 | 9.18 | 10.23
[12 empty] | 5-1-B6 | 20.32 | 13.51 | 14.06
[12 empty] | 5-1-A7 | 12.28 | 18.35 | 14.1
| C2C | [10 empty] | 5-1-B7 | 11.42 | 10.3 | 7.07
[12 empty] | 5-1-A8 | 19.53 | 13.16 | 14.74
[12 empty] | 5-1-B8 | 20.97 | 10.27 | 14.09
[12 empty] | 5-1-A9 | 5.42 | 7.17 | 2.39 | 14.98
[12 empty] | 5-1-B9 | 4.73 | 4.96 | 1.21 | 10.9
[12 empty] | 5-1-A10 | 27.28 | 28.15 | 20.18
|  |  |  | 복도 | [7 empty] | 5-1-B10 | 23.94 | 23.55 | 18.68
[12 empty] | 5-1-A11 | 30.38 | 29.08 | 17.1
[12 empty] | 5-1-B11 | 25.71 | 24.82 | 17.21 |  | 286.08
|  |  |  | ▼ | [8 empty] | 333.62 | 279.47 | 223.72 | 836.81
128.3
965.11
[5 empty] | Singtel-1 |  | Singtel-2 |  | Pacnet
Note on A226: 이현상: 계약전류 10A/랙 ? 초과시 AM연락 필요! (임영호팀장/장우창M/장태영M)
Note on A274: 이현상: 계약전류 10A/랙 ? 초과시 AM연락 필요 (임영호팀장/장우창M/장태영M)

## 5F_current (hidden)
5F | A(전류)
5-DaHall 1-PDU-01-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-01-02 | [branch#055] [A] current
5-DaHall 1-PDU-01-03 | [branch#002] [A] current
5-DaHall 1-PDU-01-04 | [branch#056] [A] current
5-DaHall 1-PDU-01-05 | [branch#003] [A] current
5-DaHall 1-PDU-01-06 | [branch#057] [A] current
5-DaHall 1-PDU-01-07 | [branch#004] [A] current
5-DaHall 1-PDU-01-08 | [branch#058] [A] current
5-DaHall 1-PDU-01-09 | [branch#005] [A] current
5-DaHall 1-PDU-01-10 | [branch#059] [A] current
5-DaHall 1-PDU-01-11 | [branch#006] [A] current
5-DaHall 1-PDU-01-12 | [branch#060] [A] current
5-DaHall 1-PDU-01-13 | [branch#007] [A] current
5-DaHall 1-PDU-01-14 | [branch#061] [A] current
5-DaHall 1-PDU-01-15 | [branch#008] [A] current
5-DaHall 1-PDU-01-16 | [branch#062] [A] current
5-DaHall 1-PDU-01-17 | [branch#009] [A] current
5-DaHall 1-PDU-01-18 | [branch#063] [A] current
5-DaHall 1-PDU-01-19 | [branch#010] [A] current
5-DaHall 1-PDU-01-20 | [branch#064] [A] current
5-DaHall 1-PDU-01-21 | [branch#011] [A] current
5-DaHall 1-PDU-01-22 | [branch#065] [A] current
5-DaHall 1-PDU-01-23 | [branch#012] [A] current
5-DaHall 1-PDU-01-24 | [branch#066] [A] current
5-DaHall 1-PDU-01-25 | [branch#013] [A] current
5-DaHall 1-PDU-01-26 | [branch#067] [A] current
5-DaHall 1-PDU-01-27 | [branch#014] [A] current
5-DaHall 1-PDU-01-28 | [branch#068] [A] current
5-DaHall 1-PDU-01-29 | [branch#015] [A] current
5-DaHall 1-PDU-01-30 | [branch#069] [A] current
5-DaHall 1-PDU-01-31 | [branch#016] [A] current
5-DaHall 1-PDU-01-32 | [branch#070] [A] current
5-DaHall 1-PDU-01-33 | [branch#017] [A] current
5-DaHall 1-PDU-01-34 | [branch#071] [A] current
5-DaHall 1-PDU-01-35 | [branch#018] [A] current
5-DaHall 1-PDU-01-36 | [branch#072] [A] current
5-DaHall 1-PDU-01-37 | [branch#019] [A] current
5-DaHall 1-PDU-01-38 | [branch#073] [A] current
5-DaHall 1-PDU-01-39 | [branch#020] [A] current
5-DaHall 1-PDU-01-40 | [branch#074] [A] current
5-DaHall 1-PDU-01-41 | [branch#021] [A] current
5-DaHall 1-PDU-01-42 | [branch#075] [A] current
5-DaHall 1-PDU-01-43 | [branch#022] [A] current
5-DaHall 1-PDU-01-44 | [branch#076] [A] current
5-DaHall 1-PDU-01-45 | [branch#023] [A] current
5-DaHall 1-PDU-01-46 | [branch#077] [A] current
5-DaHall 1-PDU-01-47 | [branch#024] [A] current
5-DaHall 1-PDU-01-48 | [branch#078] [A] current
5-DaHall 1-PDU-01-49 | [branch#025] [A] current
5-DaHall 1-PDU-01-50 | [branch#079] [A] current
5-DaHall 1-PDU-01-51 | [branch#026] [A] current
5-DaHall 1-PDU-01-52 | [branch#080] [A] current
5-DaHall 1-PDU-02-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-02-02 | [branch#055] [A] current
5-DaHall 1-PDU-02-03 | [branch#002] [A] current
5-DaHall 1-PDU-02-04 | [branch#056] [A] current
5-DaHall 1-PDU-02-05 | [branch#003] [A] current
5-DaHall 1-PDU-02-06 | [branch#057] [A] current
5-DaHall 1-PDU-02-07 | [branch#004] [A] current
5-DaHall 1-PDU-02-08 | [branch#058] [A] current
5-DaHall 1-PDU-02-09 | [branch#005] [A] current
5-DaHall 1-PDU-02-10 | [branch#059] [A] current
5-DaHall 1-PDU-02-11 | [branch#006] [A] current
5-DaHall 1-PDU-02-12 | [branch#060] [A] current
5-DaHall 1-PDU-02-13 | [branch#007] [A] current
5-DaHall 1-PDU-02-14 | [branch#061] [A] current
5-DaHall 1-PDU-02-15 | [branch#008] [A] current
5-DaHall 1-PDU-02-16 | [branch#062] [A] current
5-DaHall 1-PDU-02-17 | [branch#009] [A] current
5-DaHall 1-PDU-02-18 | [branch#063] [A] current
5-DaHall 1-PDU-02-19 | [branch#010] [A] current
5-DaHall 1-PDU-02-20 | [branch#064] [A] current
5-DaHall 1-PDU-02-21 | [branch#011] [A] current
5-DaHall 1-PDU-02-22 | [branch#065] [A] current
5-DaHall 1-PDU-02-23 | [branch#012] [A] current
5-DaHall 1-PDU-02-24 | [branch#066] [A] current
5-DaHall 1-PDU-02-25 | [branch#013] [A] current
5-DaHall 1-PDU-02-26 | [branch#067] [A] current
5-DaHall 1-PDU-02-27 | [branch#014] [A] current
5-DaHall 1-PDU-02-28 | [branch#068] [A] current
5-DaHall 1-PDU-02-29 | [branch#015] [A] current
5-DaHall 1-PDU-02-30 | [branch#069] [A] current
5-DaHall 1-PDU-02-31 | [branch#016] [A] current
5-DaHall 1-PDU-02-32 | [branch#070] [A] current
5-DaHall 1-PDU-02-33 | [branch#017] [A] current
5-DaHall 1-PDU-02-34 | [branch#071] [A] current
5-DaHall 1-PDU-02-35 | [branch#018] [A] current
5-DaHall 1-PDU-02-36 | [branch#072] [A] current
5-DaHall 1-PDU-02-37 | [branch#019] [A] current
5-DaHall 1-PDU-02-38 | [branch#073] [A] current
5-DaHall 1-PDU-02-39 | [branch#020] [A] current
5-DaHall 1-PDU-02-40 | [branch#074] [A] current
5-DaHall 1-PDU-02-41 | [branch#021] [A] current
5-DaHall 1-PDU-02-42 | [branch#075] [A] current
5-DaHall 1-PDU-02-43 | [branch#022] [A] current
5-DaHall 1-PDU-02-44 | [branch#076] [A] current
5-DaHall 1-PDU-02-45 | [branch#023] [A] current
5-DaHall 1-PDU-02-46 | [branch#077] [A] current
5-DaHall 1-PDU-02-47 | [branch#024] [A] current
5-DaHall 1-PDU-02-48 | [branch#078] [A] current
5-DaHall 1-PDU-02-49 | [branch#025] [A] current
5-DaHall 1-PDU-02-50 | [branch#079] [A] current
5-DaHall 1-PDU-02-51 | [branch#026] [A] current
5-DaHall 1-PDU-02-52 | [branch#080] [A] current
5-DaHall 1-PDU-03-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-03-02 | [branch#055] [A] current
5-DaHall 1-PDU-03-03 | [branch#002] [A] current
5-DaHall 1-PDU-03-04 | [branch#056] [A] current
5-DaHall 1-PDU-03-05 | [branch#003] [A] current
5-DaHall 1-PDU-03-06 | [branch#057] [A] current
5-DaHall 1-PDU-03-07 | [branch#004] [A] current
5-DaHall 1-PDU-03-08 | [branch#058] [A] current
5-DaHall 1-PDU-03-09 | [branch#005] [A] current
5-DaHall 1-PDU-03-10 | [branch#059] [A] current
5-DaHall 1-PDU-03-11 | [branch#006] [A] current
5-DaHall 1-PDU-03-12 | [branch#060] [A] current
5-DaHall 1-PDU-03-13 | [branch#007] [A] current
5-DaHall 1-PDU-03-14 | [branch#061] [A] current
5-DaHall 1-PDU-03-15 | [branch#008] [A] current
5-DaHall 1-PDU-03-16 | [branch#062] [A] current
5-DaHall 1-PDU-03-17 | [branch#009] [A] current
5-DaHall 1-PDU-03-18 | [branch#063] [A] current
5-DaHall 1-PDU-03-19 | [branch#010] [A] current
5-DaHall 1-PDU-03-20 | [branch#064] [A] current
5-DaHall 1-PDU-03-21 | [branch#011] [A] current
5-DaHall 1-PDU-03-22 | [branch#065] [A] current
5-DaHall 1-PDU-03-23 | [branch#012] [A] current
5-DaHall 1-PDU-03-24 | [branch#066] [A] current
5-DaHall 1-PDU-03-25 | [branch#013] [A] current
5-DaHall 1-PDU-03-26 | [branch#067] [A] current
5-DaHall 1-PDU-03-27 | [branch#014] [A] current
5-DaHall 1-PDU-03-28 | [branch#068] [A] current
5-DaHall 1-PDU-03-29 | [branch#015] [A] current
5-DaHall 1-PDU-03-30 | [branch#069] [A] current
5-DaHall 1-PDU-03-31 | [branch#016] [A] current
5-DaHall 1-PDU-03-32 | [branch#070] [A] current
5-DaHall 1-PDU-03-33 | [branch#017] [A] current
5-DaHall 1-PDU-03-34 | [branch#071] [A] current
5-DaHall 1-PDU-03-35 | [branch#018] [A] current
5-DaHall 1-PDU-03-36 | [branch#072] [A] current
5-DaHall 1-PDU-03-37 | [branch#019] [A] current
5-DaHall 1-PDU-03-38 | [branch#073] [A] current
5-DaHall 1-PDU-03-39 | [branch#020] [A] current
5-DaHall 1-PDU-03-40 | [branch#074] [A] current
5-DaHall 1-PDU-03-41 | [branch#021] [A] current
5-DaHall 1-PDU-03-42 | [branch#075] [A] current
5-DaHall 1-PDU-03-43 | [branch#022] [A] current
5-DaHall 1-PDU-03-44 | [branch#076] [A] current
5-DaHall 1-PDU-03-45 | [branch#023] [A] current
5-DaHall 1-PDU-03-46 | [branch#077] [A] current
5-DaHall 1-PDU-03-47 | [branch#024] [A] current
5-DaHall 1-PDU-03-48 | [branch#078] [A] current
5-DaHall 1-PDU-03-49 | [branch#025] [A] current
5-DaHall 1-PDU-03-50 | [branch#079] [A] current
5-DaHall 1-PDU-03-51 | [branch#026] [A] current
5-DaHall 1-PDU-03-52 | [branch#080] [A] current
5-DaHall 1-PDU-04-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-04-02 | [branch#055] [A] current
5-DaHall 1-PDU-04-03 | [branch#002] [A] current
5-DaHall 1-PDU-04-04 | [branch#056] [A] current
5-DaHall 1-PDU-04-05 | [branch#003] [A] current
5-DaHall 1-PDU-04-06 | [branch#057] [A] current
5-DaHall 1-PDU-04-07 | [branch#004] [A] current
5-DaHall 1-PDU-04-08 | [branch#058] [A] current
5-DaHall 1-PDU-04-09 | [branch#005] [A] current
5-DaHall 1-PDU-04-10 | [branch#059] [A] current
5-DaHall 1-PDU-04-11 | [branch#006] [A] current
5-DaHall 1-PDU-04-12 | [branch#060] [A] current
5-DaHall 1-PDU-04-13 | [branch#007] [A] current
5-DaHall 1-PDU-04-14 | [branch#061] [A] current
5-DaHall 1-PDU-04-15 | [branch#008] [A] current
5-DaHall 1-PDU-04-16 | [branch#062] [A] current
5-DaHall 1-PDU-04-17 | [branch#009] [A] current
5-DaHall 1-PDU-04-18 | [branch#063] [A] current
5-DaHall 1-PDU-04-19 | [branch#010] [A] current
5-DaHall 1-PDU-04-20 | [branch#064] [A] current
5-DaHall 1-PDU-04-21 | [branch#011] [A] current
5-DaHall 1-PDU-04-22 | [branch#065] [A] current
5-DaHall 1-PDU-04-23 | [branch#012] [A] current
5-DaHall 1-PDU-04-24 | [branch#066] [A] current
5-DaHall 1-PDU-04-25 | [branch#013] [A] current
5-DaHall 1-PDU-04-26 | [branch#067] [A] current
5-DaHall 1-PDU-04-27 | [branch#014] [A] current
5-DaHall 1-PDU-04-28 | [branch#068] [A] current
5-DaHall 1-PDU-04-29 | [branch#015] [A] current
5-DaHall 1-PDU-04-30 | [branch#069] [A] current
5-DaHall 1-PDU-04-31 | [branch#016] [A] current
5-DaHall 1-PDU-04-32 | [branch#070] [A] current
5-DaHall 1-PDU-04-33 | [branch#017] [A] current
5-DaHall 1-PDU-04-34 | [branch#071] [A] current
5-DaHall 1-PDU-04-35 | [branch#018] [A] current
5-DaHall 1-PDU-04-36 | [branch#072] [A] current
5-DaHall 1-PDU-04-37 | [branch#019] [A] current
5-DaHall 1-PDU-04-38 | [branch#073] [A] current
5-DaHall 1-PDU-04-39 | [branch#020] [A] current
5-DaHall 1-PDU-04-40 | [branch#074] [A] current
5-DaHall 1-PDU-04-41 | [branch#021] [A] current
5-DaHall 1-PDU-04-42 | [branch#075] [A] current
5-DaHall 1-PDU-04-43 | [branch#022] [A] current
5-DaHall 1-PDU-04-44 | [branch#076] [A] current
5-DaHall 1-PDU-04-45 | [branch#023] [A] current
5-DaHall 1-PDU-04-46 | [branch#077] [A] current
5-DaHall 1-PDU-04-47 | [branch#024] [A] current
5-DaHall 1-PDU-04-48 | [branch#078] [A] current
5-DaHall 1-PDU-04-49 | [branch#025] [A] current
5-DaHall 1-PDU-04-50 | [branch#079] [A] current
5-DaHall 1-PDU-04-51 | [branch#026] [A] current
5-DaHall 1-PDU-04-52 | [branch#080] [A] current
5-DaHall 1-PDU-05-01 | [branch#001] [A] current
5-DaHall 1-PDU-05-02 | [branch#002] [A] current
5-DaHall 1-PDU-05-03 | [branch#003] [A] current
5-DaHall 1-PDU-05-04 | [branch#004] [A] current
5-DaHall 1-PDU-05-05 | [branch#005] [A] current
5-DaHall 1-PDU-05-06 | [branch#006] [A] current
5-DaHall 1-PDU-05-07 | [branch#007] [A] current
5-DaHall 1-PDU-05-08 | [branch#008] [A] current
5-DaHall 1-PDU-05-09 | [branch#009] [A] current
5-DaHall 1-PDU-05-10 | [branch#010] [A] current
5-DaHall 1-PDU-05-11 | [branch#011] [A] current
5-DaHall 1-PDU-05-12 | [branch#012] [A] current
5-DaHall 1-PDU-05-13 | [branch#013] [A] current
5-DaHall 1-PDU-05-14 | [branch#014] [A] current
5-DaHall 1-PDU-05-15 | [branch#015] [A] current
5-DaHall 1-PDU-05-16 | [branch#016] [A] current
5-DaHall 1-PDU-05-17 | [branch#017] [A] current
5-DaHall 1-PDU-05-18 | [branch#018] [A] current
5-DaHall 1-PDU-05-19 | [branch#019] [A] current
5-DaHall 1-PDU-05-20 | [branch#020] [A] current
5-DaHall 1-PDU-05-21 | [branch#021] [A] current
5-DaHall 1-PDU-05-22 | [branch#022] [A] current
5-DaHall 1-PDU-05-23 | [branch#023] [A] current
5-DaHall 1-PDU-05-24 | [branch#024] [A] current
5-DaHall 1-PDU-05-25 | [branch#025] [A] current
5-DaHall 1-PDU-05-26 | [branch#026] [A] current
5-DaHall 1-PDU-05-27 | [branch#027] [A] current
5-DaHall 1-PDU-05-28 | [branch#028] [A] current
5-DaHall 1-PDU-05-29 | [branch#029] [A] current
5-DaHall 1-PDU-05-30 | [branch#030] [A] current
5-DaHall 1-PDU-05-31 | [branch#031] [A] current
5-DaHall 1-PDU-05-32 | [branch#032] [A] current
5-DaHall 1-PDU-05-33 | [branch#033] [A] current
5-DaHall 1-PDU-05-34 | [branch#034] [A] current
5-DaHall 1-PDU-05-35 | [branch#035] [A] current
5-DaHall 1-PDU-05-36 | [branch#036] [A] current
5-DaHall 1-PDU-05-37 | [branch#037] [A] current
5-DaHall 1-PDU-05-38 | [branch#038] [A] current
5-DaHall 1-PDU-05-39 | [branch#039] [A] current
5-DaHall 1-PDU-05-40 | [branch#040] [A] current
5-DaHall 1-PDU-05-41 | [branch#041] [A] current
5-DaHall 1-PDU-05-42 | [branch#042] [A] current
5-DaHall 1-PDU-05-43 | [branch#043] [A] current
5-DaHall 1-PDU-05-44 | [branch#044] [A] current
5-DaHall 1-PDU-05-45 | [branch#045] [A] current
5-DaHall 1-PDU-05-46 | [branch#046] [A] current
5-DaHall 1-PDU-05-47 | [branch#047] [A] current
5-DaHall 1-PDU-05-48 | [branch#048] [A] current
5-DaHall 1-PDU-05-49 | [branch#049] [A] current
5-DaHall 1-PDU-05-50 | [branch#050] [A] current
5-DaHall 1-PDU-05-51 | [branch#051] [A] current
5-DaHall 1-PDU-05-52 | [branch#052] [A] current
5-DaHall 1-PDU-05-53 | [branch#053] [A] current
5-DaHall 1-PDU-05-54 | [branch#054] [A] current
5-DaHall 1-PDU-06-01 | [branch#001] [A] current
5-DaHall 1-PDU-06-02 | [branch#002] [A] current
5-DaHall 1-PDU-06-03 | [branch#003] [A] current
5-DaHall 1-PDU-06-04 | [branch#004] [A] current
5-DaHall 1-PDU-06-05 | [branch#005] [A] current
5-DaHall 1-PDU-06-06 | [branch#006] [A] current
5-DaHall 1-PDU-06-07 | [branch#007] [A] current
5-DaHall 1-PDU-06-08 | [branch#008] [A] current
5-DaHall 1-PDU-06-09 | [branch#009] [A] current
5-DaHall 1-PDU-06-10 | [branch#010] [A] current
5-DaHall 1-PDU-06-11 | [branch#011] [A] current
5-DaHall 1-PDU-06-12 | [branch#012] [A] current
5-DaHall 1-PDU-06-13 | [branch#013] [A] current
5-DaHall 1-PDU-06-14 | [branch#014] [A] current
5-DaHall 1-PDU-06-15 | [branch#015] [A] current
5-DaHall 1-PDU-06-16 | [branch#016] [A] current
5-DaHall 1-PDU-06-17 | [branch#017] [A] current
5-DaHall 1-PDU-06-18 | [branch#018] [A] current
5-DaHall 1-PDU-06-19 | [branch#019] [A] current
5-DaHall 1-PDU-06-20 | [branch#020] [A] current
5-DaHall 1-PDU-06-21 | [branch#021] [A] current
5-DaHall 1-PDU-06-22 | [branch#022] [A] current
5-DaHall 1-PDU-06-23 | [branch#023] [A] current
5-DaHall 1-PDU-06-24 | [branch#024] [A] current
5-DaHall 1-PDU-06-25 | [branch#025] [A] current
5-DaHall 1-PDU-06-26 | [branch#026] [A] current
5-DaHall 1-PDU-06-27 | [branch#027] [A] current
5-DaHall 1-PDU-06-28 | [branch#028] [A] current
5-DaHall 1-PDU-06-29 | [branch#029] [A] current
5-DaHall 1-PDU-06-30 | [branch#030] [A] current
5-DaHall 1-PDU-06-31 | [branch#031] [A] current
5-DaHall 1-PDU-06-32 | [branch#032] [A] current
5-DaHall 1-PDU-06-33 | [branch#033] [A] current
5-DaHall 1-PDU-06-34 | [branch#034] [A] current
5-DaHall 1-PDU-06-35 | [branch#035] [A] current
5-DaHall 1-PDU-06-36 | [branch#036] [A] current
5-DaHall 1-PDU-06-37 | [branch#037] [A] current
5-DaHall 1-PDU-06-38 | [branch#038] [A] current
5-DaHall 1-PDU-06-39 | [branch#039] [A] current
5-DaHall 1-PDU-06-40 | [branch#040] [A] current
5-DaHall 1-PDU-06-41 | [branch#041] [A] current
5-DaHall 1-PDU-06-42 | [branch#042] [A] current
5-DaHall 1-PDU-06-43 | [branch#043] [A] current
5-DaHall 1-PDU-06-44 | [branch#044] [A] current
5-DaHall 1-PDU-06-45 | [branch#045] [A] current
5-DaHall 1-PDU-06-46 | [branch#046] [A] current
5-DaHall 1-PDU-06-47 | [branch#047] [A] current
5-DaHall 1-PDU-06-48 | [branch#048] [A] current
5-DaHall 1-PDU-06-49 | [branch#049] [A] current
5-DaHall 1-PDU-06-50 | [branch#050] [A] current
5-DaHall 1-PDU-06-51 | [branch#051] [A] current
5-DaHall 1-PDU-06-52 | [branch#052] [A] current
5-DaHall 1-PDU-06-53 | [branch#053] [A] current
5-DaHall 1-PDU-06-54 | [branch#054] [A] current
5-DaHall 1-PDU-07-01 | [branch#001] [A] current
5-DaHall 1-PDU-07-02 | [branch#002] [A] current
5-DaHall 1-PDU-07-03 | [branch#003] [A] current
5-DaHall 1-PDU-07-04 | [branch#004] [A] current
5-DaHall 1-PDU-07-05 | [branch#005] [A] current
5-DaHall 1-PDU-07-06 | [branch#006] [A] current
5-DaHall 1-PDU-07-07 | [branch#007] [A] current
5-DaHall 1-PDU-07-08 | [branch#008] [A] current
5-DaHall 1-PDU-07-09 | [branch#009] [A] current
5-DaHall 1-PDU-07-10 | [branch#010] [A] current
5-DaHall 1-PDU-07-11 | [branch#011] [A] current
5-DaHall 1-PDU-07-12 | [branch#012] [A] current
5-DaHall 1-PDU-07-13 | [branch#013] [A] current
5-DaHall 1-PDU-07-14 | [branch#014] [A] current
5-DaHall 1-PDU-07-15 | [branch#015] [A] current
5-DaHall 1-PDU-07-16 | [branch#016] [A] current
5-DaHall 1-PDU-07-17 | [branch#017] [A] current
5-DaHall 1-PDU-07-18 | [branch#018] [A] current
5-DaHall 1-PDU-07-19 | [branch#019] [A] current
5-DaHall 1-PDU-07-20 | [branch#020] [A] current
5-DaHall 1-PDU-07-21 | [branch#021] [A] current
5-DaHall 1-PDU-07-22 | [branch#022] [A] current
5-DaHall 1-PDU-07-23 | [branch#023] [A] current
5-DaHall 1-PDU-07-24 | [branch#024] [A] current
5-DaHall 1-PDU-07-25 | [branch#025] [A] current
5-DaHall 1-PDU-07-26 | [branch#026] [A] current
5-DaHall 1-PDU-07-27 | [branch#027] [A] current
5-DaHall 1-PDU-07-28 | [branch#028] [A] current
5-DaHall 1-PDU-07-29 | [branch#029] [A] current
5-DaHall 1-PDU-07-30 | [branch#030] [A] current
5-DaHall 1-PDU-07-31 | [branch#031] [A] current
5-DaHall 1-PDU-07-32 | [branch#032] [A] current
5-DaHall 1-PDU-07-33 | [branch#033] [A] current
5-DaHall 1-PDU-07-34 | [branch#034] [A] current
5-DaHall 1-PDU-07-35 | [branch#035] [A] current
5-DaHall 1-PDU-07-36 | [branch#036] [A] current
5-DaHall 1-PDU-08-01 | [branch#001] [A] current
5-DaHall 1-PDU-08-02 | [branch#002] [A] current
5-DaHall 1-PDU-08-03 | [branch#003] [A] current
5-DaHall 1-PDU-08-04 | [branch#004] [A] current
5-DaHall 1-PDU-08-05 | [branch#005] [A] current
5-DaHall 1-PDU-08-06 | [branch#006] [A] current
5-DaHall 1-PDU-08-07 | [branch#007] [A] current
5-DaHall 1-PDU-08-08 | [branch#008] [A] current
5-DaHall 1-PDU-08-09 | [branch#009] [A] current
5-DaHall 1-PDU-08-10 | [branch#010] [A] current
5-DaHall 1-PDU-08-11 | [branch#011] [A] current
5-DaHall 1-PDU-08-12 | [branch#012] [A] current
5-DaHall 1-PDU-08-13 | [branch#013] [A] current
5-DaHall 1-PDU-08-14 | [branch#014] [A] current
5-DaHall 1-PDU-08-15 | [branch#015] [A] current
5-DaHall 1-PDU-08-16 | [branch#016] [A] current
5-DaHall 1-PDU-08-17 | [branch#017] [A] current
5-DaHall 1-PDU-08-18 | [branch#018] [A] current
5-DaHall 1-PDU-08-19 | [branch#019] [A] current
5-DaHall 1-PDU-08-20 | [branch#020] [A] current
5-DaHall 1-PDU-08-21 | [branch#021] [A] current
5-DaHall 1-PDU-08-22 | [branch#022] [A] current
5-DaHall 1-PDU-08-23 | [branch#023] [A] current
5-DaHall 1-PDU-08-24 | [branch#024] [A] current
5-DaHall 1-PDU-08-25 | [branch#025] [A] current
5-DaHall 1-PDU-08-26 | [branch#026] [A] current
5-DaHall 1-PDU-08-27 | [branch#027] [A] current
5-DaHall 1-PDU-08-28 | [branch#028] [A] current
5-DaHall 1-PDU-08-29 | [branch#029] [A] current
5-DaHall 1-PDU-08-30 | [branch#030] [A] current
5-DaHall 1-PDU-08-31 | [branch#031] [A] current
5-DaHall 1-PDU-08-32 | [branch#032] [A] current
5-DaHall 1-PDU-08-33 | [branch#033] [A] current
5-DaHall 1-PDU-08-34 | [branch#034] [A] current
5-DaHall 1-PDU-08-35 | [branch#035] [A] current
5-DaHall 1-PDU-08-36 | [branch#036] [A] current
5-DaHall 1-PDU-09-01 | [branch#001] [A] current
5-DaHall 1-PDU-09-02 | [branch#002] [A] current
5-DaHall 1-PDU-09-03 | [branch#003] [A] current
5-DaHall 1-PDU-09-04 | [branch#004] [A] current
5-DaHall 1-PDU-09-05 | [branch#005] [A] current
5-DaHall 1-PDU-09-06 | [branch#006] [A] current
5-DaHall 1-PDU-09-07 | [branch#007] [A] current
5-DaHall 1-PDU-09-08 | [branch#008] [A] current
5-DaHall 1-PDU-09-09 | [branch#009] [A] current
5-DaHall 1-PDU-09-10 | [branch#010] [A] current
5-DaHall 1-PDU-09-11 | [branch#011] [A] current
5-DaHall 1-PDU-09-12 | [branch#012] [A] current
5-DaHall 1-PDU-09-13 | [branch#013] [A] current
5-DaHall 1-PDU-09-14 | [branch#014] [A] current
5-DaHall 1-PDU-09-15 | [branch#015] [A] current
5-DaHall 1-PDU-09-16 | [branch#016] [A] current
5-DaHall 1-PDU-09-17 | [branch#017] [A] current
5-DaHall 1-PDU-09-18 | [branch#018] [A] current
5-DaHall 1-PDU-09-19 | [branch#019] [A] current
5-DaHall 1-PDU-09-20 | [branch#020] [A] current
5-DaHall 1-PDU-09-21 | [branch#021] [A] current
5-DaHall 1-PDU-09-22 | [branch#022] [A] current
5-DaHall 1-PDU-09-23 | [branch#023] [A] current
5-DaHall 1-PDU-09-24 | [branch#024] [A] current
5-DaHall 1-PDU-09-25 | [branch#025] [A] current
5-DaHall 1-PDU-09-26 | [branch#026] [A] current
5-DaHall 1-PDU-09-27 | [branch#027] [A] current
5-DaHall 1-PDU-09-28 | [branch#028] [A] current
5-DaHall 1-PDU-09-29 | [branch#029] [A] current
5-DaHall 1-PDU-09-30 | [branch#030] [A] current
5-DaHall 1-PDU-09-31 | [branch#031] [A] current
5-DaHall 1-PDU-09-32 | [branch#032] [A] current
5-DaHall 1-PDU-09-33 | [branch#033] [A] current
5-DaHall 1-PDU-09-34 | [branch#034] [A] current
5-DaHall 1-PDU-09-35 | [branch#035] [A] current
5-DaHall 1-PDU-09-36 | [branch#036] [A] current
5-DaHall 1-PDU-09-37 | [branch#037] [A] current
5-DaHall 1-PDU-09-38 | [branch#038] [A] current
5-DaHall 1-PDU-10-01 | [branch#001] [A] current
5-DaHall 1-PDU-10-02 | [branch#002] [A] current
5-DaHall 1-PDU-10-03 | [branch#003] [A] current
5-DaHall 1-PDU-10-04 | [branch#004] [A] current
5-DaHall 1-PDU-10-05 | [branch#005] [A] current
5-DaHall 1-PDU-10-06 | [branch#006] [A] current
5-DaHall 1-PDU-10-07 | [branch#007] [A] current
5-DaHall 1-PDU-10-08 | [branch#008] [A] current
5-DaHall 1-PDU-10-09 | [branch#009] [A] current
5-DaHall 1-PDU-10-10 | [branch#010] [A] current
5-DaHall 1-PDU-10-11 | [branch#011] [A] current
5-DaHall 1-PDU-10-12 | [branch#012] [A] current
5-DaHall 1-PDU-10-13 | [branch#013] [A] current
5-DaHall 1-PDU-10-14 | [branch#014] [A] current
5-DaHall 1-PDU-10-15 | [branch#015] [A] current
5-DaHall 1-PDU-10-16 | [branch#016] [A] current
5-DaHall 1-PDU-10-17 | [branch#017] [A] current
5-DaHall 1-PDU-10-18 | [branch#018] [A] current
5-DaHall 1-PDU-10-19 | [branch#019] [A] current
5-DaHall 1-PDU-10-20 | [branch#020] [A] current
5-DaHall 1-PDU-10-21 | [branch#021] [A] current
5-DaHall 1-PDU-10-22 | [branch#022] [A] current
5-DaHall 1-PDU-10-23 | [branch#023] [A] current
5-DaHall 1-PDU-10-24 | [branch#024] [A] current
5-DaHall 1-PDU-10-25 | [branch#025] [A] current
5-DaHall 1-PDU-10-26 | [branch#026] [A] current
5-DaHall 1-PDU-10-27 | [branch#027] [A] current
5-DaHall 1-PDU-10-28 | [branch#028] [A] current
5-DaHall 1-PDU-10-29 | [branch#029] [A] current
5-DaHall 1-PDU-10-30 | [branch#030] [A] current
5-DaHall 1-PDU-10-31 | [branch#031] [A] current
5-DaHall 1-PDU-10-32 | [branch#032] [A] current
5-DaHall 1-PDU-10-33 | [branch#033] [A] current
5-DaHall 1-PDU-10-34 | [branch#034] [A] current
5-DaHall 1-PDU-10-35 | [branch#035] [A] current
5-DaHall 1-PDU-10-36 | [branch#036] [A] current
5-DaHall 1-PDU-10-37 | [branch#037] [A] current
5-DaHall 1-PDU-10-38 | [branch#038] [A] current
5-DaHall 1-PDU-11-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-11-02 | [branch#002] [A] current
5-DaHall 1-PDU-11-03 | [branch#003] [A] current
5-DaHall 1-PDU-11-04 | [branch#004] [A] current
5-DaHall 1-PDU-11-05 | [branch#005] [A] current
5-DaHall 1-PDU-11-06 | [branch#006] [A] current
5-DaHall 1-PDU-11-07 | [branch#007] [A] current
5-DaHall 1-PDU-11-08 | [branch#008] [A] current
5-DaHall 1-PDU-11-09 | [branch#009] [A] current
5-DaHall 1-PDU-11-10 | [branch#010] [A] current
5-DaHall 1-PDU-11-11 | [branch#011] [A] current
5-DaHall 1-PDU-11-12 | [branch#012] [A] current
5-DaHall 1-PDU-11-13 | [branch#013] [A] current
5-DaHall 1-PDU-11-14 | [branch#014] [A] current
5-DaHall 1-PDU-11-15 | [branch#015] [A] current
5-DaHall 1-PDU-11-16 | [branch#016] [A] current
5-DaHall 1-PDU-11-17 | [branch#017] [A] current
5-DaHall 1-PDU-11-18 | [branch#018] [A] current
5-DaHall 1-PDU-11-19 | [branch#019] [A] current
5-DaHall 1-PDU-11-20 | [branch#020] [A] current
5-DaHall 1-PDU-11-21 | [branch#021] [A] current
5-DaHall 1-PDU-11-22 | [branch#022] [A] current
5-DaHall 1-PDU-11-23 | [branch#023] [A] current
5-DaHall 1-PDU-11-24 | [branch#024] [A] current
5-DaHall 1-PDU-11-25 | [branch#025] [A] current
5-DaHall 1-PDU-11-26 | [branch#026] [A] current
5-DaHall 1-PDU-11-27 | [branch#027] [A] current
5-DaHall 1-PDU-11-28 | [branch#028] [A] current
5-DaHall 1-PDU-11-29 | [branch#029] [A] current
5-DaHall 1-PDU-11-30 | [branch#030] [A] current
5-DaHall 1-PDU-11-31 | [branch#031] [A] current
5-DaHall 1-PDU-11-32 | [branch#032] [A] current
5-DaHall 1-PDU-12-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-12-02 | [branch#002] [A] current
5-DaHall 1-PDU-12-03 | [branch#003] [A] current
5-DaHall 1-PDU-12-04 | [branch#004] [A] current
5-DaHall 1-PDU-12-05 | [branch#005] [A] current
5-DaHall 1-PDU-12-06 | [branch#006] [A] current
5-DaHall 1-PDU-12-07 | [branch#007] [A] current
5-DaHall 1-PDU-12-08 | [branch#008] [A] current
5-DaHall 1-PDU-12-09 | [branch#009] [A] current
5-DaHall 1-PDU-12-10 | [branch#010] [A] current
5-DaHall 1-PDU-12-11 | [branch#011] [A] current
5-DaHall 1-PDU-12-12 | [branch#012] [A] current
5-DaHall 1-PDU-12-13 | [branch#013] [A] current
5-DaHall 1-PDU-12-14 | [branch#014] [A] current
5-DaHall 1-PDU-12-15 | [branch#015] [A] current
5-DaHall 1-PDU-12-16 | [branch#016] [A] current
5-DaHall 1-PDU-12-17 | [branch#017] [A] current
5-DaHall 1-PDU-12-18 | [branch#018] [A] current
5-DaHall 1-PDU-12-19 | [branch#019] [A] current
5-DaHall 1-PDU-12-20 | [branch#020] [A] current
5-DaHall 1-PDU-12-21 | [branch#021] [A] current
5-DaHall 1-PDU-12-22 | [branch#022] [A] current
5-DaHall 1-PDU-12-23 | [branch#023] [A] current
5-DaHall 1-PDU-12-24 | [branch#024] [A] current
5-DaHall 1-PDU-12-25 | [branch#025] [A] current
5-DaHall 1-PDU-12-26 | [branch#026] [A] current
5-DaHall 1-PDU-12-27 | [branch#027] [A] current
5-DaHall 1-PDU-12-28 | [branch#028] [A] current
5-DaHall 1-PDU-12-29 | [branch#029] [A] current
5-DaHall 1-PDU-12-30 | [branch#030] [A] current
5-DaHall 1-PDU-12-31 | [branch#031] [A] current
5-DaHall 1-PDU-12-32 | [branch#032] [A] current
5-DaHall 1-PDU-13-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-13-02 | [branch#002] [A] current
5-DaHall 1-PDU-13-03 | [branch#003] [A] current
5-DaHall 1-PDU-13-04 | [branch#004] [A] current
5-DaHall 1-PDU-13-05 | [branch#005] [A] current
5-DaHall 1-PDU-13-06 | [branch#006] [A] current
5-DaHall 1-PDU-13-07 | [branch#007] [A] current
5-DaHall 1-PDU-13-08 | [branch#008] [A] current
5-DaHall 1-PDU-13-09 | [branch#009] [A] current
5-DaHall 1-PDU-13-10 | [branch#010] [A] current
5-DaHall 1-PDU-13-11 | [branch#011] [A] current
5-DaHall 1-PDU-13-12 | [branch#012] [A] current
5-DaHall 1-PDU-13-13 | [branch#013] [A] current
5-DaHall 1-PDU-13-14 | [branch#014] [A] current
5-DaHall 1-PDU-13-15 | [branch#015] [A] current
5-DaHall 1-PDU-13-16 | [branch#016] [A] current
5-DaHall 1-PDU-13-17 | [branch#017] [A] current
5-DaHall 1-PDU-13-18 | [branch#018] [A] current
5-DaHall 1-PDU-13-19 | [branch#019] [A] current
5-DaHall 1-PDU-13-20 | [branch#020] [A] current
5-DaHall 1-PDU-13-21 | [branch#021] [A] current
5-DaHall 1-PDU-13-22 | [branch#022] [A] current
5-DaHall 1-PDU-13-23 | [branch#023] [A] current
5-DaHall 1-PDU-13-24 | [branch#024] [A] current
5-DaHall 1-PDU-13-25 | [branch#025] [A] current
5-DaHall 1-PDU-13-26 | [branch#026] [A] current
5-DaHall 1-PDU-13-27 | [branch#027] [A] current
5-DaHall 1-PDU-13-28 | [branch#028] [A] current
5-DaHall 1-PDU-13-29 | [branch#029] [A] current
5-DaHall 1-PDU-13-30 | [branch#030] [A] current
5-DaHall 1-PDU-13-31 | [branch#031] [A] current
5-DaHall 1-PDU-13-32 | [branch#032] [A] current
5-DaHall 1-PDU-14-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-14-02 | [branch#002] [A] current
5-DaHall 1-PDU-14-03 | [branch#003] [A] current
5-DaHall 1-PDU-14-04 | [branch#004] [A] current
5-DaHall 1-PDU-14-05 | [branch#005] [A] current
5-DaHall 1-PDU-14-06 | [branch#006] [A] current
5-DaHall 1-PDU-14-07 | [branch#007] [A] current
5-DaHall 1-PDU-14-08 | [branch#008] [A] current
5-DaHall 1-PDU-14-09 | [branch#009] [A] current
5-DaHall 1-PDU-14-10 | [branch#010] [A] current
5-DaHall 1-PDU-14-11 | [branch#011] [A] current
5-DaHall 1-PDU-14-12 | [branch#012] [A] current
5-DaHall 1-PDU-14-13 | [branch#013] [A] current
5-DaHall 1-PDU-14-14 | [branch#014] [A] current
5-DaHall 1-PDU-14-15 | [branch#015] [A] current
5-DaHall 1-PDU-14-16 | [branch#016] [A] current
5-DaHall 1-PDU-14-17 | [branch#017] [A] current
5-DaHall 1-PDU-14-18 | [branch#018] [A] current
5-DaHall 1-PDU-14-19 | [branch#019] [A] current
5-DaHall 1-PDU-14-20 | [branch#020] [A] current
5-DaHall 1-PDU-14-21 | [branch#021] [A] current
5-DaHall 1-PDU-14-22 | [branch#022] [A] current
5-DaHall 1-PDU-14-23 | [branch#023] [A] current
5-DaHall 1-PDU-14-24 | [branch#024] [A] current
5-DaHall 1-PDU-14-25 | [branch#025] [A] current
5-DaHall 1-PDU-14-26 | [branch#026] [A] current
5-DaHall 1-PDU-14-27 | [branch#027] [A] current
5-DaHall 1-PDU-14-28 | [branch#028] [A] current
5-DaHall 1-PDU-14-29 | [branch#029] [A] current
5-DaHall 1-PDU-14-30 | [branch#030] [A] current
5-DaHall 1-PDU-14-31 | [branch#031] [A] current
5-DaHall 1-PDU-14-32 | [branch#032] [A] current
5-DaHall 1-PDU-15-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-15-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
5-DaHall 1-PDU-15-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
5-DaHall 1-PDU-15-04 | [branch#004] [R] I1 | [branch#004] [S] I2 | [branch#004] [T] I3
5-DaHall 1-PDU-15-05 | [branch#005] [R] I1 | [branch#005] [S] I2 | [branch#005] [T] I3
5-DaHall 1-PDU-15-06 | [branch#006] [R] I1 | [branch#006] [S] I2 | [branch#006] [T] I3
5-DaHall 1-PDU-15-07 | [branch#007] [A] current
5-DaHall 1-PDU-15-08 | [branch#008] [A] current
5-DaHall 1-PDU-15-09 | [branch#009] [A] current
5-DaHall 1-PDU-15-10 | [branch#010] [A] current
5-DaHall 1-PDU-15-11 | [branch#011] [A] current
5-DaHall 1-PDU-15-12 | [branch#012] [A] current
5-DaHall 1-PDU-15-13 | [branch#013] [A] current
5-DaHall 1-PDU-15-14 | [branch#014] [A] current
5-DaHall 1-PDU-15-15 | [branch#015] [A] current
5-DaHall 1-PDU-15-16 | [branch#016] [A] current
5-DaHall 1-PDU-15-17 | [branch#017] [A] current
5-DaHall 1-PDU-15-18 | [branch#018] [A] current
5-DaHall 1-PDU-15-19 | [branch#019] [A] current
5-DaHall 1-PDU-15-20 | [branch#020] [A] current
5-DaHall 1-PDU-15-21 | [branch#021] [A] current
5-DaHall 1-PDU-15-22 | [branch#022] [A] current
5-DaHall 1-PDU-15-23 | [branch#023] [A] current
5-DaHall 1-PDU-15-24 | [branch#024] [A] current
5-DaHall 1-PDU-15-25 | [branch#025] [A] current
5-DaHall 1-PDU-15-26 | [branch#026] [A] current
5-DaHall 1-PDU-15-27 | [branch#027] [A] current
5-DaHall 1-PDU-15-28 | [branch#028] [A] current
5-DaHall 1-PDU-15-29 | [branch#029] [A] current
5-DaHall 1-PDU-15-30 | [branch#030] [A] current
5-DaHall 1-PDU-16-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-16-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
5-DaHall 1-PDU-16-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
5-DaHall 1-PDU-16-04 | [branch#004] [R] I1 | [branch#004] [S] I2 | [branch#004] [T] I3
5-DaHall 1-PDU-16-05 | [branch#005] [R] I1 | [branch#005] [S] I2 | [branch#005] [T] I3
5-DaHall 1-PDU-16-06 | [branch#006] [R] I1 | [branch#006] [S] I2 | [branch#006] [T] I3
5-DaHall 1-PDU-16-07 | [branch#007] [A] current
5-DaHall 1-PDU-16-08 | [branch#008] [A] current
5-DaHall 1-PDU-16-09 | [branch#009] [A] current
5-DaHall 1-PDU-16-10 | [branch#010] [A] current
5-DaHall 1-PDU-16-11 | [branch#011] [A] current
5-DaHall 1-PDU-16-12 | [branch#012] [A] current
5-DaHall 1-PDU-16-13 | [branch#013] [A] current
5-DaHall 1-PDU-16-14 | [branch#014] [A] current
5-DaHall 1-PDU-16-15 | [branch#015] [A] current
5-DaHall 1-PDU-16-16 | [branch#016] [A] current
5-DaHall 1-PDU-16-17 | [branch#017] [A] current
5-DaHall 1-PDU-16-18 | [branch#018] [A] current
5-DaHall 1-PDU-16-19 | [branch#019] [A] current
5-DaHall 1-PDU-16-20 | [branch#020] [A] current
5-DaHall 1-PDU-16-21 | [branch#021] [A] current
5-DaHall 1-PDU-16-22 | [branch#022] [A] current
5-DaHall 1-PDU-16-23 | [branch#023] [A] current
5-DaHall 1-PDU-16-24 | [branch#024] [A] current
5-DaHall 1-PDU-16-25 | [branch#025] [A] current
5-DaHall 1-PDU-16-26 | [branch#026] [A] current
5-DaHall 1-PDU-16-27 | [branch#027] [A] current
5-DaHall 1-PDU-16-28 | [branch#028] [A] current
5-DaHall 1-PDU-16-29 | [branch#029] [A] current
5-DaHall 1-PDU-16-30 | [branch#030] [A] current
5-DaHall 1-PDU-17-01 | 0150 [branch#01] [A] current
5-DaHall 1-PDU-17-02 | 0290 [branch#02] [A] current
5-DaHall 1-PDU-17-03 | 0430 [branch#03] [A] current
5-DaHall 1-PDU-17-04 | 0570 [branch#04] [A] current
5-DaHall 1-PDU-17-05 | 0710 [branch#05] [A] current
5-DaHall 1-PDU-17-06 | 0850 [branch#06] [A] current
5-DaHall 1-PDU-17-07 | 0990 [branch#07] [A] current
5-DaHall 1-PDU-17-08 | 1130 [branch#08] [A] current
5-DaHall 1-PDU-17-09 | 1270 [branch#09] [A] current
5-DaHall 1-PDU-17-10 | 1410 [branch#10] [A] current
5-DaHall 1-PDU-17-11 | 1550 [branch#11] [A] current
5-DaHall 1-PDU-17-12 | 1690 [branch#12] [A] current
5-DaHall 1-PDU-17-13 | 1830 [branch#13] [A] current
5-DaHall 1-PDU-17-14 | 1970 [branch#14] [A] current
5-DaHall 1-PDU-17-15 | 2110 [branch#15] [A] current
5-DaHall 1-PDU-17-16 | 2250 [branch#16] [A] current
5-DaHall 1-PDU-17-17 | 2390 [branch#17] [A] current
5-DaHall 1-PDU-17-18 | 2530 [branch#18] [A] current
5-DaHall 1-PDU-17-19 | 2670 [branch#19] [A] current
5-DaHall 1-PDU-17-20 | 2810 [branch#20] [A] current
5-DaHall 1-PDU-17-21 | 2950 [branch#21] [A] current
5-DaHall 1-PDU-17-22 | 3090 [branch#22] [A] current
5-DaHall 1-PDU-17-23 | 3230 [branch#23] [A] current
5-DaHall 1-PDU-17-24 | 3370 [branch#24] [A] current
5-DaHall 1-PDU-17-25 | 3510 [branch#25] [A] current
5-DaHall 1-PDU-17-26 | 3650 [branch#26] [A] current
5-DaHall 1-PDU-17-27 | 3790 [branch#27] [A] current
5-DaHall 1-PDU-17-28 | 3930 [branch#28] [A] current
5-DaHall 1-PDU-17-29 | 4070 [branch#29] [A] current
5-DaHall 1-PDU-17-30 | 4210 [branch#30] [A] current
5-DaHall 1-PDU-17-31 | 4350 [branch#31] [A] current
5-DaHall 1-PDU-17-32 | 4490 [branch#32] [A] current
5-DaHall 1-PDU-17-33 | 4630 [branch#33] [A] current
5-DaHall 1-PDU-17-34 | 4770 [branch#34] [A] current
5-DaHall 1-PDU-18-01 | 0150 [branch#01] [A] current
5-DaHall 1-PDU-18-02 | 0290 [branch#02] [A] current
5-DaHall 1-PDU-18-03 | 0430 [branch#03] [A] current
5-DaHall 1-PDU-18-04 | 0570 [branch#04] [A] current
5-DaHall 1-PDU-18-05 | 0710 [branch#05] [A] current
5-DaHall 1-PDU-18-06 | 0850 [branch#06] [A] current
5-DaHall 1-PDU-18-07 | 0990 [branch#07] [A] current
5-DaHall 1-PDU-18-08 | 1130 [branch#08] [A] current
5-DaHall 1-PDU-18-09 | 1270 [branch#09] [A] current
5-DaHall 1-PDU-18-10 | 1410 [branch#10] [A] current
5-DaHall 1-PDU-18-11 | 1550 [branch#11] [A] current
5-DaHall 1-PDU-18-12 | 1690 [branch#12] [A] current
5-DaHall 1-PDU-18-13 | 1830 [branch#13] [A] current
5-DaHall 1-PDU-18-14 | 1970 [branch#14] [A] current
5-DaHall 1-PDU-18-15 | 2110 [branch#15] [A] current
5-DaHall 1-PDU-18-16 | 2250 [branch#16] [A] current
5-DaHall 1-PDU-18-17 | 2390 [branch#17] [A] current
5-DaHall 1-PDU-18-18 | 2530 [branch#18] [A] current
5-DaHall 1-PDU-18-19 | 2670 [branch#19] [A] current
5-DaHall 1-PDU-18-20 | 2810 [branch#20] [A] current
5-DaHall 1-PDU-18-21 | 2950 [branch#21] [A] current
5-DaHall 1-PDU-18-22 | 3090 [branch#22] [A] current
5-DaHall 1-PDU-18-23 | 3230 [branch#23] [A] current
5-DaHall 1-PDU-18-24 | 3370 [branch#24] [A] current
5-DaHall 1-PDU-18-25 | 3510 [branch#25] [A] current
5-DaHall 1-PDU-18-26 | 3650 [branch#26] [A] current
5-DaHall 1-PDU-18-27 | 3790 [branch#27] [A] current
5-DaHall 1-PDU-18-28 | 3930 [branch#28] [A] current
5-DaHall 1-PDU-18-29 | 4070 [branch#29] [A] current
5-DaHall 1-PDU-18-30 | 4210 [branch#30] [A] current
5-DaHall 1-PDU-18-31 | 4350 [branch#31] [A] current
5-DaHall 1-PDU-18-32 | 4490 [branch#32] [A] current
5-DaHall 1-PDU-18-33 | 4630 [branch#33] [A] current
5-DaHall 1-PDU-18-34 | 4770 [branch#34] [A] current
5-DaHall 1-PDU-19-01 | 0150 [branch#01] [A] current
5-DaHall 1-PDU-19-02 | 0290 [branch#02] [A] current
5-DaHall 1-PDU-19-03 | 0430 [branch#03] [A] current
5-DaHall 1-PDU-19-04 | 0570 [branch#04] [A] current
5-DaHall 1-PDU-19-05 | 0710 [branch#05] [A] current
5-DaHall 1-PDU-19-06 | 0850 [branch#06] [A] current
5-DaHall 1-PDU-19-07 | 0990 [branch#07] [A] current
5-DaHall 1-PDU-19-08 | 1130 [branch#08] [A] current
5-DaHall 1-PDU-19-09 | 1270 [branch#09] [A] current
5-DaHall 1-PDU-19-10 | 1410 [branch#10] [A] current
5-DaHall 1-PDU-19-11 | 1550 [branch#11] [A] current
5-DaHall 1-PDU-19-12 | 1690 [branch#12] [A] current
5-DaHall 1-PDU-19-13 | 1830 [branch#13] [A] current
5-DaHall 1-PDU-19-14 | 1970 [branch#14] [A] current
5-DaHall 1-PDU-19-15 | 2110 [branch#15] [A] current
5-DaHall 1-PDU-19-16 | 2250 [branch#16] [A] current
5-DaHall 1-PDU-19-17 | 2390 [branch#17] [A] current
5-DaHall 1-PDU-19-18 | 2530 [branch#18] [A] current
5-DaHall 1-PDU-19-19 | 2670 [branch#19] [A] current
5-DaHall 1-PDU-19-20 | 2810 [branch#20] [A] current
5-DaHall 1-PDU-19-21 | 2950 [branch#21] [A] current
5-DaHall 1-PDU-19-22 | 3090 [branch#22] [A] current
5-DaHall 1-PDU-19-23 | 3230 [branch#23] [A] current
5-DaHall 1-PDU-19-24 | 3370 [branch#24] [A] current
5-DaHall 1-PDU-20-01 | 0150 [branch#01] [A] current
5-DaHall 1-PDU-20-02 | 0290 [branch#02] [A] current
5-DaHall 1-PDU-20-03 | 0430 [branch#03] [A] current
5-DaHall 1-PDU-20-04 | 0570 [branch#04] [A] current
5-DaHall 1-PDU-20-05 | 0710 [branch#05] [A] current
5-DaHall 1-PDU-20-06 | 0850 [branch#06] [A] current
5-DaHall 1-PDU-20-07 | 0990 [branch#07] [A] current
5-DaHall 1-PDU-20-08 | 1130 [branch#08] [A] current
5-DaHall 1-PDU-20-09 | 1270 [branch#09] [A] current
5-DaHall 1-PDU-20-10 | 1410 [branch#10] [A] current
5-DaHall 1-PDU-20-11 | 1550 [branch#11] [A] current
5-DaHall 1-PDU-20-12 | 1690 [branch#12] [A] current
5-DaHall 1-PDU-20-13 | 1830 [branch#13] [A] current
5-DaHall 1-PDU-20-14 | 1970 [branch#14] [A] current
5-DaHall 1-PDU-20-15 | 2110 [branch#15] [A] current
5-DaHall 1-PDU-20-16 | 2250 [branch#16] [A] current
5-DaHall 1-PDU-20-17 | 2390 [branch#17] [A] current
5-DaHall 1-PDU-20-18 | 2530 [branch#18] [A] current
5-DaHall 1-PDU-20-19 | 2670 [branch#19] [A] current
5-DaHall 1-PDU-20-20 | 2810 [branch#20] [A] current
5-DaHall 1-PDU-20-21 | 2950 [branch#21] [A] current
5-DaHall 1-PDU-20-22 | 3090 [branch#22] [A] current
5-DaHall 1-PDU-20-23 | 3230 [branch#23] [A] current
5-DaHall 1-PDU-20-24 | 3370 [branch#24] [A] current
5-DaHall 1-PDU-21-01 | 0150 [branch#01] [A] current
5-DaHall 1-PDU-21-02 | 0290 [branch#02] [A] current
5-DaHall 1-PDU-21-03 | 0430 [branch#03] [A] current
5-DaHall 1-PDU-21-04 | 0570 [branch#04] [A] current
5-DaHall 1-PDU-21-05 | 0710 [branch#05] [A] current
5-DaHall 1-PDU-21-06 | 0850 [branch#06] [A] current
5-DaHall 1-PDU-21-07 | 0990 [branch#07] [A] current
5-DaHall 1-PDU-21-08 | 1130 [branch#08] [A] current
5-DaHall 1-PDU-21-09 | 1270 [branch#09] [A] current
5-DaHall 1-PDU-21-10 | 1410 [branch#10] [A] current
5-DaHall 1-PDU-21-11 | 1550 [branch#11] [A] current
5-DaHall 1-PDU-21-12 | 1690 [branch#12] [A] current
5-DaHall 1-PDU-21-13 | 1830 [branch#13] [A] current
5-DaHall 1-PDU-21-14 | 1970 [branch#14] [A] current
5-DaHall 1-PDU-21-15 | 2110 [branch#15] [A] current
5-DaHall 1-PDU-21-16 | 2250 [branch#16] [A] current
5-DaHall 1-PDU-21-17 | 2390 [branch#17] [A] current
5-DaHall 1-PDU-21-18 | 2530 [branch#18] [A] current
5-DaHall 1-PDU-21-19 | 2670 [branch#19] [A] current
5-DaHall 1-PDU-21-20 | 2810 [branch#20] [A] current
5-DaHall 1-PDU-21-21 | 2950 [branch#21] [A] current
5-DaHall 1-PDU-21-22 | 3090 [branch#22] [A] current
5-DaHall 1-PDU-21-23 | 3230 [branch#23] [A] current
5-DaHall 1-PDU-21-24 | 3370 [branch#24] [A] current
5-DaHall 1-PDU-22-01 | 0150 [branch#01] [A] current
5-DaHall 1-PDU-22-02 | 0290 [branch#02] [A] current
5-DaHall 1-PDU-22-03 | 0430 [branch#03] [A] current
5-DaHall 1-PDU-22-04 | 0570 [branch#04] [A] current
5-DaHall 1-PDU-22-05 | 0710 [branch#05] [A] current
5-DaHall 1-PDU-22-06 | 0850 [branch#06] [A] current
5-DaHall 1-PDU-22-07 | 0990 [branch#07] [A] current
5-DaHall 1-PDU-22-08 | 1130 [branch#08] [A] current
5-DaHall 1-PDU-22-09 | 1270 [branch#09] [A] current
5-DaHall 1-PDU-22-10 | 1410 [branch#10] [A] current
5-DaHall 1-PDU-22-11 | 1550 [branch#11] [A] current
5-DaHall 1-PDU-22-12 | 1690 [branch#12] [A] current
5-DaHall 1-PDU-22-13 | 1830 [branch#13] [A] current
5-DaHall 1-PDU-22-14 | 1970 [branch#14] [A] current
5-DaHall 1-PDU-22-15 | 2110 [branch#15] [A] current
5-DaHall 1-PDU-22-16 | 2250 [branch#16] [A] current
5-DaHall 1-PDU-22-17 | 2390 [branch#17] [A] current
5-DaHall 1-PDU-22-18 | 2530 [branch#18] [A] current
5-DaHall 1-PDU-22-19 | 2670 [branch#19] [A] current
5-DaHall 1-PDU-22-20 | 2810 [branch#20] [A] current
5-DaHall 1-PDU-22-21 | 2950 [branch#21] [A] current
5-DaHall 1-PDU-22-22 | 3090 [branch#22] [A] current
5-DaHall 1-PDU-22-23 | 3230 [branch#23] [A] current
5-DaHall 1-PDU-22-24 | 3370 [branch#24] [A] current
5-DaHall 1-CEP-05-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-CEP-05-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
5-DaHall 1-CEP-05-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
5-DaHall 1-CEP-05-04 | [branch#004] [R] I1 | [branch#004] [S] I2 | [branch#004] [T] I3
5-DaHall 1-CEP-05-05 | [branch#005] [R] I1 | [branch#005] [S] I2 | [branch#005] [T] I3
5-DaHall 1-CEP-05-06 | [branch#006] [R] I1 | [branch#006] [S] I2 | [branch#006] [T] I3
5-DaHall 1-CEP-05-07 | [branch#007] [R] I1 | [branch#007] [S] I2 | [branch#007] [T] I3
5-DaHall 1-CEP-05-08 | [branch#008] [R] I1 | [branch#008] [S] I2 | [branch#008] [T] I3
5-DaHall 1-CEP-05-09 | [branch#009] [R] I1 | [branch#009] [S] I2 | [branch#009] [T] I3
5-DaHall 1-CEP-05-10 | [branch#010] [R] I1 | [branch#010] [S] I2 | [branch#010] [T] I3
5-DaHall 1-CEP-05-11 | [branch#011] [R] I1 | [branch#011] [S] I2 | [branch#011] [T] I3
5-DaHall 1-CEP-05-12 | [branch#012] [R] I1 | [branch#012] [S] I2 | [branch#012] [T] I3
5-DaHall 1-CEP-05-13 | [branch#012] [A] current
5-DaHall 1-CEP-05-14 | [branch#013] [A] current
5-DaHall 1-CEP-05-15 | [branch#014] [A] current
5-DaHall 1-CEP-05-16 | [branch#015] [A] current
5-DaHall 1-CEP-05-17 | [branch#016] [A] current
5-DaHall 1-CEP-05-18 | [branch#017] [A] current
5-DaHall 1-CEP-06-01 | 0205 [branch#01] [R] I1 | 0230 [branch#01] [S] I2 | 0255 [branch#01] [T] I3
5-DaHall 1-CEP-06-02 | 0345 [branch#02] [R] I1 | 0370 [branch#02] [S] I2 | 0395 [branch#02] [T] I3
5-DaHall 1-CEP-06-03 | 0485 [branch#03] [R] I1 | 0510 [branch#03] [S] I2 | 0535 [branch#03] [T] I3
5-DaHall 1-CEP-06-04 | 0625 [branch#04] [R] I1 | 0650 [branch#04] [S] I2 | 0675 [branch#04] [T] I3

## 5층_부하량(월간_MAX)
Date : 2024-01-01 ~ 2024-01-31
5-DaHall 1-CEP-05 | [8 empty] | Main CB 4P 350A
[12 empty] | MAIN 계측값 : | 62.2 | 67 | 61.8 | <- 실측값 |  |  | -1
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
5-DaHall 1-CRAC-16 보조 5F-2호기(구글) | O | ON | 11.7 | 11.38 | 12.76 |  | 4P 50A | #01 | . | . | #02 | 4P 50A | 11.31 | 12.15 | 11.74 |  | O | ON | 5-DaHall 1-CRAC-15 보조 5F-1호기(구글)
5-DaHall 1-CRAC-01 LG CRAC #01 | O | ON | 21.34 | 21.44 | 21.11 |  | 4P 50A | #03 | . | . | #04 | 4P 50A | 23.39 | 23.54 | 23.26 |  | O | ON | 5-DaHall 1-CRAC-02 LG CRAC #02
5-DaHall 1-CRAC-03 LG CRAC #03 | O | ON | 22.15 | 22.3 | 22.01 |  | 4P 50A | #05 | . | . | #06 | 4P 50A | 23.91 | 23.6 | 24.02 |  | O | ON | 5-DaHall 1-CRAC-04 LG CRAC #04
5-DaHall 1-CRAC-05 LG CRAC #05 | O | ON | 24.27 | 24.43 | 23.99 |  | 4P 50A | #07 | . | . | #08 | 4P 50A | 24.15 | 24.64 | 24.11 |  | O | ON | 5-DaHall 1-CRAC-06 LG CRAC #06
5-DaHall 1-CRAC-07 LG CRAC #07 | O | ON | 21.51 | 21.7 | 21.25 |  | 4P 50A | #09 | . | . | #10 | 4P 50A | 20.25 | 20.59 | 20.22 |  | O | ON | 5-DaHall 1-CRAC-08 LG CRAC #08
5-DaHall 1-CRAC-09 LG CRAC #09 | O | ON | 25 | 25.64 | 24.92 |  | 4P 50A | #11 | . | . | #12 | 4P 50A | 23.79 | 21.74 | 23.56 |  | O | ON | 5-DaHall 1-CRAC-13 CF CRAC #01
spare | X | OFF | 0 |  |  |  | 2P 30A | #13 | . | . | #14 | 2P 30A | 0 |  |  |  | X | OFF | spare
spare | X | OFF |  | 0 |  |  | 2P 30A | #15 | . | . | #16 | 2P 50A |  | 18.29 |  |  | O | ON | 5-DaHall 1-EH (5층 가습기 Main)
spare | X | OFF |  |  | 0 |  | 2P 30A | #17 | . | . | #18 | 2P 50A |  |  | 16.37 |  | O | ON | 4-DaHall 1-EH (4층 가습기 Main)
[12 empty] | 합계: | 252.77 | 271.44 | 269.32
5-DaHall 1-CEP-06 | [8 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 0.7 | 0 | 0.7 | <- 실측값
[10 empty] | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
[10 empty] | . | #01 | 4P 60A | 20.41 | 19.9 | 19.59 |  | O | ON | LG CRAC #10 (수냉식)
[10 empty] | . | #02 | 4P 60A | 20.72 | 20.36 | 20.2 |  | O | ON | LG CRAC #11 (수냉식)
[10 empty] | . | #03 | 4P 60A | 19.99 | 19.59 | 19.6 |  | O | ON | LG CRAC #12 (수냉식)
[10 empty] | . | #04 | 4P 60A | 0 | 0 | 0 |  | X | OFF | spare
[12 empty] | 합계: | 61.12 | 59.85 | 59.39
5-DaHall 1-PDU-01 |  | PDU : SEL1 - 5-1 - A1 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 34.6 | 37.8 | 27.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0.59 | 0.74 |  | O | ON | 보다폰정류기-A
1A-1-1 | O | ON | 0 |  |  |  | 2P 30A | #01 | CF상면 |  | #02 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-21 / 1A-2-11
1A-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | CF상면 | 구글202-A | #04 | 2P 30A |  | 0 |  |  | O | ON | 1A-2-12
1A-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | CF상면 | 구글201-A | #06 | 2P 30A |  |  | 2.15 |  | O | ON | 1A-2-13
1A-1-4 | O | OFF | 0 |  |  |  | 2P 30A | #07 | CF상면 |  | #08 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-24 / 1A-2-14
G1101 (1A-1-5) | O | ON |  | 14.02 |  |  | 2P 30A | #09 | cloudflare | 구글 시스템박스 | #10 | 2P 30A |  | 0 |  |  | O | ON | 1A-2-15
G1102 (1A-1-6) | O | ON |  |  | 12.56 |  | 2P 30A | #11 | cloudflare | 철거필요 | #12 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-1
G1103 (1A-1-7) | O | ON | 15.26 |  |  |  | 2P 30A | #13 | cloudflare | 철거필요 | #14 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-2
G1104 (1A-1-8) | O | ON |  | 6.65 |  |  | 2P 30A | #15 | cloudflare | 철거필요 | #16 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-3
G1105 (1A-1-9) | O | ON |  |  | 0 |  | 2P 30A | #17 | cloudflare | 철거필요 | #18 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-4
1A-1-10 | O | ON | 1.05 |  |  |  | 2P 30A | #19 | 구글104-A | 철거필요 | #20 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-5
1A-1-11 | O | ON |  | 1.54 |  |  | 2P 30A | #21 | 구글103-A | 철거필요 | #22 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-6
1A-1-12 | O | ON |  |  | 1.58 |  | 2P 30A | #23 | 구글102-A | 철거필요 | #24 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-7
1A-1-13 | O | ON | 0 |  |  |  | 2P 30A | #25 | 구글101-A | 철거필요 | #26 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-8
1A-1-14 | O | OFF |  | 0 |  |  | 2P 30A | #27 |  | 철거필요 | #28 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-9
1A-1-15 | O | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | O | OFF | 5F-P-20 / 1A-3-10
G1201 (1A-2-1) | O | ON | 11.9 |  |  |  | 2P 30A | #31 | cloudflare |  | #32 | 2P 30A | 0 |  |  |  | O | OFF | 5F-P-21 / 1A-3-11
G1202 (1A-2-2) | O | ON |  | 10.86 |  |  | 2P 30A | #33 | cloudflare |  | #34 | 2P 30A |  | 0 |  |  | O | OFF | 5F-P-22 / 1A-3-12
G1203 (1A-2-3) | O | ON |  |  | 12.82 |  | 2P 30A | #35 | cloudflare |  | #36 | 2P 30A |  |  | 0 |  | O | OFF | 5F-P-23 / 1A-3-13
G1204 (1A-2-4) | O | ON | 10.49 |  |  |  | 2P 30A | #37 | cloudflare |  | #38 | 2P 30A | 0 |  |  |  | O | OFF | 5F-P-24 / 1A-3-14
G1205 (1A-2-5) | O | ON |  | 13.25 |  |  | 2P 30A | #39 | cloudflare | ?? | #40 | 2P 30A |  | 0 |  |  | X | OFF
1A-2-6 | O | OFF |  |  | 0 |  | 2P 30A | #41 | CF상면 | 보다폰 케이지 안쪽 | #42 | 2P 30A |  |  | 0 |  | O | OFF | 1A-4-1
1A-2-7 | O | OFF | 0 |  |  |  | 2P 30A | #43 | CF상면 | 보다폰 케이지 안쪽 | #44 | 2P 30A | 0 |  |  |  | O | OFF | 1A-4-2
1A-2-8 | O | OFF |  | 0 |  |  | 2P 30A | #45 | CF상면 | 보다폰 케이지 안쪽 | #46 | 2P 30A |  | 0.65 |  |  | O | ON | 1A-4-3
1A-2-9 | O | OFF |  |  | 0 |  | 2P 30A | #47 | CF상면 | Vodafone | #48 | 2P 30A |  |  | 1.75 |  | O | ON | VF Rack#1-상
5F-Q-20 | O | OFF | 0 |  |  |  | 2P 30A | #49 |  | Vodafone | #50 | 2P 30A | 0 |  |  |  | O | ON | VF Rack#2-상
[12 empty] | 합계: | 38.7 | 47.56 | 31.6
5-DaHall 1-PDU-02 |  | PDU : SEL1 - 5-1 - B1 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 34.6 | 35.2 | 26.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0.66 | 0.74 |  | O | ON | 보다폰정류기-B
1B-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | CF상면 |  | #02 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-21 / 1B-2-11
1B-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | CF상면 | 구글202-A | #04 | 2P 30A |  | 0 |  |  | O | ON | 1B-2-12
1B-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | CF상면 | 구글201-A | #06 | 2P 30A |  |  | 1.92 |  | O | ON | 1B-2-13
1B-1-4 | O | OFF | 0 |  |  |  | 2P 30A | #07 | CF상면 |  | #08 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-24 / 1B-2-14
G1101 (1B-1-5) | O | ON |  | 11.73 |  |  | 2P 30A | #09 | cloudflare | 구글Cage 지문인식기 | #10 | 2P 30A |  | 0 |  |  | O | ON | 1B-2-15
G1102 (1B-1-6) | O | ON |  |  | 14.33 |  | 2P 30A | #11 | cloudflare |  | #12 | 2P 30A |  |  | 0 |  | O | OFF | 1B-3-1
G1103 (1B-1-7) | O | ON | 12.61 |  |  |  | 2P 30A | #13 | cloudflare |  | #14 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-2
G1104 (1B-1-8) | O | ON |  | 6.29 |  |  | 2P 30A | #15 | cloudflare |  | #16 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-3
G1105 (1B-1-9) | O | ON |  |  | 6.72 |  | 2P 30A | #17 | cloudflare |  | #18 | 2P 30A |  |  | 0 |  | O | ON | 1B-3-4
1B-1-10 | O | ON | 0 |  |  |  | 2P 30A | #19 | 구글104-A |  | #20 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-5
1B-1-11 | O | ON |  | 1.71 |  |  | 2P 30A | #21 | 구글103-A |  | #22 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-6
1B-1-12 | O | ON |  |  | 1.34 |  | 2P 30A | #23 | 구글102-A |  | #24 | 2P 30A |  |  | 0 |  | O | ON | 1B-3-7
1B-1-13 | O | ON | 0 |  |  |  | 2P 30A | #25 | 구글101-A |  | #26 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-8
1B-1-14 | O | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-9
1B-1-15 | O | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | O | ON | 5F-P-20 / 1B-3-10
G1201 (1A-2-1) | O | ON | 13.16 |  |  |  | 2P 30A | #31 | cloudflare |  | #32 | 2P 30A | 0 |  |  |  | O | ON | 5F-P-21 / 1B-3-11
G1202 (1B-2-2) | O | ON |  | 12.74 |  |  | 2P 30A | #33 | cloudflare |  | #34 | 2P 30A |  | 0 |  |  | O | ON | 5F-P-22 / 1B-3-12
G1203 (1B-2-3) | O | ON |  |  | 10.69 |  | 2P 30A | #35 | cloudflare |  | #36 | 2P 30A |  |  | 0 |  | O | ON | 5F-P-23 / 1B-3-13
G1204 (1B-2-4) | O | ON | 12.61 |  |  |  | 2P 30A | #37 | cloudflare |  | #38 | 2P 30A | 0 |  |  |  | O | ON | 5F-P-24 / 1B-3-14
G1205 (1B-2-5) | O | ON |  | 10.61 |  |  | 2P 30A | #39 | cloudflare |  | #40 | 2P 30A |  | 0 |  |  | O | OFF | 5F-P-25 / 1B-3-15
1B-2-6 | O | OFF |  |  | 0 |  | 2P 30A | #41 | CF상면 | ?? | #42 | 2P 30A |  |  | 0 |  | O | OFF | 1B-7-1(2)
1B-2-7 | O | OFF | 0 |  |  |  | 2P 30A | #43 | CF상면 |  | #44 | 2P 30A | 0 |  |  |  | O | OFF | 1B-4-2
1B-2-8 | O | OFF |  | 0 |  |  | 2P 30A | #45 | CF상면 | 보다폰 케이지 안쪽 | #46 | 2P 30A |  | 0.65 |  |  | O | ON | 1B-4-3
1B-2-9 | O | OFF |  |  | 0 |  | 2P 30A | #47 | CF상면 | Vodafone | #48 | 2P 30A |  |  | 1.15 |  | O | ON | VF Rack#1-하
5F-Q-20 | O | OFF | 0 |  |  |  | 2P 30A | #49 |  | Vodafone | #50 | 2P 30A | 0 |  |  |  | O | ON | VF Rack#2-하
[12 empty] | 합계: | 38.38 | 44.39 | 36.89
5-DaHall 1-PDU-03 |  | PDU : SEL1 - 5-1 - A2 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 26.8 | 15.9 | 18 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0 | 0 |  | X | OFF
5F-O-16 / 2A-4-6 | O | ON | 0 |  |  |  | 2P 30A | #01 |  | KG이니시스 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B221 (R13)-1
5F-O-17 / 2A-4-7 | O | ON |  | 0 |  |  | 2P 30A | #03 |  | KG이니시스 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B221 (R13)-2
5F-O-18 | O | ON |  |  | 0 |  | 2P 30A | #05 |  | KG이니시스 | #06 | 2P 30A |  |  | 0.68 |  | O | ON | B222 (R14)-1
5F-O-19 | O | ON | 0 |  |  |  | 2P 30A | #07 |  | KG이니시스 | #08 | 2P 30A | 1.75 |  |  |  | O | ON | B222 (R14)-2
5F-O-20 | O | ON |  | 0 |  |  | 2P 30A | #09 |  | KG이니시스 | #10 | 2P 30A |  | 4.52 |  |  | O | ON | B316 (R15)-1
5F-O-21 | O | ON |  |  | 0 |  | 2P 30A | #11 |  | KG이니시스 | #12 | 2P 30A |  |  | 2.02 |  | O | ON | B316 (R15)-2
5F-O-22 | O | ON | 0 |  |  |  | 2P 30A | #13 |  | KG이니시스 | #14 | 2P 30A | 0.39 |  |  |  | O | ON | B317 (R16)-1
5F-O-23 | O | ON |  | 0 |  |  | 2P 30A | #15 |  | KG이니시스 | #16 | 2P 30A |  | 4.45 |  |  | O | ON | B318 (R17)-1
5F-O-24 | O | ON |  |  | 0 |  | 2P 30A | #17 |  | KG이니시스 | #18 | 2P 30A |  |  | 0.86 |  | O | ON | B319 (R18)
2A-7-2(2) | X | OFF | 0 |  |  |  | 2P 30A | #19 | ?? | KG이니시스 | #20 | 2P 30A | 2.96 |  |  |  | O | ON | B320 (R19)
2A-5-1 | O | OFF |  | 0 |  |  | 2P 30A | #21 | 보다폰상면 | KG이니시스 | #22 | 2P 30A |  | 3.16 |  |  | O | ON | B321 (R20)
2A-5-2 | O | ON |  |  | 0 |  | 2P 30A | #23 | 보다폰상면 | KG이니시스 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B322 (R21)
2A-5-3 | O | ON | 0 |  |  |  | 2P 30A | #25 | 보다폰상면 | KG이니시스 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B416 (R22)
2A-5-4 | O | ON |  | 0 |  |  | 2P 30A | #27 | 보다폰상면 | KG이니시스 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B417 (R23)
2A-5-5 | O | ON |  |  | 0 |  | 2P 30A | #29 |  | KG이니시스 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B418 (R24)
5-1-A2-31 | X | OFF | 0 |  |  |  | 2P 30A | #31 |  | KG이니시스 | #32 | 2P 30A | 2.56 |  |  |  | O | ON | B116 (R12)
5-1-A2-33 | X | OFF |  | 0 |  |  | 2P 30A | #33 |  | KG이니시스 | #34 | 2P 30A |  | 2.53 |  |  | O | ON | B117 (R11)
5-1-A2-35 | X | OFF |  |  | 0 |  | 2P 30A | #35 |  | KG이니시스 | #36 | 2P 30A |  |  | 2.2 |  | O | ON | B118 (R10)
B317 (R16)-2 | O | ON | 4.35 |  |  |  | 2P 30A | #37 | KG이니시스 | KG이니시스 | #38 | 2P 30A | 2.38 |  |  |  | O | ON | B119 (R9)
B318 (R17)-2 | O | ON |  | 2.21 |  |  | 2P 30A | #39 | KG이니시스 | KG이니시스 | #40 | 2P 30A |  | 1.39 |  |  | O | ON | B120 (R8)
B221 (R13)-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | KG이니시스 | KG이니시스 | #42 | 2P 30A |  |  | 1.86 |  | O | ON | B121 (R7)
B222 (R14)-3 | O | ON | 3.31 |  |  |  | 2P 30A | #43 | KG이니시스 | KG이니시스 | #44 | 2P 30A | 3.21 |  |  |  | O | ON | B122 (R6)
B316 (R15)-3 | O | ON |  | 0 |  |  | 2P 30A | #45 | KG이니시스 | KG이니시스 | #46 | 2P 30A |  | 3.18 |  |  | O | ON | B216 (R5)
B219 (R2) | O | ON |  |  | 4.61 |  | 2P 30A | #47 | KG이니시스 | KG이니시스 | #48 | 2P 30A |  |  | 4 |  | O | ON | B217 (R4)
B220 (R1) | O | ON | 6.52 |  |  |  | 2P 30A | #49 | KG이니시스 | KG이니시스 | #50 | 2P 30A | 4.67 |  |  |  | O | ON | B218 (R3)
[12 empty] | 합계: | 32.1 | 21.44 | 16.23
5-DaHall 1-PDU-04 |  | PDU : SEL1 - 5-1 - B2 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 25.1 | 15.5 | 18.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| O | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0 | 0 |  | O | OFF
5F-O-16 / 2B-4-6 | O | ON | 0 |  |  |  | 2P 30A | #01 | 철거가능 | KG이니시스 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B221 (R13)-1
5F-O-17 / 2B-4-7 | O | ON |  | 0 |  |  | 2P 30A | #03 | 철거가능 | KG이니시스 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B221 (R13)-2
5F-O-18 | O | ON |  |  | 0 |  | 2P 30A | #05 | 철거가능 | KG이니시스 | #06 | 2P 30A |  |  | 0.69 |  | O | ON | B222 (R14)-1
5F-O-19 | O | ON | 0 |  |  |  | 2P 30A | #07 | 철거가능 | KG이니시스 | #08 | 2P 30A | 2.05 |  |  |  | O | ON | B222 (R14)-2
5F-O-20 | O | ON |  | 0 |  |  | 2P 30A | #09 | 철거가능 | KG이니시스 | #10 | 2P 30A |  | 4.45 |  |  | O | ON | B316 (R15)-1
5F-O-21 | O | ON |  |  | 0 |  | 2P 30A | #11 | 철거가능 | KG이니시스 | #12 | 2P 30A |  |  | 2.06 |  | O | ON | B316 (R15)-2
5F-O-22 | O | ON | 0 |  |  |  | 2P 30A | #13 | 철거가능 | KG이니시스 | #14 | 2P 30A | 1.02 |  |  |  | O | ON | B317 (R16)-1
5F-O-23 | O | ON |  | 0 |  |  | 2P 30A | #15 | 철거가능 | KG이니시스 | #16 | 2P 30A |  | 4.35 |  |  | O | ON | B318 (R17)-1
5F-O-24 | O | ON |  |  | 0 |  | 2P 30A | #17 | 철거가능 | KG이니시스 | #18 | 2P 30A |  |  | 0.92 |  | O | ON | B319 (R18)
2B-7-2(2) | O | OFF | 0 |  |  |  | 2P 30A | #19 | ?? | KG이니시스 | #20 | 2P 30A | 1.89 |  |  |  | O | ON | B320 (R19)
2B-5-1 | O | OFF |  | 0 |  |  | 2P 30A | #21 | 보다폰상면 | KG이니시스 | #22 | 2P 30A |  | 3.31 |  |  | O | ON | B321 (R20)
2B-5-2 | O | ON |  |  | 0 |  | 2P 30A | #23 | 보다폰상면 | KG이니시스 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B322 (R21)
2B-5-3 | O | ON | 0 |  |  |  | 2P 30A | #25 | 보다폰상면 | KG이니시스 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B416 (R22)
2B-5-4 | O | ON |  | 0 |  |  | 2P 30A | #27 | 보다폰상면 | KG이니시스 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B417 (R23)
2B-5-5 | O | ON |  |  | 0 |  | 2P 30A | #29 | 철거필요 | KG이니시스 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B418 (R24)
| X | OFF | 0 |  |  |  | 2P 30A | #31 | 철거필요 | KG이니시스 | #32 | 2P 30A | 0.75 |  |  |  | O | ON | B116 (R12)
| X | OFF |  | 0 |  |  | 2P 30A | #33 | 철거필요 | KG이니시스 | #34 | 2P 30A |  | 0.29 |  |  | O | ON | B117 (R11)
| X | OFF |  |  | 0 |  | 2P 30A | #35 | 철거가능 | KG이니시스 | #36 | 2P 30A |  |  | 2.31 |  | O | ON | B118 (R10)
B317 (R16)-2 | O | ON | 5 |  |  |  | 2P 30A | #37 | KG이니시스 | KG이니시스 | #38 | 2P 30A | 2.96 |  |  |  | O | ON | B119 (R9)
B318 (R17)-2 | O | ON |  | 1.59 |  |  | 2P 30A | #39 | KG이니시스 | KG이니시스 | #40 | 2P 30A |  | 2.33 |  |  | O | ON | B120 (R8)
B221 (R13)-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | KG이니시스 | KG이니시스 | #42 | 2P 30A |  |  | 1.6 |  | O | ON | B121 (R7)
B222 (R14)-3 | O | ON | 3.36 |  |  |  | 2P 30A | #43 | KG이니시스 | KG이니시스 | #44 | 2P 30A | 2.5 |  |  |  | O | ON | B122 (R6)
B316 (R15)-3 | O | ON |  | 0 |  |  | 2P 30A | #45 | KG이니시스 | KG이니시스 | #46 | 2P 30A |  | 2.5 |  |  | O | ON | B216 (R5)
B219 (R2) | O | ON |  |  | 4.97 |  | 2P 30A | #47 | KG이니시스 | KG이니시스 | #48 | 2P 30A |  |  | 3.77 |  | O | ON | B217 (R4)
B220 (R1) | O | ON | 6.32 |  |  |  | 2P 30A | #49 | KG이니시스 | KG이니시스 | #50 | 2P 30A | 4.46 |  |  |  | O | ON | B218 (R3)
[12 empty] | 합계: | 30.31 | 18.82 | 16.32
PDU6B-1T |  | PDU : | [6 empty] | Main CB 4P 150A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A |  |  |  |  | X | OFF
1T-1-3 | O | OFF |  |  |  |  | 3P 30A | #03 | CF상면 | . | #04 | 3P 30A |  |  |  |  | O | OFF | 1T-4-3
1T-1-6 | O | OFF |  |  |  |  | 3P 30A | #05 | CF상면 | . | #06 | 3P 30A |  |  |  |  | O | OFF | 1T-4-6
1T-1A9 | O | OFF |  |  |  |  | 3P 30A | #07 | . | . | #08 | 3P 30A |  |  |  |  | O | OFF | 1T-4-9
1T-1-12 | O | OFF |  |  |  |  | 3P 30A | #09 | Google상면 | . | #10 | 3P 30A |  |  |  |  | O | OFF | 1T-4-12
1T-2-3 | O | OFF |  |  |  |  | 3P 30A | #11 | CF상면 | . | #12 | 3P 20A |  |  |  |  | O | OFF | 1T-5-3
1T-2-6 | O | OFF |  |  |  |  | 3P 20A | #13 | . | . | #14 | 3P 20A |  |  |  |  | O | OFF | 1T-5-6
1T-2-9 | O | OFF |  |  |  |  | 3P 20A | #15 | . | . | #16 | 3P 20A |  |  |  |  | O | OFF | 1T-5-9
1T-2-12 | O | OFF |  |  |  |  | 3P 20A | #17 | Google상면 | . | #18 | 3P 20A |  |  |  |  | O | OFF | 1T-5-12
1T-3-3 | O | OFF |  |  |  |  | 3P 20A | #19 | . | . | #20 | 3P 20A |  |  |  |  | O | OFF | 1T-6-2
1T-3-6 | O | OFF |  |  |  |  | 3P 20A | #21 | . | . | #22 | 3P 20A |  |  |  |  | O | OFF | 1T-6-4
1T-3-9 | O | OFF |  |  |  |  | 3P 20A | #23 | . | . | #24 | 3P 20A |  |  |  |  | X | OFF
1T-3-12 | O | OFF |  |  |  |  | 3P 20A | #25 | . | . | #26 | 3P 20A |  |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-05 |  | PDU : SEL1 - 5-1 - A3 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  | 0 |  | 2P 30A | #01 |  |  | #02 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #03 |  |  | #04 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #13 |  |  | #14 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #19 |  |  | #20 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-2
| X | OFF |  | 0 |  |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-3
| X | OFF |  |  | 0 |  | 2P 30A | #25 |  |  | #26 | 2P 30A |  |  | 0 |  | O | OFF | 3A-12-3T
| X | OFF | 0 |  |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-4
| X | OFF |  | 0 |  |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-5
| X | OFF |  |  | 0 |  | 2P 30A | #31 |  |  | #32 | 2P 30A |  |  | 0 |  | O | OFF | 3A-12-6
| X | OFF | 0 |  |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-7
| X | OFF |  | 0 |  |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-8
| X | OFF |  |  | 0 |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #43 |  |  | #44 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-06 |  | PDU : SEL1 - 5-1 - B3 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  | 0 |  | 2P 30A | #01 |  |  | #02 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #03 |  |  | #04 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #13 |  |  | #14 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #19 |  |  | #20 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A | 0 |  |  |  | O | OFF | 3B-12-2
| X | OFF |  | 0 |  |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  | 0 |  |  | O | OFF | 3B-12-3
| X | OFF |  |  | 0 |  | 2P 30A | #25 |  |  | #26 | 2P 30A |  |  | 0 |  | O | OFF | 3B-12-4
| X | OFF | 0 |  |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A | 0 |  |  |  | O | OFF | 3B-12-5
| X | OFF |  | 0 |  |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  | 0 |  |  | O | OFF | 3B-12-6
| X | OFF |  |  | 0 |  | 2P 30A | #31 |  |  | #32 | 2P 30A |  |  | 0 |  | O | OFF | 3B-12-6T
| X | OFF | 0 |  |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A | 0 |  |  |  | O | OFF | 3B-12-7
| X | OFF |  | 0 |  |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  | 0 |  |  | O | OFF | 3B-12-8
| X | OFF |  |  | 0 |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #43 |  |  | #44 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-07 |  | PDU : SEL1 - 5-1 - A4 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 8.6 | 1.1 | 0.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
9A-1-5 (PCCW) /5F-A-14 | O | ON | 8 |  |  |  | 3P 30A | #01 | PCCW | 센츄리링크코리아 | #02 | 3P 30A | 1.07 |  |  |  | O | ON | 9A-1-8 / 5F-A-17
9A-1-6 / 5F-A-15 | O | ON |  | 1.45 |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A |  | 0 |  |  | O | ON | 9A-1-9 / 5F-A-18
9A-1-7 / 5F-A-16 | O | ON |  |  | 0.4 |  | 3P 30A | #05 | PCCW | 세종 인터넷(IES.YSM.S51) | #06 | 3P 30A |  |  | 0.39 |  | O | ON | 9A-1-10 / 5F-A-19
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #09 |  |  | #10 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 9.07 | 1.45 | 0.79
5-DaHall 1-PDU-09 |  | PDU : SEL1 - 5-1 - A5 | [6 empty] | Main CB 4P 200A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #03 |  |  | #04 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #09 |  |  | #10 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #37 |  |  | #38 | 3P 20A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-08 |  | PDU : SEL1 - 5-1 - B4 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 6.5 | 1.4 | 1.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01 | 코로케션 | 센츄리링크코리아 | #02 | 3P 30A | 1.25 |  |  |  | O | ON | 9B-1-8 / 5F-A-17
9B-1-6 / 5F-A-15 | O | ON |  | 1.49 |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A |  | 0 |  |  | O | ON | 9B-1-9 / 5F-A-18
9B-1-7 / 5F-A-16 | O | ON |  |  | 0 |  | 3P 30A | #05 | PCCW | 세종 인터넷(IES.YSM.S51) | #06 | 3P 30A |  |  | 1.38 |  | O | ON | 9B-1-10 / 5F-A-19
9B-1-5 (PCCW)/5F-A-14 | O | ON | 5.43 |  |  |  | 3P 30A | #07 | PCCW |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #09 |  |  | #10 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| O | ON |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 6.68 | 1.49 | 1.38
5-DaHall 1-PDU-10 |  | PDU : SEL1 - 5-1 - B5 | [6 empty] | Main CB 4P 200A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #03 |  |  | #04 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #09 |  |  | #10 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #37 |  |  | #38 | 3P 20A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-11 |  | PDU : SEL1 - 5-1 - A6 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 15.3 | 10.2 | 9.9 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
1A-1-1 / 5F-A-10 | O | ON | 0 |  |  |  | 3P 30A | #03 | 코로케션 |  | #04 | 3P 30A | 0 |  |  |  | O | OFF | A1-3-2
1A-1-2 / 5F-A-11 | O | ON |  | 0 |  |  | 3P 30A | #05 | 코로케션 | 코로케션 | #06 | 3P 30A |  | 2.1 |  |  | O | ON | A1-3-3
1A-1-2(2) | O | ON |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 20A |  |  | 0 |  | O | ON | A1-3-4
1A-1-3 / 5F-A-12 | O | ON | 5.3 |  |  |  | 3P 30A | #09 | PCCW | 코로케션 | #10 | 3P 20A | 0 |  |  |  | O | ON | A1-3-5
1A-1-4 / 5F-A-13 | O | ON |  | 0 |  |  | 3P 30A | #11 | PCCW | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | A1-3-6
1A-1-4(2) / 5F-A-13 (2) | O | ON |  |  | 2 |  | 3P 30A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 0 |  | O | ON | A1-3-7
A1-2-1 / 5F-B-10 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 0 |  |  |  | O | ON | A1-3-8
A1-2-2 / 5F-B-11 | O | ON |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 3.56 |  |  | O | ON | A1-3-9
A1-2-3 / 5F-B-12 | O | OFF |  |  | 0 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 3.09 |  | O | ON | A1-3-10
A1-2-4 / 5F-B-13 | O | ON | 2.7 |  |  |  | 3P 20A | #21 | 다코스 |  | #22 | 3P 20A | 0 |  |  |  | O | ON | A807 / 5F-D-16 / A1-4-7(2)
A1-2-5 / A605 (A) | O | ON |  | 5.62 |  |  | 3P 20A | #23 | 이비즈네트웍스 | PCCW | #24 | 3P 20A |  | 0 |  |  | O | ON | A1-5-10(2) / 5F-E-19
A1-2-6 / 5F-B-15 | O | ON |  |  | 0 |  | 3P 20A | #25 | 다코스 & NTT | PCCW | #26 | 3P 20A |  |  | 5.54 |  | O | ON | A1-1-3(2) / 5F-A-12(2)
A1-2-7 / 5F-B-16 | O | ON | 2.81 |  |  |  | 3P 20A | #27 | 제우스네트웍스 |  | #28 | 3P 20A | 5.63 |  |  |  | O | ON | A1-1-8(2) / 5F-A-17 (2)
A1-2-8 / 5F-B-17 | O | ON |  | 0 |  |  | 3P 20A | #29 | COLT |  | #30 | 3P 20A |  | 0 |  |  | O | ON | 5F-D-18 임시
A1-3-1 | O | OFF |  |  | 0 |  | 3P 20A | #31 |  | 코로케션 | #32 | 3P 20A |  |  | 0 |  | O | ON
[12 empty] | 합계: | 16.44 | 11.28 | 10.63
5-DaHall 1-PDU-13 |  | PDU : SEL1 - 5-1 - A7 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 12 | 18.7 | 14.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
A2-2-9 / 5F-B-18 | O | ON | 6.41 |  |  |  | 3P 30A | #03 | 코로케션 | 코로케션 | #04 | 3P 30A | 0 |  |  |  | O | ON | A2-5-4
A2-2-10 / 5F-B-19 | O | ON |  | 6.05 |  |  | 3P 30A | #05 | PCCW | 코로케션 | #06 | 3P 30A |  | 6.3 |  |  | O | ON | A2-5-5
A2-4-1 | O | ON |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 4.75 |  | O | ON | A2-5-6
A2-4-2 | O | ON | 0 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 30A | 0 |  |  |  | O | ON | A2-5-7
A2-4-3 | O | ON |  | 0 |  |  | 3P 20A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | A2-5-8
A2-4-4 | O | ON |  |  | 0.73 |  | 3P 20A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 0 |  | O | ON | A2-5-9
A2-4-5 / 5F-D-14 | O | ON | 0 |  |  |  | 3P 20A | #15 | PCCW | PCCW | #16 | 3P 20A | 3.94 |  |  |  | O | ON | A2-5-10 / 5F-E-19
A2-4-6 / 5F-D-15 | O | ON |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 0 |  |  | O | OFF | A2-6-1
A2-4-7 | O | ON |  |  | 5.51 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 0 |  | O | OFF | A2-6-2
A2-4-8 | O | ON | 3.69 |  |  |  | 3P 20A | #21 | 코로케션 | 코로케션 | #22 | 3P 20A | 0 |  |  |  | O | OFF | A2-6-3
A2-4-9 | O | ON |  | 10.05 |  |  | 3P 20A | #23 | 코로케션 | 코로케션 | #24 | 3P 20A |  | 0 |  |  | O | OFF | A2-6-4
A2-4-10 | O | ON |  |  | 2.59 |  | 3P 20A | #25 | 코로케션 | 코로케션 | #26 | 3P 20A |  |  | 2.03 |  | O | ON | A2-6-5 / F-14
A2-5-1 | O | ON | 0 |  |  |  | 3P 20A | #27 | 코로케션 | 코로케션 | #28 | 3P 20A | 0 |  |  |  | O | OFF | A2-6-6 / F-15
A2-5-2 | O | ON |  | 0 |  |  | 3P 20A | #29 | 코로케션 | 코로케션 | #30 | 3P 20A |  | 0 |  |  | O | OFF | A2-6-7 / F-16
A2-5-3 | O | ON |  |  | 0 |  | 3P 20A | #31 | 코로케션 | 코로케션 | #32 | 3P 20A |  |  | 0 |  | O | ON | A2-6-8 / F-17
[12 empty] | 합계: | 14.04 | 22.4 | 15.61
5-DaHall 1-PDU-15 |  | PDU : SEL1 - 5-1 - A8 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 19.1 | 6.2 | 14.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
AC PDU-3#A | O | ON | 6.07 | 1.28 | 8.16 |  | 3P 50A | #01(3상) | 텔스트라 | 텔스트라 | #02(3상) | 3P 50A | 3.43 | 2.84 | 2.16 |  | O | ON | TO:PDU(A)-3A
| X | OFF | 0 | 0 | 0 |  | 3P 50A | #03(3상) |  | Singtel-1 | #04(3상) | 3P 50A | 0 | 0 | 0 |  | X | OFF | DC정류기A
TRANSDUSER | O | OFF | 0 | 0 | 0 |  | 3P 30A | #05(3상) |  |  | #06(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF | customer con
PUD(A)-3-07 / 5F-B-17 (2) | O | ON | 3.88 |  |  |  | 3P 30A | #07 | COLT |  | #08 | 3P 30A | 4.34 |  |  |  | O | ON | A1007 / 5F-F-16
PUD(A)-3-09 / 5F-B-17 (3) | O | ON |  | 1.77 |  |  | 3P 30A | #09 | COLT |  | #10 | 3P 30A |  | 6.92 |  |  | O | OFF | A1006 / 5F-F-15
A603 / Colt, A-1 (23/08/23 On) | O | ON |  |  | 0 |  | 3P 30A | #11 |  | CMI | #12 | 3P 30A |  |  | 2.33 |  | O | ON | D-15랙(CMI)-A ('21.09.29 투입)
P여(A)-3 싱텔 SKB CWDM A전원 | O | ON | 0.64 |  |  |  | 3P 30A | #13 |  |  | #14 | 3P 30A | 1.59 |  |  |  | O | ON | A603 / Colt, 정류기A (23/08/23 On)
PUD(A)-2-15 | X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
PUD(A)-2-17 | X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
PUD(A)-2-19 | X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
PUD(A)-2-21 | X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
PUD(A)-2-23 | O | ON |  |  | 2.33 |  | 3P 20A | #23 | Singtel-2 |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
DACOM EOS | X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
PUD(A)-2-27 | X | OFF |  | 0 |  |  | 3P 20A | #27 |  | 다코스 & NTT | #28 | 3P 20A |  | 0.72 |  |  | O | ON | A3-2-6(2) / 5F-B-15 (2)
PUD(A)-2-29 | O | ON |  |  | 0.37 |  | 3P 20A | #29 | Singtel-2 |  | #30 | 3P 20A |  |  | 0 |  | X | OFF | TNSI A
[12 empty] | 합계: | 19.95 | 13.53 | 15.35
5-DaHall 1-PDU-12 |  | PDU : SEL1 - 5-1 - B6 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 20.1 | 13.1 | 14 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
1B-1-1 / 5F-A-10 | O | ON | 0 |  |  |  | 3P 30A | #03 | 코로케션 | 코로케션 | #04 | 3P 30A | 1.96 |  |  |  | O | ON | B1-3-3
1B-1-2 / 5F-A-11 | O | ON |  | 0 |  |  | 3P 30A | #05 | PCCW | 코로케션 | #06 | 3P 30A |  | 0 |  |  | O | ON | B1-3-4
| X | OFF |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 0 |  | O | ON | B1-3-5
1B-1-4 / 5F-A-13 | O | ON | 2.97 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 20A | 0 |  |  |  | O | ON | B1-3-6
1B-1-4(2) / 5F-A-13 (2) | O | ON |  | 0 |  |  | 3P 30A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | B1-3-7
B1-2-1 / 5F-B-10 | O | ON |  |  | 0 |  | 3P 20A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 0 |  | O | ON | B1-3-8
B1-2-2 / 5F-B-11 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 6.75 |  |  |  | O | ON | B1-3-9
B1-2-3 / 5F-B-12 | O | OFF |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 3.68 |  |  | O | ON | B1-3-10
B1-2-4 / 5F-B-13 | O | ON |  |  | 3.16 |  | 3P 20A | #19 | 다코스 |  | #20 | 3P 20A |  |  | 0 |  | X | OFF
B1-2-5 / A605 (B) | O | ON | 5.37 |  |  |  | 3P 20A | #21 | 이비즈네트웍스 |  | #22 | 3P 20A | 0 |  |  |  | X | OFF | A807 / 5F-D-16 / B1-4-7(2)
B1-2-6 / 5F-B-15 | O | ON |  | 0 |  |  | 3P 20A | #23 | 다코스 & NTT | PCCW | #24 | 3P 20A |  | 3.56 |  |  | O | ON | B1-5-10(2) / 5F-E-19
B1-2-7 / 5F-B-16 | O | ON |  |  | 3.76 |  | 3P 20A | #25 | 제우스네트웍스 | PCCW | #26 | 3P 20A |  |  | 5.04 |  | O | ON | 1B-1-3 / 5F-A-12
B1-2-8 / 5F-B-17 | O | ON | 0 |  |  |  | 3P 20A | #27 | COLT |  | #28 | 3P 20A | 5.99 |  |  |  | O | ON | B1-1-8(2) / 5F-A-17 (2)
B1-3-1 | O | ON |  | 0 |  |  | 3P 20A | #29 | 코로케션 | PCCW | #30 | 3P 20A |  | 6.56 |  |  | X | ON | B1-1-3(2) / 5F-A-12 (2)
B1-3-2 | O | OFF |  |  | 0 |  | 3P 20A | #31 | 코로케션 | 코로케션 | #32 | 3P 20A |  |  | 3.31 |  | O | ON | B1-2-9 / 5F-B-18
[12 empty] | 합계: | 23.04 | 13.8 | 15.27
5-DaHall 1-PDU-14 |  | PDU : SEL1 - 5-1 - B7 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 13.4 | 11.6 | 7.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
B2-2-10 / 5F-B-19 | O | ON | 3.3 |  |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A | 7.81 |  |  |  | O | ON | B2-5-5
B2-4-1 | O | ON |  | 0 |  |  | 3P 30A | #05 | 코로케션 | 코로케션 | #06 | 3P 30A |  | 3.09 |  |  | O | ON | B2-5-6
B2-4-2 | O | ON |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 0 |  | O | ON | B2-5-7
B2-4-3 | O | OFF | 0 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 30A | 0 |  |  |  | O | ON | B2-5-8
B2-4-4 | O | ON |  | 0 |  |  | 3P 20A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | B2-5-9
B2-4-5 / 5F-D-14 | O | ON |  |  | 1.82 |  | 3P 20A | #13 | PCCW | PCCW | #14 | 3P 20A |  |  | 3.25 |  | O | ON | B2-5-10 / 5F-E-19
B2-4-6 / 5F-D-15 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 0 |  |  |  | O | OFF | B2-6-1
B2-4-7 | O | ON |  | 1.06 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 0 |  |  | O | OFF | B2-6-2
B2-4-8 | O | ON |  |  | 2.66 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 0 |  | O | OFF | B2-6-3
B2-4-9 | O | ON | 3.72 |  |  |  | 3P 20A | #21 | 코로케션 | 코로케션 | #22 | 3P 20A | 0 |  |  |  | O | OFF | B2-6-4
B2-4-10 | O | ON |  | 2.64 |  |  | 3P 20A | #23 | 코로케션 | 코로케션 | #24 | 3P 20A |  | 5.72 |  |  | O | ON | B2-6-5 / F-14
B2-5-1 | O | ON |  |  | 0 |  | 3P 20A | #25 | 코로케션 | 코로케션 | #26 | 3P 20A |  |  | 0 |  | O | OFF | B2-6-6 / F-15
B2-5-2 | O | ON | 0 |  |  |  | 3P 20A | #27 | 코로케션 | 코로케션 | #28 | 3P 20A | 0 |  |  |  | O | OFF | B2-6-7 / F-16
B2-5-3 | O | ON |  | 0 |  |  | 3P 20A | #29 | 코로케션 | 코로케션 | #30 | 3P 20A |  | 0 |  |  | O | ON | B2-6-8 / F-17
B2-5-4 | O | ON |  |  | 0 |  | 3P 20A | #31 | 코로케션 |  | #32 | 3P 20A |  |  | 0 |  | O | ON | FMS 5층 메인전원
[12 empty] | 합계: | 14.83 | 12.51 | 7.73
5-DaHall 1-PDU-16 |  | PDU : SEL1 - 5-1 - B8 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 20.1 | 11.1 | 16 | <- 실측값 |  |  | <- 디스플래이값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
AC PDU-3#B | O | ON | 4.76 | 1.35 | 6.11 |  | 3P 50A | #01(3상) | 텔스트라 | 텔스트라 | #02(3상) | 3P 50A | 3.19 | 3.18 | 1.92 |  | O | ON | TO:PDU(B)-3A
| X | OFF | 0 | 0 | 0 |  | 3P 50A | #03(3상) |  | Singtel-1 | #04(3상) | 3P 50A | 0 | 0 | 0 |  | X | OFF | DC정류기B
TRANSDUSER | X | OFF | 0 | 0 | 0 |  | 3P 30A | #05(3상) |  |  | #06(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF | customer con
PUD(B)-3-07 / 5F-B-17 (2) | O | ON | 4.09 |  |  |  | 3P 30A | #07 | COLT |  | #08 | 3P 30A | 4.9 |  |  |  | O | ON | A1007 / 5F-F-16
PUD(B)-3-09 / 5F-B-17 (3) | O | ON |  | 1.83 |  |  | 3P 30A | #09 | COLT |  | #10 | 3P 30A |  | 1.03 |  |  | X | OFF | A1006 / 5F-F-15
A603 / Colt, B-1 (23/08/23 On) | O | ON |  |  | 0 |  | 3P 30A | #11 |  | CMI | #12 | 3P 30A |  |  | 2.59 |  | O | ON | D-15랙(CMI)-B ('21.09.29 투입)
P여(B)-3 싱텔 SKB CWDM B전원 | O | ON | 1.69 |  |  |  | 3P 30A | #13 |  |  | #14 | 3P 30A | 1.74 |  |  |  | O | ON | A603 / Colt, 정류기B (23/08/23 On)
KT Rack #2 (소형 임시정류기) | O | ON |  | 3.29 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
KT Rack #3 (소형 임시정류기) | O | ON |  |  | 3.28 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
KT Rack #4 (소형 임시정류기) | O | ON | 0 |  |  |  | 3P 20A | #19 |  | 4F BMS | #20 | 3P 20A | 0.62 |  |  |  | O | ON | 신규 BMS(4F TPS실) Rack
텔스트라 CCTV 모니터링PC 및 시스템 박스 | O | ON |  | 0.64 |  |  | 3P 20A | #21 |  | 5F BMS | #22 | 3P 20A |  | 0.59 |  |  | O | ON | 신규 BMS(5F TPS실) Rack
DACOM EOS | O | ON |  |  | 0 |  | 3P 20A | #23 | Singtel-2 | Singtel-2 | #24 | 3P 20A |  |  | 3.5 |  | O | ON | kt mspp 전원
| O | ON | 0.43 |  |  |  | 3P 20A | #25 | Singtel-2 |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
SKB2.5G전용 PDU B3 27 | O | ON |  | 1.49 |  |  | 3P 20A | #27 | Singtel-2 | 다코스 & NTT | #28 | 3P 20A |  | 0.31 |  |  | O | ON | B3-2-6(2) / 5F-B-15 (2)
데이콤 AC전원 | O | ON |  |  | 2.23 |  | 3P 20A | #29 | Singtel-2 | Singtel-2 | #30 | 3P 20A |  |  | 0.5 |  | O | ON | TNSI A
[12 empty] | 합계: | 21.42 | 13.71 | 20.13
PDU(C) | [8 empty] | Main CB 4P 50A
[12 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  |  |  | 3P 50A | #01(3상) |  |  | #02(3상) | 3P 50A |  |  |  |  | X | OFF
라우터룸 System box | O | ON |  |  |  |  | 3P 30A | #03(3상) | Singtel-2 |  | #04(3상) | 3P 30A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  |  |  | X | OFF
SYSTEM BOX | X | OFF |  |  |  |  | 3P 30A | #07 |  | Singtel-2 | #08 | 3P 30A |  |  |  |  | O | ON | SYSTEM BOX
customer con | X | OFF |  |  |  |  | 3P 20A | #09 |  | Singtel-2 | #10 | 3P 20A |  |  |  |  | O | ON | SYSTEM BOX
SYSTEM BOX | O | ON |  |  |  |  | 3P 20A | #11 | Singtel-2 |  | #12 | 3P 20A |  |  |  |  | X | OFF | customer con
| O | OFF |  |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A |  |  |  |  | X | OFF | customer con
M/S 단파 | O | ON |  |  |  |  | 3P 20A | #15 | Singtel-2 |  | #16 | 3P 20A |  |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-17 |  | PDU : SEL1 - 5-1 - A9 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 5.5 | 7.2 | 2.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RT-07 | ○ | ON | 0.72 |  |  |  | 2P 30A | #01 | U08-A-01 | U08-A-02 | #02 | 2P 30A | 0.84 |  |  |  | ○ | ON | RT-08
RT-09 | ○ | ON |  | 0 |  |  | 2P 30A | #03 | U08-A-03 | U08-A-04 | #04 | 2P 30A |  | 0 |  |  | ○ | ON | RT-10
RT-11 | ○ | ON |  |  | 0 |  | 2P 30A | #05 | U08-A-05 | U08-A-06 | #06 | 2P 30A |  |  | 0 |  | ○ | ON | RT-12
RT-13 | ○ | ON | 0 |  |  |  | 2P 30A | #07 | U08-A-07 | U08-A-08 | #08 | 2P 30A | 2.43 |  |  |  | ○ | ON | RT-14
RT-15 | ○ | ON |  | 7.33 |  |  | 2P 30A | #09 | U08-A-09 | U08-A-10 | #10 | 2P 30A |  | 0 |  |  | ○ | ON | RT-16
RT-17 | ○ | ON |  |  | 0.54 |  | 2P 30A | #11 | U08-A-11 | U08-A-12 | #12 | 2P 30A |  |  | 1.12 |  | ○ | ON | RT-18
RT-19 | ○ | ON | 0 |  |  |  | 2P 30A | #13 | U08-A-13 | U08-A-14 | #14 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-01
LSP-02 | ○ | OFF |  | 0 |  |  | 2P 30A | #15 | U08-A-15 | U08-A-16 | #16 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-03
LSP-04 | ○ | ON |  |  | 0.77 |  | 2P 30A | #17 | U08-A-17 | U08-A-18 | #18 | 2P 30A |  |  | 0 |  | ○ | OFF | LSP-05
LSP-06 | ○ | OFF | 0 |  |  |  | 2P 30A | #19 | U08-A-19 | U08-A-20 | #20 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-07
LSP-08 | ○ | OFF |  | 0 |  |  | 2P 30A | #21 | U08-A-21 | U08-A-22 | #22 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-09
LSP-10 | ○ | OFF |  |  | 0 |  | 2P 30A | #23 | U08-A-23 | U08-A-24 | #24 | 2P 30A |  |  | 0 |  | ○ | ON | MT-06
RT-08 정류기 | ○ | ON | 1.83 |  |  |  | 2P 30A | #25 | U08-A-25 |  | #26 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 5.82 | 7.33 | 2.43
5-DaHall 1-PDU-18 |  | PDU : SEL1 - 5-1 - B9 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 4.6 | 5 | 1.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RT-07 | ○ | ON | 1.12 |  |  |  | 2P 30A | #01 | U08-B-01 | U08-B-02 | #02 | 2P 30A | 0.79 |  |  |  | ○ | ON | RT-08
RT-09 | ○ | ON |  | 0 |  |  | 2P 30A | #03 | U08-B-03 | U08-B-04 | #04 | 2P 30A |  | 0 |  |  | ○ | ON | RT-10
RT-11 | ○ | ON |  |  | 0 |  | 2P 30A | #05 | U08-B-05 | U08-B-06 | #06 | 2P 30A |  |  | 0 |  | ○ | ON | RT-12
RT-13 | ○ | ON | 0 |  |  |  | 2P 30A | #07 | U08-B-07 | U08-B-08 | #08 | 2P 30A | 2.27 |  |  |  | ○ | ON | RT-14
RT-15 | ○ | ON |  | 5.05 |  |  | 2P 30A | #09 | U08-B-09 | U08-B-10 | #10 | 2P 30A |  | 0 |  |  | ○ | ON | RT-16
RT-17 | ○ | ON |  |  | 0.42 |  | 2P 30A | #11 | U08-B-11 | U08-B-12 | #12 | 2P 30A |  |  | 0.81 |  | ○ | ON | RT-18
RT-19 | ○ | ON | 0 |  |  |  | 2P 30A | #13 | U08-B-13 | U08-B-14 | #14 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-01
LSP-02 | ○ | OFF |  | 0 |  |  | 2P 30A | #15 | U08-B-15 | U08-B-16 | #16 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-03
LSP-04 | ○ | OFF |  |  | 0 |  | 2P 30A | #17 | U08-B-17 | U08-B-18 | #18 | 2P 30A |  |  | 0 |  | ○ | OFF | LSP-05
LSP-06 | ○ | OFF | 0 |  |  |  | 2P 30A | #19 | U08-B-19 | U08-B-20 | #20 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-07
LSP-08 | ○ | OFF |  | 0 |  |  | 2P 30A | #21 | U08-B-21 | U08-B-22 | #22 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-09
LSP-10 | ○ | OFF |  |  | 0 |  | 2P 30A | #23 | U08-B-23 | U08-B-24 | #24 | 2P 30A |  |  | 0 |  | ○ | ON | 시로코팬
RT-08 정류기 | ○ | ON | 1.02 |  |  |  | 2P 30A | #25 | U08-B-25 |  | #26 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 5.2 | 5.05 | 1.23
5-DaHall 1-PDU-19 |  | PDU : SEL1 - 5-1 - A10 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 35.1 | 38.9 | 22.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-1 | ○ | ON | 4.31 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 11.86 |  |  |  | ○ | ON | RTX Rack#8, R3-1-1
RTX Rack#2, R1-2-1 | ○ | ON |  | 8.04 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 10.64 |  |  | ○ | ON | RTX Rack#9, R3-2-1
RTX Rack#3, R1-3-1 | ○ | ON |  |  | 0 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 4.04 |  | ○ | ON | NW/Mgmt Rack, R3-3-1
RTX Rack#4, R2-1-1 | ○ | ON | 12.58 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 8.53 |  |  |  | ○ | ON | A40 Rack#1, R4-1-1
RTX Rack#5, R2-2-1 | ○ | ON |  | 13.86 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 10.7 |  |  | ○ | ON | A40 Rack#2, R4-2-1
RTX Rack#6, R2-3-1 | ○ | ON |  |  | 9.01 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 4.17 |  | ○ | ON | NetApp FAS#1, R4-3-1
RTX Rack#7, R2-4-1 | ○ | ON | 12.88 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 1.53 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-1
DGX Rack#1, R5-1-1 | ○ | ON |  | 10.02 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 15.36 |  |  | ○ | OFF | 예비Rack#1, R6-1-1
DGX Rack#2, R5-2-1 | ○ | ON |  |  | 6.31 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 8.98 |  | ○ | OFF | 예비Rack#2, R6-2-1
DGX Rack#3, R5-3-1 | ○ | ON | 7.41 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 11.5 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-1
| X | OFF |  | 0 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 11.78 |  |  | ○ | OFF | 예비Rack#4, R6-4-1
| X | OFF |  |  | 6.52 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 70.6 | 80.4 | 39.03
5-DaHall 1-PDU-20 |  | PDU : SEL1 - 5-1 - B10 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 28.1 | 32.6 | 23.1 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-2 | ○ | ON | 5.62 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 12.76 |  |  |  | ○ | ON | RTX Rack#8, R3-1-2
RTX Rack#2, R1-2-2 | ○ | ON |  | 8.56 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 10.55 |  |  | ○ | ON | RTX Rack#9, R3-2-2
RTX Rack#3, R1-3-2 | ○ | ON |  |  | 0 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 3.7 |  | ○ | ON | NW/Mgmt Rack, R3-3-2
RTX Rack#4, R2-1-2 | ○ | ON | 12.2 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 8.93 |  |  |  | ○ | ON | A40 Rack#1, R4-1-2
RTX Rack#5, R2-2-2 | ○ | ON |  | 14.09 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 10.8 |  |  | ○ | ON | A40 Rack#2, R4-2-2
RTX Rack#6, R2-3-2 | ○ | ON |  |  | 8.3 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 4.07 |  | ○ | ON | NetApp FAS#1, R4-3-2
RTX Rack#7, R2-4-2 | ○ | ON | 12.57 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 1.4 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-2
DGX Rack#1, R5-1-2 | ○ | ON |  | 10.98 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 15.9 |  |  | ○ | OFF | 예비Rack#1, R6-1-2
DGX Rack#2, R5-2-2 | ○ | ON |  |  | 6.57 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 8.55 |  | ○ | OFF | 예비Rack#2, R6-2-2
DGX Rack#3, R5-3-2 | ○ | ON | 7.96 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 5.8 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-2
| X | OFF |  | 0 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 3.61 |  |  | ○ | OFF | 예비Rack#4, R6-4-2
| X | OFF |  |  | 6.72 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 67.24 | 74.49 | 37.91
5-DaHall 1-PDU-21 |  | PDU : SEL1 - 5-1 - A11 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 41.9 | 33.6 | 29.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-3 | ○ | ON | 10.25 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 9.48 |  |  |  | ○ | ON | RTX Rack#8, R3-1-3
RTX Rack#2, R1-2-3 | ○ | ON |  | 9.18 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 9.99 |  |  | ○ | ON | RTX Rack#9, R3-2-3
RTX Rack#3, R1-3-3 | ○ | ON |  |  | 4.61 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 5.59 |  | ○ | ON | NW/Mgmt Rack, R3-3-3
RTX Rack#4, R2-1-3 | ○ | ON | 12.68 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 7.83 |  |  |  | ○ | ON | A40 Rack#1, R4-1-3
RTX Rack#5, R2-2-3 | ○ | ON |  | 13.38 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 11.14 |  |  | ○ | ON | A40 Rack#2, R4-2-3
RTX Rack#6, R2-3-3 | ○ | ON |  |  | 12.1 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 3.14 |  | ○ | ON | NetApp FAS#1, R4-3-3
RTX Rack#7, R2-4-3 | ○ | ON | 10.86 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 1.97 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-3
DGX Rack#1, R5-1-3 | ○ | ON |  | 5.28 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 11.65 |  |  | ○ | OFF | 예비Rack#1, R6-1-3
DGX Rack#2, R5-2-3 | ○ | ON |  |  | 6.62 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 10.04 |  | ○ | OFF | 예비Rack#2, R6-2-3
DGX Rack#3, R5-3-3 | ○ | ON | 6.55 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 11.45 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-3
| X | OFF |  | 0 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 8.26 |  |  | ○ | OFF | 예비Rack#4, R6-4-3
| X | OFF |  |  | 6.31 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 71.07 | 68.88 | 48.41
5-DaHall 1-PDU-22 |  | PDU : SEL1 - 5-1 - B11 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 37 | 27.7 | 24 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-4 | ○ | ON | 11.16 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 9.45 |  |  |  | ○ | ON | RTX Rack#8, R3-1-4
RTX Rack#2, R1-2-4 | ○ | ON |  | 9.65 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 10.03 |  |  | ○ | ON | RTX Rack#9, R3-2-4
RTX Rack#3, R1-3-4 | ○ | ON |  |  | 4.48 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 4.57 |  | ○ | ON | NW/Mgmt Rack, R3-3-4
RTX Rack#4, R2-1-4 | ○ | ON | 12.46 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 10.17 |  |  |  | ○ | ON | A40 Rack#1, R4-1-4
RTX Rack#5, R2-2-4 | ○ | ON |  | 13.4 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 10.77 |  |  | ○ | ON | A40 Rack#2, R4-2-4
RTX Rack#6, R2-3-4 | ○ | ON |  |  | 12.6 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 3.14 |  | ○ | ON | NetApp FAS#1, R4-3-4
RTX Rack#7, R2-4-4 | ○ | ON | 10.13 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 1.98 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-4
DGX Rack#1, R5-1-4 | ○ | ON |  | 5.81 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 11.89 |  |  | ○ | OFF | 예비Rack#1, R6-1-4
DGX Rack#2, R5-2-4 | ○ | ON |  |  | 6.4 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 9.65 |  | ○ | OFF | 예비Rack#2, R6-2-4
DGX Rack#3, R5-3-4 | ○ | ON | 6.56 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 4.6 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-4
| X | OFF |  | 0 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 3.8 |  |  | ○ | OFF | 예비Rack#4, R6-4-4
| X | OFF |  |  | 6.52 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 66.51 | 65.35 | 47.36
5층 TR룸
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
PDU-8 (A) | O | ON | 5.6 | 7.2 | 2.3 | 3.8 | 3P 200A | #08 | Singtel | Singtel | #08 | 3P 200A | 4.6 | 5 | 1.5 | 2.7 | O | ON | PDU-8 (B)
텔스트라 정류기 A1 | O | ON | 8.4 | 19.2 | 9.2 | 10.7 | 3P 30A | #03 | C2C | C2C | #04 | 3P 30A | 8.6 | 8.4 | 9 | 2.1 | O | ON | 텔스트라 정류기 A2
텔스트라 정류기 B1 | O | ON | 11.2 | 8 | 11.6 | 4 | 3P 30A | #05 | C2C | C2C | #06 | 3P 30A | 11.7 | 11.5 | 11.5 | 1.8 | O | ON | 텔스트라 정류기 B2
|  |  | 사용량 | 배분
| IDC |  | 603.51 | 38.66% | [7 empty] | 5-1-A1 | 38.7 | 47.56 | 31.6
| 텔스트라 |  | 45.09 | 2.889% | [7 empty] | 5-1-B1 | 38.38 | 44.39 | 36.89
| 텔스트라 정류기 |  | 128.3 | 8.219% | [7 empty] | 5-1-A2 | 32.1 | 21.44 | 16.23
| singtel PDU-8-A |  | 15.58 | 0.9981% | [7 empty] | 6-1-B2 | 30.31 | 18.82 | 16.32
| singtel PDU-8-B |  | 11.48 | 0.7354% | =>합계 | 1.734% | [5 empty] | 5-1-A3 | 0 | 0 | 0
| singtel (기타) |  | 19.75 | 1.265% | [7 empty] | 5-1-B3 | 0 | 0 | 0
| LG CNS |  | 737.25 | 47.23% | [7 empty] | 5-1-A4 | 9.07 | 1.45 | 0.79
함계 | IDC |  | 1560.96 | 100% | [7 empty] | 5-1-B4 | 6.68 | 1.49 | 1.38
[12 empty] | 5-1-A5 | 0 | 0 | 0
[12 empty] | 5-1-B5 | 0 | 0 | 0
[12 empty] | 5-1-A6 | 16.44 | 11.28 | 10.63
[12 empty] | 5-1-B6 | 23.04 | 13.8 | 15.27
[12 empty] | 5-1-A7 | 14.04 | 22.4 | 15.61
| C2C | [10 empty] | 5-1-B7 | 14.83 | 12.51 | 7.73
[12 empty] | 5-1-A8 | 19.95 | 13.53 | 15.35
[12 empty] | 5-1-B8 | 21.42 | 13.71 | 20.13
[12 empty] | 5-1-A9 | 5.82 | 7.33 | 2.43 | 15.58
[12 empty] | 5-1-B9 | 5.2 | 5.05 | 1.23 | 11.48
[12 empty] | 5-1-A10 | 70.6 | 80.4 | 39.03
|  |  |  | 복도 | [7 empty] | 5-1-B10 | 67.24 | 74.49 | 37.91
[12 empty] | 5-1-A11 | 71.07 | 68.88 | 48.41
[12 empty] | 5-1-B11 | 66.51 | 65.35 | 47.36 |  | 737.25
|  |  |  | ▼ | [8 empty] | 551.4 | 523.88 | 364.3 | 1439.58
128.3
1567.88
[5 empty] | Singtel-1 |  | Singtel-2 |  | Pacnet
Note on A226: 이현상: 계약전류 10A/랙 ? 초과시 AM연락 필요! (임영호팀장/장우창M/장태영M)
Note on A274: 이현상: 계약전류 10A/랙 ? 초과시 AM연락 필요 (임영호팀장/장우창M/장태영M)

## 5층_부하량(월간_AVG)
Date : 2024-01-01 ~ 2024-01-31
5-DaHall 1-CEP-05 | [8 empty] | Main CB 4P 350A
[12 empty] | MAIN 계측값 : | 62.2 | 67 | 61.8 | <- 실측값 |  |  | -1
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
5-DaHall 1-CRAC-16 보조 5F-2호기(구글) | O | ON | 0.07166 | 0.06934 | 0.078111 |  | 4P 50A | #01 | . | . | #02 | 4P 50A | 0.062509 | 0.066942 | 0.064941 |  | O | ON | 5-DaHall 1-CRAC-15 보조 5F-1호기(구글)
5-DaHall 1-CRAC-01 LG CRAC #01 | O | ON | 0.067326 | 0.067576 | 0.067472 |  | 4P 50A | #03 | . | . | #04 | 4P 50A | 18.4935 | 18.7089 | 18.3071 |  | O | ON | 5-DaHall 1-CRAC-02 LG CRAC #02
5-DaHall 1-CRAC-03 LG CRAC #03 | O | ON | 0.055622 | 0.055907 | 0.05581 |  | 4P 50A | #05 | . | . | #06 | 4P 50A | 18.8825 | 18.5658 | 18.8317 |  | O | ON | 5-DaHall 1-CRAC-04 LG CRAC #04
5-DaHall 1-CRAC-05 LG CRAC #05 | O | ON | 18.3005 | 18.3892 | 17.9394 |  | 4P 50A | #07 | . | . | #08 | 4P 50A | 12.941 | 13.148 | 12.9276 |  | O | ON | 5-DaHall 1-CRAC-06 LG CRAC #06
5-DaHall 1-CRAC-07 LG CRAC #07 | O | ON | 1.2625 | 1.278 | 1.2543 |  | 4P 50A | #09 | . | . | #10 | 4P 50A | 0.061327 | 0.062265 | 0.061974 |  | O | ON | 5-DaHall 1-CRAC-08 LG CRAC #08
5-DaHall 1-CRAC-09 LG CRAC #09 | O | ON | 0.061369 | 0.06271 | 0.06196 |  | 4P 50A | #11 | . | . | #12 | 4P 50A | 0.057938 | 0.052778 | 0.057076 |  | O | ON | 5-DaHall 1-CRAC-13 CF CRAC #01
spare | X | OFF | 0 |  |  |  | 2P 30A | #13 | . | . | #14 | 2P 30A | 0 |  |  |  | X | OFF | spare
spare | X | OFF |  | 0 |  |  | 2P 30A | #15 | . | . | #16 | 2P 50A |  | 12.8881 |  |  | O | ON | 5-DaHall 1-EH (5층 가습기 Main)
spare | X | OFF |  |  | 0 |  | 2P 30A | #17 | . | . | #18 | 2P 50A |  |  | 8.3019 |  | O | ON | 4-DaHall 1-EH (4층 가습기 Main)
[12 empty] | 합계: | 70.3177 | 83.4155 | 78.0093
5-DaHall 1-CEP-06 | [8 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 0.7 | 0 | 0.7 | <- 실측값
[10 empty] | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
[10 empty] | . | #01 | 4P 60A | 0.24568 | 0.12391 | 0.2488 |  | O | ON | LG CRAC #10 (수냉식)
[10 empty] | . | #02 | 4P 60A | 0.24447 | 0.071929 | 0.24801 |  | O | ON | LG CRAC #11 (수냉식)
[10 empty] | . | #03 | 4P 60A | 0.24546 | 0.061563 | 0.23486 |  | O | ON | LG CRAC #12 (수냉식)
[10 empty] | . | #04 | 4P 60A | 0 | 0 | 0 |  | X | OFF | spare
[12 empty] | 합계: | 0.73561 | 0.2574 | 0.73167
5-DaHall 1-PDU-01 |  | PDU : SEL1 - 5-1 - A1 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 34.6 | 37.8 | 27.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0.58627 | 0.72983 |  | O | ON | 보다폰정류기-A
1A-1-1 | O | ON | 0 |  |  |  | 2P 30A | #01 | CF상면 |  | #02 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-21 / 1A-2-11
1A-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | CF상면 | 구글202-A | #04 | 2P 30A |  | 0 |  |  | O | ON | 1A-2-12
1A-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | CF상면 | 구글201-A | #06 | 2P 30A |  |  | 1.5779 |  | O | ON | 1A-2-13
1A-1-4 | O | OFF | 0 |  |  |  | 2P 30A | #07 | CF상면 |  | #08 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-24 / 1A-2-14
G1101 (1A-1-5) | O | ON |  | 12.4089 |  |  | 2P 30A | #09 | cloudflare | 구글 시스템박스 | #10 | 2P 30A |  | 0 |  |  | O | ON | 1A-2-15
G1102 (1A-1-6) | O | ON |  |  | 11.186 |  | 2P 30A | #11 | cloudflare | 철거필요 | #12 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-1
G1103 (1A-1-7) | O | ON | 13.2166 |  |  |  | 2P 30A | #13 | cloudflare | 철거필요 | #14 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-2
G1104 (1A-1-8) | O | ON |  | 3.1842 |  |  | 2P 30A | #15 | cloudflare | 철거필요 | #16 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-3
G1105 (1A-1-9) | O | ON |  |  | 0 |  | 2P 30A | #17 | cloudflare | 철거필요 | #18 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-4
1A-1-10 | O | ON | 1.0387 |  |  |  | 2P 30A | #19 | 구글104-A | 철거필요 | #20 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-5
1A-1-11 | O | ON |  | 1.4715 |  |  | 2P 30A | #21 | 구글103-A | 철거필요 | #22 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-6
1A-1-12 | O | ON |  |  | 1.5393 |  | 2P 30A | #23 | 구글102-A | 철거필요 | #24 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-7
1A-1-13 | O | ON | 0 |  |  |  | 2P 30A | #25 | 구글101-A | 철거필요 | #26 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-8
1A-1-14 | O | OFF |  | 0 |  |  | 2P 30A | #27 |  | 철거필요 | #28 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-9
1A-1-15 | O | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | O | OFF | 5F-P-20 / 1A-3-10
G1201 (1A-2-1) | O | ON | 11.1759 |  |  |  | 2P 30A | #31 | cloudflare |  | #32 | 2P 30A | 0 |  |  |  | O | OFF | 5F-P-21 / 1A-3-11
G1202 (1A-2-2) | O | ON |  | 9.8387 |  |  | 2P 30A | #33 | cloudflare |  | #34 | 2P 30A |  | 0 |  |  | O | OFF | 5F-P-22 / 1A-3-12
G1203 (1A-2-3) | O | ON |  |  | 11.6822 |  | 2P 30A | #35 | cloudflare |  | #36 | 2P 30A |  |  | 0 |  | O | OFF | 5F-P-23 / 1A-3-13
G1204 (1A-2-4) | O | ON | 9.5743 |  |  |  | 2P 30A | #37 | cloudflare |  | #38 | 2P 30A | 0 |  |  |  | O | OFF | 5F-P-24 / 1A-3-14
G1205 (1A-2-5) | O | ON |  | 11.7622 |  |  | 2P 30A | #39 | cloudflare | ?? | #40 | 2P 30A |  | 0 |  |  | X | OFF
1A-2-6 | O | OFF |  |  | 0 |  | 2P 30A | #41 | CF상면 | 보다폰 케이지 안쪽 | #42 | 2P 30A |  |  | 0 |  | O | OFF | 1A-4-1
1A-2-7 | O | OFF | 0 |  |  |  | 2P 30A | #43 | CF상면 | 보다폰 케이지 안쪽 | #44 | 2P 30A | 0 |  |  |  | O | OFF | 1A-4-2
1A-2-8 | O | OFF |  | 0 |  |  | 2P 30A | #45 | CF상면 | 보다폰 케이지 안쪽 | #46 | 2P 30A |  | 0.62005 |  |  | O | ON | 1A-4-3
1A-2-9 | O | OFF |  |  | 0 |  | 2P 30A | #47 | CF상면 | Vodafone | #48 | 2P 30A |  |  | 1.7327 |  | O | ON | VF Rack#1-상
5F-Q-20 | O | OFF | 0 |  |  |  | 2P 30A | #49 |  | Vodafone | #50 | 2P 30A | 0 |  |  |  | O | ON | VF Rack#2-상
[12 empty] | 합계: | 35.0055 | 39.8719 | 28.4479
5-DaHall 1-PDU-02 |  | PDU : SEL1 - 5-1 - B1 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 34.6 | 35.2 | 26.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0.65712 | 0.73016 |  | O | ON | 보다폰정류기-B
1B-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | CF상면 |  | #02 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-21 / 1B-2-11
1B-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | CF상면 | 구글202-A | #04 | 2P 30A |  | 0 |  |  | O | ON | 1B-2-12
1B-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | CF상면 | 구글201-A | #06 | 2P 30A |  |  | 1.308 |  | O | ON | 1B-2-13
1B-1-4 | O | OFF | 0 |  |  |  | 2P 30A | #07 | CF상면 |  | #08 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-24 / 1B-2-14
G1101 (1B-1-5) | O | ON |  | 10.4156 |  |  | 2P 30A | #09 | cloudflare | 구글Cage 지문인식기 | #10 | 2P 30A |  | 0 |  |  | O | ON | 1B-2-15
G1102 (1B-1-6) | O | ON |  |  | 12.7078 |  | 2P 30A | #11 | cloudflare |  | #12 | 2P 30A |  |  | 0 |  | O | OFF | 1B-3-1
G1103 (1B-1-7) | O | ON | 10.9951 |  |  |  | 2P 30A | #13 | cloudflare |  | #14 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-2
G1104 (1B-1-8) | O | ON |  | 3.0387 |  |  | 2P 30A | #15 | cloudflare |  | #16 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-3
G1105 (1B-1-9) | O | ON |  |  | 3.0577 |  | 2P 30A | #17 | cloudflare |  | #18 | 2P 30A |  |  | 0 |  | O | ON | 1B-3-4
1B-1-10 | O | ON | 0 |  |  |  | 2P 30A | #19 | 구글104-A |  | #20 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-5
1B-1-11 | O | ON |  | 1.6336 |  |  | 2P 30A | #21 | 구글103-A |  | #22 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-6
1B-1-12 | O | ON |  |  | 1.3191 |  | 2P 30A | #23 | 구글102-A |  | #24 | 2P 30A |  |  | 0 |  | O | ON | 1B-3-7
1B-1-13 | O | ON | 0 |  |  |  | 2P 30A | #25 | 구글101-A |  | #26 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-8
1B-1-14 | O | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-9
1B-1-15 | O | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | O | ON | 5F-P-20 / 1B-3-10
G1201 (1A-2-1) | O | ON | 11.5619 |  |  |  | 2P 30A | #31 | cloudflare |  | #32 | 2P 30A | 0 |  |  |  | O | ON | 5F-P-21 / 1B-3-11
G1202 (1B-2-2) | O | ON |  | 11.5925 |  |  | 2P 30A | #33 | cloudflare |  | #34 | 2P 30A |  | 0 |  |  | O | ON | 5F-P-22 / 1B-3-12
G1203 (1B-2-3) | O | ON |  |  | 9.714 |  | 2P 30A | #35 | cloudflare |  | #36 | 2P 30A |  |  | 0 |  | O | ON | 5F-P-23 / 1B-3-13
G1204 (1B-2-4) | O | ON | 11.4477 |  |  |  | 2P 30A | #37 | cloudflare |  | #38 | 2P 30A | 0 |  |  |  | O | ON | 5F-P-24 / 1B-3-14
G1205 (1B-2-5) | O | ON |  | 9.4716 |  |  | 2P 30A | #39 | cloudflare |  | #40 | 2P 30A |  | 0 |  |  | O | OFF | 5F-P-25 / 1B-3-15
1B-2-6 | O | OFF |  |  | 0 |  | 2P 30A | #41 | CF상면 | ?? | #42 | 2P 30A |  |  | 0 |  | O | OFF | 1B-7-1(2)
1B-2-7 | O | OFF | 0 |  |  |  | 2P 30A | #43 | CF상면 |  | #44 | 2P 30A | 0 |  |  |  | O | OFF | 1B-4-2
1B-2-8 | O | OFF |  | 0 |  |  | 2P 30A | #45 | CF상면 | 보다폰 케이지 안쪽 | #46 | 2P 30A |  | 0.63018 |  |  | O | ON | 1B-4-3
1B-2-9 | O | OFF |  |  | 0 |  | 2P 30A | #47 | CF상면 | Vodafone | #48 | 2P 30A |  |  | 1.1048 |  | O | ON | VF Rack#1-하
5F-Q-20 | O | OFF | 0 |  |  |  | 2P 30A | #49 |  | Vodafone | #50 | 2P 30A | 0 |  |  |  | O | ON | VF Rack#2-하
[12 empty] | 합계: | 34.0047 | 37.4394 | 29.9416
5-DaHall 1-PDU-03 |  | PDU : SEL1 - 5-1 - A2 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 26.8 | 15.9 | 18 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0 | 0 |  | X | OFF
5F-O-16 / 2A-4-6 | O | ON | 0 |  |  |  | 2P 30A | #01 |  | KG이니시스 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B221 (R13)-1
5F-O-17 / 2A-4-7 | O | ON |  | 0 |  |  | 2P 30A | #03 |  | KG이니시스 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B221 (R13)-2
5F-O-18 | O | ON |  |  | 0 |  | 2P 30A | #05 |  | KG이니시스 | #06 | 2P 30A |  |  | 0.56762 |  | O | ON | B222 (R14)-1
5F-O-19 | O | ON | 0 |  |  |  | 2P 30A | #07 |  | KG이니시스 | #08 | 2P 30A | 1.4476 |  |  |  | O | ON | B222 (R14)-2
5F-O-20 | O | ON |  | 0 |  |  | 2P 30A | #09 |  | KG이니시스 | #10 | 2P 30A |  | 3.56 |  |  | O | ON | B316 (R15)-1
5F-O-21 | O | ON |  |  | 0 |  | 2P 30A | #11 |  | KG이니시스 | #12 | 2P 30A |  |  | 1.7723 |  | O | ON | B316 (R15)-2
5F-O-22 | O | ON | 0 |  |  |  | 2P 30A | #13 |  | KG이니시스 | #14 | 2P 30A | 0.35264 |  |  |  | O | ON | B317 (R16)-1
5F-O-23 | O | ON |  | 0 |  |  | 2P 30A | #15 |  | KG이니시스 | #16 | 2P 30A |  | 3.9112 |  |  | O | ON | B318 (R17)-1
5F-O-24 | O | ON |  |  | 0 |  | 2P 30A | #17 |  | KG이니시스 | #18 | 2P 30A |  |  | 0.84995 |  | O | ON | B319 (R18)
2A-7-2(2) | X | OFF | 0 |  |  |  | 2P 30A | #19 | ?? | KG이니시스 | #20 | 2P 30A | 2.8169 |  |  |  | O | ON | B320 (R19)
2A-5-1 | O | OFF |  | 0 |  |  | 2P 30A | #21 | 보다폰상면 | KG이니시스 | #22 | 2P 30A |  | 2.8763 |  |  | O | ON | B321 (R20)
2A-5-2 | O | ON |  |  | 0 |  | 2P 30A | #23 | 보다폰상면 | KG이니시스 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B322 (R21)
2A-5-3 | O | ON | 0 |  |  |  | 2P 30A | #25 | 보다폰상면 | KG이니시스 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B416 (R22)
2A-5-4 | O | ON |  | 0 |  |  | 2P 30A | #27 | 보다폰상면 | KG이니시스 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B417 (R23)
2A-5-5 | O | ON |  |  | 0 |  | 2P 30A | #29 |  | KG이니시스 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B418 (R24)
5-1-A2-31 | X | OFF | 0 |  |  |  | 2P 30A | #31 |  | KG이니시스 | #32 | 2P 30A | 2.4823 |  |  |  | O | ON | B116 (R12)
5-1-A2-33 | X | OFF |  | 0 |  |  | 2P 30A | #33 |  | KG이니시스 | #34 | 2P 30A |  | 2.2286 |  |  | O | ON | B117 (R11)
5-1-A2-35 | X | OFF |  |  | 0 |  | 2P 30A | #35 |  | KG이니시스 | #36 | 2P 30A |  |  | 2.1677 |  | O | ON | B118 (R10)
B317 (R16)-2 | O | ON | 3.2319 |  |  |  | 2P 30A | #37 | KG이니시스 | KG이니시스 | #38 | 2P 30A | 2.3507 |  |  |  | O | ON | B119 (R9)
B318 (R17)-2 | O | ON |  | 1.7992 |  |  | 2P 30A | #39 | KG이니시스 | KG이니시스 | #40 | 2P 30A |  | 1.366 |  |  | O | ON | B120 (R8)
B221 (R13)-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | KG이니시스 | KG이니시스 | #42 | 2P 30A |  |  | 1.7853 |  | O | ON | B121 (R7)
B222 (R14)-3 | O | ON | 2.432 |  |  |  | 2P 30A | #43 | KG이니시스 | KG이니시스 | #44 | 2P 30A | 2.9196 |  |  |  | O | ON | B122 (R6)
B316 (R15)-3 | O | ON |  | 0 |  |  | 2P 30A | #45 | KG이니시스 | KG이니시스 | #46 | 2P 30A |  | 2.893 |  |  | O | ON | B216 (R5)
B219 (R2) | O | ON |  |  | 4.0531 |  | 2P 30A | #47 | KG이니시스 | KG이니시스 | #48 | 2P 30A |  |  | 3.6755 |  | O | ON | B217 (R4)
B220 (R1) | O | ON | 5.7896 |  |  |  | 2P 30A | #49 | KG이니시스 | KG이니시스 | #50 | 2P 30A | 4.1026 |  |  |  | O | ON | B218 (R3)
[12 empty] | 합계: | 27.9258 | 18.6343 | 14.8715
5-DaHall 1-PDU-04 |  | PDU : SEL1 - 5-1 - B2 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 25.1 | 15.5 | 18.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| O | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0 | 0 |  | O | OFF
5F-O-16 / 2B-4-6 | O | ON | 0 |  |  |  | 2P 30A | #01 | 철거가능 | KG이니시스 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B221 (R13)-1
5F-O-17 / 2B-4-7 | O | ON |  | 0 |  |  | 2P 30A | #03 | 철거가능 | KG이니시스 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B221 (R13)-2
5F-O-18 | O | ON |  |  | 0 |  | 2P 30A | #05 | 철거가능 | KG이니시스 | #06 | 2P 30A |  |  | 0.56844 |  | O | ON | B222 (R14)-1
5F-O-19 | O | ON | 0 |  |  |  | 2P 30A | #07 | 철거가능 | KG이니시스 | #08 | 2P 30A | 1.7486 |  |  |  | O | ON | B222 (R14)-2
5F-O-20 | O | ON |  | 0 |  |  | 2P 30A | #09 | 철거가능 | KG이니시스 | #10 | 2P 30A |  | 3.5361 |  |  | O | ON | B316 (R15)-1
5F-O-21 | O | ON |  |  | 0 |  | 2P 30A | #11 | 철거가능 | KG이니시스 | #12 | 2P 30A |  |  | 1.8126 |  | O | ON | B316 (R15)-2
5F-O-22 | O | ON | 0 |  |  |  | 2P 30A | #13 | 철거가능 | KG이니시스 | #14 | 2P 30A | 0.65122 |  |  |  | O | ON | B317 (R16)-1
5F-O-23 | O | ON |  | 0 |  |  | 2P 30A | #15 | 철거가능 | KG이니시스 | #16 | 2P 30A |  | 3.8372 |  |  | O | ON | B318 (R17)-1
5F-O-24 | O | ON |  |  | 0 |  | 2P 30A | #17 | 철거가능 | KG이니시스 | #18 | 2P 30A |  |  | 0.85023 |  | O | ON | B319 (R18)
2B-7-2(2) | O | OFF | 0 |  |  |  | 2P 30A | #19 | ?? | KG이니시스 | #20 | 2P 30A | 1.8217 |  |  |  | O | ON | B320 (R19)
2B-5-1 | O | OFF |  | 0 |  |  | 2P 30A | #21 | 보다폰상면 | KG이니시스 | #22 | 2P 30A |  | 3.0523 |  |  | O | ON | B321 (R20)
2B-5-2 | O | ON |  |  | 0 |  | 2P 30A | #23 | 보다폰상면 | KG이니시스 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B322 (R21)
2B-5-3 | O | ON | 0 |  |  |  | 2P 30A | #25 | 보다폰상면 | KG이니시스 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B416 (R22)
2B-5-4 | O | ON |  | 0 |  |  | 2P 30A | #27 | 보다폰상면 | KG이니시스 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B417 (R23)
2B-5-5 | O | ON |  |  | 0 |  | 2P 30A | #29 | 철거필요 | KG이니시스 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B418 (R24)
| X | OFF | 0 |  |  |  | 2P 30A | #31 | 철거필요 | KG이니시스 | #32 | 2P 30A | 0.27073 |  |  |  | O | ON | B116 (R12)
| X | OFF |  | 0 |  |  | 2P 30A | #33 | 철거필요 | KG이니시스 | #34 | 2P 30A |  | 0.28991 |  |  | O | ON | B117 (R11)
| X | OFF |  |  | 0 |  | 2P 30A | #35 | 철거가능 | KG이니시스 | #36 | 2P 30A |  |  | 2.2841 |  | O | ON | B118 (R10)
B317 (R16)-2 | O | ON | 3.9333 |  |  |  | 2P 30A | #37 | KG이니시스 | KG이니시스 | #38 | 2P 30A | 2.759 |  |  |  | O | ON | B119 (R9)
B318 (R17)-2 | O | ON |  | 1.2236 |  |  | 2P 30A | #39 | KG이니시스 | KG이니시스 | #40 | 2P 30A |  | 1.4517 |  |  | O | ON | B120 (R8)
B221 (R13)-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | KG이니시스 | KG이니시스 | #42 | 2P 30A |  |  | 1.582 |  | O | ON | B121 (R7)
B222 (R14)-3 | O | ON | 2.4836 |  |  |  | 2P 30A | #43 | KG이니시스 | KG이니시스 | #44 | 2P 30A | 2.3193 |  |  |  | O | ON | B122 (R6)
B316 (R15)-3 | O | ON |  | 0 |  |  | 2P 30A | #45 | KG이니시스 | KG이니시스 | #46 | 2P 30A |  | 2.3497 |  |  | O | ON | B216 (R5)
B219 (R2) | O | ON |  |  | 4.4097 |  | 2P 30A | #47 | KG이니시스 | KG이니시스 | #48 | 2P 30A |  |  | 3.1896 |  | O | ON | B217 (R4)
B220 (R1) | O | ON | 5.5645 |  |  |  | 2P 30A | #49 | KG이니시스 | KG이니시스 | #50 | 2P 30A | 3.9358 |  |  |  | O | ON | B218 (R3)
[12 empty] | 합계: | 25.4878 | 15.7406 | 14.6967
PDU6B-1T |  | PDU : | [6 empty] | Main CB 4P 150A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A |  |  |  |  | X | OFF
1T-1-3 | O | OFF |  |  |  |  | 3P 30A | #03 | CF상면 | . | #04 | 3P 30A |  |  |  |  | O | OFF | 1T-4-3
1T-1-6 | O | OFF |  |  |  |  | 3P 30A | #05 | CF상면 | . | #06 | 3P 30A |  |  |  |  | O | OFF | 1T-4-6
1T-1A9 | O | OFF |  |  |  |  | 3P 30A | #07 | . | . | #08 | 3P 30A |  |  |  |  | O | OFF | 1T-4-9
1T-1-12 | O | OFF |  |  |  |  | 3P 30A | #09 | Google상면 | . | #10 | 3P 30A |  |  |  |  | O | OFF | 1T-4-12
1T-2-3 | O | OFF |  |  |  |  | 3P 30A | #11 | CF상면 | . | #12 | 3P 20A |  |  |  |  | O | OFF | 1T-5-3
1T-2-6 | O | OFF |  |  |  |  | 3P 20A | #13 | . | . | #14 | 3P 20A |  |  |  |  | O | OFF | 1T-5-6
1T-2-9 | O | OFF |  |  |  |  | 3P 20A | #15 | . | . | #16 | 3P 20A |  |  |  |  | O | OFF | 1T-5-9
1T-2-12 | O | OFF |  |  |  |  | 3P 20A | #17 | Google상면 | . | #18 | 3P 20A |  |  |  |  | O | OFF | 1T-5-12
1T-3-3 | O | OFF |  |  |  |  | 3P 20A | #19 | . | . | #20 | 3P 20A |  |  |  |  | O | OFF | 1T-6-2
1T-3-6 | O | OFF |  |  |  |  | 3P 20A | #21 | . | . | #22 | 3P 20A |  |  |  |  | O | OFF | 1T-6-4
1T-3-9 | O | OFF |  |  |  |  | 3P 20A | #23 | . | . | #24 | 3P 20A |  |  |  |  | X | OFF
1T-3-12 | O | OFF |  |  |  |  | 3P 20A | #25 | . | . | #26 | 3P 20A |  |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-05 |  | PDU : SEL1 - 5-1 - A3 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  | 0 |  | 2P 30A | #01 |  |  | #02 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #03 |  |  | #04 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #13 |  |  | #14 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #19 |  |  | #20 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-2
| X | OFF |  | 0 |  |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-3
| X | OFF |  |  | 0 |  | 2P 30A | #25 |  |  | #26 | 2P 30A |  |  | 0 |  | O | OFF | 3A-12-3T
| X | OFF | 0 |  |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-4
| X | OFF |  | 0 |  |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-5
| X | OFF |  |  | 0 |  | 2P 30A | #31 |  |  | #32 | 2P 30A |  |  | 0 |  | O | OFF | 3A-12-6
| X | OFF | 0 |  |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-7
| X | OFF |  | 0 |  |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-8
| X | OFF |  |  | 0 |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #43 |  |  | #44 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-06 |  | PDU : SEL1 - 5-1 - B3 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  | 0 |  | 2P 30A | #01 |  |  | #02 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #03 |  |  | #04 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #13 |  |  | #14 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #19 |  |  | #20 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A | 0 |  |  |  | O | OFF | 3B-12-2
| X | OFF |  | 0 |  |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  | 0 |  |  | O | OFF | 3B-12-3
| X | OFF |  |  | 0 |  | 2P 30A | #25 |  |  | #26 | 2P 30A |  |  | 0 |  | O | OFF | 3B-12-4
| X | OFF | 0 |  |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A | 0 |  |  |  | O | OFF | 3B-12-5
| X | OFF |  | 0 |  |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  | 0 |  |  | O | OFF | 3B-12-6
| X | OFF |  |  | 0 |  | 2P 30A | #31 |  |  | #32 | 2P 30A |  |  | 0 |  | O | OFF | 3B-12-6T
| X | OFF | 0 |  |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A | 0 |  |  |  | O | OFF | 3B-12-7
| X | OFF |  | 0 |  |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  | 0 |  |  | O | OFF | 3B-12-8
| X | OFF |  |  | 0 |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #43 |  |  | #44 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-07 |  | PDU : SEL1 - 5-1 - A4 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 8.6 | 1.1 | 0.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
9A-1-5 (PCCW) /5F-A-14 | O | ON | 7.8089 |  |  |  | 3P 30A | #01 | PCCW | 센츄리링크코리아 | #02 | 3P 30A | 1.0019 |  |  |  | O | ON | 9A-1-8 / 5F-A-17
9A-1-6 / 5F-A-15 | O | ON |  | 1.2814 |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A |  | 0 |  |  | O | ON | 9A-1-9 / 5F-A-18
9A-1-7 / 5F-A-16 | O | ON |  |  | 0.4 |  | 3P 30A | #05 | PCCW | 세종 인터넷(IES.YSM.S51) | #06 | 3P 30A |  |  | 0.37117 |  | O | ON | 9A-1-10 / 5F-A-19
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #09 |  |  | #10 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 8.8108 | 1.2814 | 0.77117
5-DaHall 1-PDU-09 |  | PDU : SEL1 - 5-1 - A5 | [6 empty] | Main CB 4P 200A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #03 |  |  | #04 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #09 |  |  | #10 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #37 |  |  | #38 | 3P 20A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-08 |  | PDU : SEL1 - 5-1 - B4 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 6.5 | 1.4 | 1.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01 | 코로케션 | 센츄리링크코리아 | #02 | 3P 30A | 1.1675 |  |  |  | O | ON | 9B-1-8 / 5F-A-17
9B-1-6 / 5F-A-15 | O | ON |  | 1.4019 |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A |  | 0 |  |  | O | ON | 9B-1-9 / 5F-A-18
9B-1-7 / 5F-A-16 | O | ON |  |  | 0 |  | 3P 30A | #05 | PCCW | 세종 인터넷(IES.YSM.S51) | #06 | 3P 30A |  |  | 1.35 |  | O | ON | 9B-1-10 / 5F-A-19
9B-1-5 (PCCW)/5F-A-14 | O | ON | 5.3639 |  |  |  | 3P 30A | #07 | PCCW |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #09 |  |  | #10 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| O | ON |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 6.5314 | 1.4019 | 1.35
5-DaHall 1-PDU-10 |  | PDU : SEL1 - 5-1 - B5 | [6 empty] | Main CB 4P 200A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #03 |  |  | #04 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #09 |  |  | #10 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #37 |  |  | #38 | 3P 20A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-11 |  | PDU : SEL1 - 5-1 - A6 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 15.3 | 10.2 | 9.9 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
1A-1-1 / 5F-A-10 | O | ON | 0 |  |  |  | 3P 30A | #03 | 코로케션 |  | #04 | 3P 30A | 0 |  |  |  | O | OFF | A1-3-2
1A-1-2 / 5F-A-11 | O | ON |  | 0 |  |  | 3P 30A | #05 | 코로케션 | 코로케션 | #06 | 3P 30A |  | 2.0275 |  |  | O | ON | A1-3-3
1A-1-2(2) | O | ON |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 20A |  |  | 0 |  | O | ON | A1-3-4
1A-1-3 / 5F-A-12 | O | ON | 5.2395 |  |  |  | 3P 30A | #09 | PCCW | 코로케션 | #10 | 3P 20A | 0 |  |  |  | O | ON | A1-3-5
1A-1-4 / 5F-A-13 | O | ON |  | 0 |  |  | 3P 30A | #11 | PCCW | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | A1-3-6
1A-1-4(2) / 5F-A-13 (2) | O | ON |  |  | 1.9565 |  | 3P 30A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 0 |  | O | ON | A1-3-7
A1-2-1 / 5F-B-10 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 0 |  |  |  | O | ON | A1-3-8
A1-2-2 / 5F-B-11 | O | ON |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 3.0799 |  |  | O | ON | A1-3-9
A1-2-3 / 5F-B-12 | O | OFF |  |  | 0 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 2.9135 |  | O | ON | A1-3-10
A1-2-4 / 5F-B-13 | O | ON | 2.554 |  |  |  | 3P 20A | #21 | 다코스 |  | #22 | 3P 20A | 0 |  |  |  | O | ON | A807 / 5F-D-16 / A1-4-7(2)
A1-2-5 / A605 (A) | O | ON |  | 4.9109 |  |  | 3P 20A | #23 | 이비즈네트웍스 | PCCW | #24 | 3P 20A |  | 0 |  |  | O | ON | A1-5-10(2) / 5F-E-19
A1-2-6 / 5F-B-15 | O | ON |  |  | 0 |  | 3P 20A | #25 | 다코스 & NTT | PCCW | #26 | 3P 20A |  |  | 5.4676 |  | O | ON | A1-1-3(2) / 5F-A-12(2)
A1-2-7 / 5F-B-16 | O | ON | 2.6574 |  |  |  | 3P 20A | #27 | 제우스네트웍스 |  | #28 | 3P 20A | 5.4329 |  |  |  | O | ON | A1-1-8(2) / 5F-A-17 (2)
A1-2-8 / 5F-B-17 | O | ON |  | 0 |  |  | 3P 20A | #29 | COLT |  | #30 | 3P 20A |  | 0 |  |  | O | ON | 5F-D-18 임시
A1-3-1 | O | OFF |  |  | 0 |  | 3P 20A | #31 |  | 코로케션 | #32 | 3P 20A |  |  | 0 |  | O | ON
[12 empty] | 합계: | 15.8838 | 10.0183 | 10.3376
5-DaHall 1-PDU-13 |  | PDU : SEL1 - 5-1 - A7 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 12 | 18.7 | 14.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
A2-2-9 / 5F-B-18 | O | ON | 5.6571 |  |  |  | 3P 30A | #03 | 코로케션 | 코로케션 | #04 | 3P 30A | 0 |  |  |  | O | ON | A2-5-4
A2-2-10 / 5F-B-19 | O | ON |  | 3.9416 |  |  | 3P 30A | #05 | PCCW | 코로케션 | #06 | 3P 30A |  | 5.8641 |  |  | O | ON | A2-5-5
A2-4-1 | O | ON |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 4.2161 |  | O | ON | A2-5-6
A2-4-2 | O | ON | 0 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 30A | 0 |  |  |  | O | ON | A2-5-7
A2-4-3 | O | ON |  | 0 |  |  | 3P 20A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | A2-5-8
A2-4-4 | O | ON |  |  | 0.70734 |  | 3P 20A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 0 |  | O | ON | A2-5-9
A2-4-5 / 5F-D-14 | O | ON | 0 |  |  |  | 3P 20A | #15 | PCCW | PCCW | #16 | 3P 20A | 3.8811 |  |  |  | O | ON | A2-5-10 / 5F-E-19
A2-4-6 / 5F-D-15 | O | ON |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 0 |  |  | O | OFF | A2-6-1
A2-4-7 | O | ON |  |  | 5.2271 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 0 |  | O | OFF | A2-6-2
A2-4-8 | O | ON | 3.2932 |  |  |  | 3P 20A | #21 | 코로케션 | 코로케션 | #22 | 3P 20A | 0 |  |  |  | O | OFF | A2-6-3
A2-4-9 | O | ON |  | 9.0422 |  |  | 3P 20A | #23 | 코로케션 | 코로케션 | #24 | 3P 20A |  | 0 |  |  | O | OFF | A2-6-4
A2-4-10 | O | ON |  |  | 2.4993 |  | 3P 20A | #25 | 코로케션 | 코로케션 | #26 | 3P 20A |  |  | 1.8758 |  | O | ON | A2-6-5 / F-14
A2-5-1 | O | ON | 0 |  |  |  | 3P 20A | #27 | 코로케션 | 코로케션 | #28 | 3P 20A | 0 |  |  |  | O | OFF | A2-6-6 / F-15
A2-5-2 | O | ON |  | 0 |  |  | 3P 20A | #29 | 코로케션 | 코로케션 | #30 | 3P 20A |  | 0 |  |  | O | OFF | A2-6-7 / F-16
A2-5-3 | O | ON |  |  | 0 |  | 3P 20A | #31 | 코로케션 | 코로케션 | #32 | 3P 20A |  |  | 0 |  | O | ON | A2-6-8 / F-17
[12 empty] | 합계: | 12.8314 | 18.848 | 14.5257
5-DaHall 1-PDU-15 |  | PDU : SEL1 - 5-1 - A8 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 19.1 | 6.2 | 14.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
AC PDU-3#A | O | ON | 6.0238 | 1.2489 | 7.9433 |  | 3P 50A | #01(3상) | 텔스트라 | 텔스트라 | #02(3상) | 3P 50A | 3.391 | 2.7951 | 1.9974 |  | O | ON | TO:PDU(A)-3A
| X | OFF | 0 | 0 | 0 |  | 3P 50A | #03(3상) |  | Singtel-1 | #04(3상) | 3P 50A | 0 | 0 | 0 |  | X | OFF | DC정류기A
TRANSDUSER | O | OFF | 0 | 0 | 0 |  | 3P 30A | #05(3상) |  |  | #06(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF | customer con
PUD(A)-3-07 / 5F-B-17 (2) | O | ON | 3.7956 |  |  |  | 3P 30A | #07 | COLT |  | #08 | 3P 30A | 4.3115 |  |  |  | O | ON | A1007 / 5F-F-16
PUD(A)-3-09 / 5F-B-17 (3) | O | ON |  | 1.7567 |  |  | 3P 30A | #09 | COLT |  | #10 | 3P 30A |  | 6.7601 |  |  | O | OFF | A1006 / 5F-F-15
A603 / Colt, A-1 (23/08/23 On) | O | ON |  |  | 0 |  | 3P 30A | #11 |  | CMI | #12 | 3P 30A |  |  | 2.312 |  | O | ON | D-15랙(CMI)-A ('21.09.29 투입)
P여(A)-3 싱텔 SKB CWDM A전원 | O | ON | 0.61654 |  |  |  | 3P 30A | #13 |  |  | #14 | 3P 30A | 1.5793 |  |  |  | O | ON | A603 / Colt, 정류기A (23/08/23 On)
PUD(A)-2-15 | X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
PUD(A)-2-17 | X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
PUD(A)-2-19 | X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
PUD(A)-2-21 | X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
PUD(A)-2-23 | O | ON |  |  | 2.3094 |  | 3P 20A | #23 | Singtel-2 |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
DACOM EOS | X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
PUD(A)-2-27 | X | OFF |  | 0 |  |  | 3P 20A | #27 |  | 다코스 & NTT | #28 | 3P 20A |  | 0.71001 |  |  | O | ON | A3-2-6(2) / 5F-B-15 (2)
PUD(A)-2-29 | O | ON |  |  | 0.36265 |  | 3P 20A | #29 | Singtel-2 |  | #30 | 3P 20A |  |  | 0 |  | X | OFF | TNSI A
[12 empty] | 합계: | 19.7178 | 13.2707 | 14.9248
5-DaHall 1-PDU-12 |  | PDU : SEL1 - 5-1 - B6 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 20.1 | 13.1 | 14 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
1B-1-1 / 5F-A-10 | O | ON | 0 |  |  |  | 3P 30A | #03 | 코로케션 | 코로케션 | #04 | 3P 30A | 1.9205 |  |  |  | O | ON | B1-3-3
1B-1-2 / 5F-A-11 | O | ON |  | 0 |  |  | 3P 30A | #05 | PCCW | 코로케션 | #06 | 3P 30A |  | 0 |  |  | O | ON | B1-3-4
| X | OFF |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 0 |  | O | ON | B1-3-5
1B-1-4 / 5F-A-13 | O | ON | 2.9366 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 20A | 0 |  |  |  | O | ON | B1-3-6
1B-1-4(2) / 5F-A-13 (2) | O | ON |  | 0 |  |  | 3P 30A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | B1-3-7
B1-2-1 / 5F-B-10 | O | ON |  |  | 0 |  | 3P 20A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 0 |  | O | ON | B1-3-8
B1-2-2 / 5F-B-11 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 6.1695 |  |  |  | O | ON | B1-3-9
B1-2-3 / 5F-B-12 | O | OFF |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 3.6126 |  |  | O | ON | B1-3-10
B1-2-4 / 5F-B-13 | O | ON |  |  | 2.9717 |  | 3P 20A | #19 | 다코스 |  | #20 | 3P 20A |  |  | 0 |  | X | OFF
B1-2-5 / A605 (B) | O | ON | 4.5562 |  |  |  | 3P 20A | #21 | 이비즈네트웍스 |  | #22 | 3P 20A | 0 |  |  |  | X | OFF | A807 / 5F-D-16 / B1-4-7(2)
B1-2-6 / 5F-B-15 | O | ON |  | 0 |  |  | 3P 20A | #23 | 다코스 & NTT | PCCW | #24 | 3P 20A |  | 3.5013 |  |  | O | ON | B1-5-10(2) / 5F-E-19
B1-2-7 / 5F-B-16 | O | ON |  |  | 3.4098 |  | 3P 20A | #25 | 제우스네트웍스 | PCCW | #26 | 3P 20A |  |  | 5.0065 |  | O | ON | 1B-1-3 / 5F-A-12
B1-2-8 / 5F-B-17 | O | ON | 0 |  |  |  | 3P 20A | #27 | COLT |  | #28 | 3P 20A | 5.806 |  |  |  | O | ON | B1-1-8(2) / 5F-A-17 (2)
B1-3-1 | O | ON |  | 0 |  |  | 3P 20A | #29 | 코로케션 | PCCW | #30 | 3P 20A |  | 6.5079 |  |  | X | ON | B1-1-3(2) / 5F-A-12 (2)
B1-3-2 | O | OFF |  |  | 0 |  | 3P 20A | #31 | 코로케션 | 코로케션 | #32 | 3P 20A |  |  | 3.0076 |  | O | ON | B1-2-9 / 5F-B-18
[12 empty] | 합계: | 21.3888 | 13.6218 | 14.3956
5-DaHall 1-PDU-14 |  | PDU : SEL1 - 5-1 - B7 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 13.4 | 11.6 | 7.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
B2-2-10 / 5F-B-19 | O | ON | 3.2547 |  |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A | 7.0524 |  |  |  | O | ON | B2-5-5
B2-4-1 | O | ON |  | 0 |  |  | 3P 30A | #05 | 코로케션 | 코로케션 | #06 | 3P 30A |  | 2.8166 |  |  | O | ON | B2-5-6
B2-4-2 | O | ON |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 0 |  | O | ON | B2-5-7
B2-4-3 | O | OFF | 0 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 30A | 0 |  |  |  | O | ON | B2-5-8
B2-4-4 | O | ON |  | 0 |  |  | 3P 20A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | B2-5-9
B2-4-5 / 5F-D-14 | O | ON |  |  | 1.7295 |  | 3P 20A | #13 | PCCW | PCCW | #14 | 3P 20A |  |  | 3.2013 |  | O | ON | B2-5-10 / 5F-E-19
B2-4-6 / 5F-D-15 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 0 |  |  |  | O | OFF | B2-6-1
B2-4-7 | O | ON |  | 0.96051 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 0 |  |  | O | OFF | B2-6-2
B2-4-8 | O | ON |  |  | 2.5462 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 0 |  | O | OFF | B2-6-3
B2-4-9 | O | ON | 3.403 |  |  |  | 3P 20A | #21 | 코로케션 | 코로케션 | #22 | 3P 20A | 0 |  |  |  | O | OFF | B2-6-4
B2-4-10 | O | ON |  | 2.5495 |  |  | 3P 20A | #23 | 코로케션 | 코로케션 | #24 | 3P 20A |  | 5.0704 |  |  | O | ON | B2-6-5 / F-14
B2-5-1 | O | ON |  |  | 0 |  | 3P 20A | #25 | 코로케션 | 코로케션 | #26 | 3P 20A |  |  | 0 |  | O | OFF | B2-6-6 / F-15
B2-5-2 | O | ON | 0 |  |  |  | 3P 20A | #27 | 코로케션 | 코로케션 | #28 | 3P 20A | 0 |  |  |  | O | OFF | B2-6-7 / F-16
B2-5-3 | O | ON |  | 0 |  |  | 3P 20A | #29 | 코로케션 | 코로케션 | #30 | 3P 20A |  | 0 |  |  | O | ON | B2-6-8 / F-17
B2-5-4 | O | ON |  |  | 0 |  | 3P 20A | #31 | 코로케션 |  | #32 | 3P 20A |  |  | 0 |  | O | ON | FMS 5층 메인전원
[12 empty] | 합계: | 13.7101 | 11.3969 | 7.477
5-DaHall 1-PDU-16 |  | PDU : SEL1 - 5-1 - B8 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 20.1 | 11.1 | 16 | <- 실측값 |  |  | <- 디스플래이값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
AC PDU-3#B | O | ON | 4.7003 | 1.3374 | 6.0648 |  | 3P 50A | #01(3상) | 텔스트라 | 텔스트라 | #02(3상) | 3P 50A | 3.1513 | 3.1408 | 1.8705 |  | O | ON | TO:PDU(B)-3A
| X | OFF | 0 | 0 | 0 |  | 3P 50A | #03(3상) |  | Singtel-1 | #04(3상) | 3P 50A | 0 | 0 | 0 |  | X | OFF | DC정류기B
TRANSDUSER | X | OFF | 0 | 0 | 0 |  | 3P 30A | #05(3상) |  |  | #06(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF | customer con
PUD(B)-3-07 / 5F-B-17 (2) | O | ON | 4.01 |  |  |  | 3P 30A | #07 | COLT |  | #08 | 3P 30A | 4.877 |  |  |  | O | ON | A1007 / 5F-F-16
PUD(B)-3-09 / 5F-B-17 (3) | O | ON |  | 1.8033 |  |  | 3P 30A | #09 | COLT |  | #10 | 3P 30A |  | 0.99968 |  |  | X | OFF | A1006 / 5F-F-15
A603 / Colt, B-1 (23/08/23 On) | O | ON |  |  | 0 |  | 3P 30A | #11 |  | CMI | #12 | 3P 30A |  |  | 2.5684 |  | O | ON | D-15랙(CMI)-B ('21.09.29 투입)
P여(B)-3 싱텔 SKB CWDM B전원 | O | ON | 1.6658 |  |  |  | 3P 30A | #13 |  |  | #14 | 3P 30A | 1.7262 |  |  |  | O | ON | A603 / Colt, 정류기B (23/08/23 On)
KT Rack #2 (소형 임시정류기) | O | ON |  | 2.4403 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
KT Rack #3 (소형 임시정류기) | O | ON |  |  | 1.5901 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
KT Rack #4 (소형 임시정류기) | O | ON | 0 |  |  |  | 3P 20A | #19 |  | 4F BMS | #20 | 3P 20A | 0.59852 |  |  |  | O | ON | 신규 BMS(4F TPS실) Rack
텔스트라 CCTV 모니터링PC 및 시스템 박스 | O | ON |  | 0.29432 |  |  | 3P 20A | #21 |  | 5F BMS | #22 | 3P 20A |  | 0.58994 |  |  | O | ON | 신규 BMS(5F TPS실) Rack
DACOM EOS | O | ON |  |  | 0 |  | 3P 20A | #23 | Singtel-2 | Singtel-2 | #24 | 3P 20A |  |  | 1.4604 |  | O | ON | kt mspp 전원
| O | ON | 0.42399 |  |  |  | 3P 20A | #25 | Singtel-2 |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
SKB2.5G전용 PDU B3 27 | O | ON |  | 1.4873 |  |  | 3P 20A | #27 | Singtel-2 | 다코스 & NTT | #28 | 3P 20A |  | 0.29488 |  |  | O | ON | B3-2-6(2) / 5F-B-15 (2)
데이콤 AC전원 | O | ON |  |  | 2.2198 |  | 3P 20A | #29 | Singtel-2 | Singtel-2 | #30 | 3P 20A |  |  | 0.49261 |  | O | ON | TNSI A
[12 empty] | 합계: | 21.1531 | 12.3878 | 16.2666
PDU(C) | [8 empty] | Main CB 4P 50A
[12 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  |  |  | 3P 50A | #01(3상) |  |  | #02(3상) | 3P 50A |  |  |  |  | X | OFF
라우터룸 System box | O | ON |  |  |  |  | 3P 30A | #03(3상) | Singtel-2 |  | #04(3상) | 3P 30A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  |  |  | X | OFF
SYSTEM BOX | X | OFF |  |  |  |  | 3P 30A | #07 |  | Singtel-2 | #08 | 3P 30A |  |  |  |  | O | ON | SYSTEM BOX
customer con | X | OFF |  |  |  |  | 3P 20A | #09 |  | Singtel-2 | #10 | 3P 20A |  |  |  |  | O | ON | SYSTEM BOX
SYSTEM BOX | O | ON |  |  |  |  | 3P 20A | #11 | Singtel-2 |  | #12 | 3P 20A |  |  |  |  | X | OFF | customer con
| O | OFF |  |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A |  |  |  |  | X | OFF | customer con
M/S 단파 | O | ON |  |  |  |  | 3P 20A | #15 | Singtel-2 |  | #16 | 3P 20A |  |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-17 |  | PDU : SEL1 - 5-1 - A9 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 5.5 | 7.2 | 2.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RT-07 | ○ | ON | 0.71105 |  |  |  | 2P 30A | #01 | U08-A-01 | U08-A-02 | #02 | 2P 30A | 0.83544 |  |  |  | ○ | ON | RT-08
RT-09 | ○ | ON |  | 0 |  |  | 2P 30A | #03 | U08-A-03 | U08-A-04 | #04 | 2P 30A |  | 0 |  |  | ○ | ON | RT-10
RT-11 | ○ | ON |  |  | 0 |  | 2P 30A | #05 | U08-A-05 | U08-A-06 | #06 | 2P 30A |  |  | 0 |  | ○ | ON | RT-12
RT-13 | ○ | ON | 0 |  |  |  | 2P 30A | #07 | U08-A-07 | U08-A-08 | #08 | 2P 30A | 2.2542 |  |  |  | ○ | ON | RT-14
RT-15 | ○ | ON |  | 7.2041 |  |  | 2P 30A | #09 | U08-A-09 | U08-A-10 | #10 | 2P 30A |  | 0 |  |  | ○ | ON | RT-16
RT-17 | ○ | ON |  |  | 0.53 |  | 2P 30A | #11 | U08-A-11 | U08-A-12 | #12 | 2P 30A |  |  | 1.1137 |  | ○ | ON | RT-18
RT-19 | ○ | ON | 0 |  |  |  | 2P 30A | #13 | U08-A-13 | U08-A-14 | #14 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-01
LSP-02 | ○ | OFF |  | 0 |  |  | 2P 30A | #15 | U08-A-15 | U08-A-16 | #16 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-03
LSP-04 | ○ | ON |  |  | 0.75576 |  | 2P 30A | #17 | U08-A-17 | U08-A-18 | #18 | 2P 30A |  |  | 0 |  | ○ | OFF | LSP-05
LSP-06 | ○ | OFF | 0 |  |  |  | 2P 30A | #19 | U08-A-19 | U08-A-20 | #20 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-07
LSP-08 | ○ | OFF |  | 0 |  |  | 2P 30A | #21 | U08-A-21 | U08-A-22 | #22 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-09
LSP-10 | ○ | OFF |  |  | 0 |  | 2P 30A | #23 | U08-A-23 | U08-A-24 | #24 | 2P 30A |  |  | 0 |  | ○ | ON | MT-06
RT-08 정류기 | ○ | ON | 1.8193 |  |  |  | 2P 30A | #25 | U08-A-25 |  | #26 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 5.62 | 7.2041 | 2.3994
5-DaHall 1-PDU-18 |  | PDU : SEL1 - 5-1 - B9 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 4.6 | 5 | 1.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RT-07 | ○ | ON | 0.82156 |  |  |  | 2P 30A | #01 | U08-B-01 | U08-B-02 | #02 | 2P 30A | 0.77978 |  |  |  | ○ | ON | RT-08
RT-09 | ○ | ON |  | 0 |  |  | 2P 30A | #03 | U08-B-03 | U08-B-04 | #04 | 2P 30A |  | 0 |  |  | ○ | ON | RT-10
RT-11 | ○ | ON |  |  | 0 |  | 2P 30A | #05 | U08-B-05 | U08-B-06 | #06 | 2P 30A |  |  | 0 |  | ○ | ON | RT-12
RT-13 | ○ | ON | 0 |  |  |  | 2P 30A | #07 | U08-B-07 | U08-B-08 | #08 | 2P 30A | 2.1771 |  |  |  | ○ | ON | RT-14
RT-15 | ○ | ON |  | 5.0029 |  |  | 2P 30A | #09 | U08-B-09 | U08-B-10 | #10 | 2P 30A |  | 0 |  |  | ○ | ON | RT-16
RT-17 | ○ | ON |  |  | 0.41774 |  | 2P 30A | #11 | U08-B-11 | U08-B-12 | #12 | 2P 30A |  |  | 0.80779 |  | ○ | ON | RT-18
RT-19 | ○ | ON | 0 |  |  |  | 2P 30A | #13 | U08-B-13 | U08-B-14 | #14 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-01
LSP-02 | ○ | OFF |  | 0 |  |  | 2P 30A | #15 | U08-B-15 | U08-B-16 | #16 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-03
LSP-04 | ○ | OFF |  |  | 0 |  | 2P 30A | #17 | U08-B-17 | U08-B-18 | #18 | 2P 30A |  |  | 0 |  | ○ | OFF | LSP-05
LSP-06 | ○ | OFF | 0 |  |  |  | 2P 30A | #19 | U08-B-19 | U08-B-20 | #20 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-07
LSP-08 | ○ | OFF |  | 0 |  |  | 2P 30A | #21 | U08-B-21 | U08-B-22 | #22 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-09
LSP-10 | ○ | OFF |  |  | 0 |  | 2P 30A | #23 | U08-B-23 | U08-B-24 | #24 | 2P 30A |  |  | 0 |  | ○ | ON | 시로코팬
RT-08 정류기 | ○ | ON | 1.0102 |  |  |  | 2P 30A | #25 | U08-B-25 |  | #26 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 4.7887 | 5.0029 | 1.2255
5-DaHall 1-PDU-19 |  | PDU : SEL1 - 5-1 - A10 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 35.1 | 38.9 | 22.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-1 | ○ | ON | 3.9418 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 5.3191 |  |  |  | ○ | ON | RTX Rack#8, R3-1-1
RTX Rack#2, R1-2-1 | ○ | ON |  | 5.3769 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 4.9033 |  |  | ○ | ON | RTX Rack#9, R3-2-1
RTX Rack#3, R1-3-1 | ○ | ON |  |  | 0 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 2.9076 |  | ○ | ON | NW/Mgmt Rack, R3-3-1
RTX Rack#4, R2-1-1 | ○ | ON | 7.7593 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 5.7051 |  |  |  | ○ | ON | A40 Rack#1, R4-1-1
RTX Rack#5, R2-2-1 | ○ | ON |  | 5.6386 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 5.9452 |  |  | ○ | ON | A40 Rack#2, R4-2-1
RTX Rack#6, R2-3-1 | ○ | ON |  |  | 5.1847 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 4.0221 |  | ○ | ON | NetApp FAS#1, R4-3-1
RTX Rack#7, R2-4-1 | ○ | ON | 5.4222 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 1.459 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-1
DGX Rack#1, R5-1-1 | ○ | ON |  | 6.0915 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 8.4182 |  |  | ○ | OFF | 예비Rack#1, R6-1-1
DGX Rack#2, R5-2-1 | ○ | ON |  |  | 3.5638 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 5.7545 |  | ○ | OFF | 예비Rack#2, R6-2-1
DGX Rack#3, R5-3-1 | ○ | ON | 3.357 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 9.1726 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-1
| X | OFF |  | 0 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 8.3185 |  |  | ○ | OFF | 예비Rack#4, R6-4-1
| X | OFF |  |  | 4.093 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 42.1361 | 44.6923 | 25.5256
5-DaHall 1-PDU-20 |  | PDU : SEL1 - 5-1 - B10 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 28.1 | 32.6 | 23.1 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-2 | ○ | ON | 5.046 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 5.5928 |  |  |  | ○ | ON | RTX Rack#8, R3-1-2
RTX Rack#2, R1-2-2 | ○ | ON |  | 5.4173 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 4.7785 |  |  | ○ | ON | RTX Rack#9, R3-2-2
RTX Rack#3, R1-3-2 | ○ | ON |  |  | 0 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 1.907 |  | ○ | ON | NW/Mgmt Rack, R3-3-2
RTX Rack#4, R2-1-2 | ○ | ON | 8.0418 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 5.8267 |  |  |  | ○ | ON | A40 Rack#1, R4-1-2
RTX Rack#5, R2-2-2 | ○ | ON |  | 5.5045 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 5.8635 |  |  | ○ | ON | A40 Rack#2, R4-2-2
RTX Rack#6, R2-3-2 | ○ | ON |  |  | 4.603 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 3.9181 |  | ○ | ON | NetApp FAS#1, R4-3-2
RTX Rack#7, R2-4-2 | ○ | ON | 5.0315 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 1.3219 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-2
DGX Rack#1, R5-1-2 | ○ | ON |  | 7.227 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 8.5019 |  |  | ○ | OFF | 예비Rack#1, R6-1-2
DGX Rack#2, R5-2-2 | ○ | ON |  |  | 3.9291 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 5.5659 |  | ○ | OFF | 예비Rack#2, R6-2-2
DGX Rack#3, R5-3-2 | ○ | ON | 3.3922 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 1.977 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-2
| X | OFF |  | 0 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 1.1197 |  |  | ○ | OFF | 예비Rack#4, R6-4-2
| X | OFF |  |  | 4.2274 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 36.2298 | 38.4124 | 24.1504
5-DaHall 1-PDU-21 |  | PDU : SEL1 - 5-1 - A11 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 41.9 | 33.6 | 29.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-3 | ○ | ON | 7.5995 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 4.1999 |  |  |  | ○ | ON | RTX Rack#8, R3-1-3
RTX Rack#2, R1-2-3 | ○ | ON |  | 6.8495 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 3.873 |  |  | ○ | ON | RTX Rack#9, R3-2-3
RTX Rack#3, R1-3-3 | ○ | ON |  |  | 2.1626 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 4.0804 |  | ○ | ON | NW/Mgmt Rack, R3-3-3
RTX Rack#4, R2-1-3 | ○ | ON | 4.5803 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 5.9152 |  |  |  | ○ | ON | A40 Rack#1, R4-1-3
RTX Rack#5, R2-2-3 | ○ | ON |  | 7.0874 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 6.6714 |  |  | ○ | ON | A40 Rack#2, R4-2-3
RTX Rack#6, R2-3-3 | ○ | ON |  |  | 5.0477 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 1.3844 |  | ○ | ON | NetApp FAS#1, R4-3-3
RTX Rack#7, R2-4-3 | ○ | ON | 5.5473 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 1.8972 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-3
DGX Rack#1, R5-1-3 | ○ | ON |  | 3.3058 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 7.0836 |  |  | ○ | OFF | 예비Rack#1, R6-1-3
DGX Rack#2, R5-2-3 | ○ | ON |  |  | 4.3588 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 5.4447 |  | ○ | OFF | 예비Rack#2, R6-2-3
DGX Rack#3, R5-3-3 | ○ | ON | 3.8694 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 8.7852 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-3
| X | OFF |  | 0 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 6.872 |  |  | ○ | OFF | 예비Rack#4, R6-4-3
| X | OFF |  |  | 4.0131 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 42.394 | 41.7426 | 26.4917
5-DaHall 1-PDU-22 |  | PDU : SEL1 - 5-1 - B11 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 37 | 27.7 | 24 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-4 | ○ | ON | 7.8832 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 4.1375 |  |  |  | ○ | ON | RTX Rack#8, R3-1-4
RTX Rack#2, R1-2-4 | ○ | ON |  | 7.0698 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 3.794 |  |  | ○ | ON | RTX Rack#9, R3-2-4
RTX Rack#3, R1-3-4 | ○ | ON |  |  | 2.0665 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 2.3277 |  | ○ | ON | NW/Mgmt Rack, R3-3-4
RTX Rack#4, R2-1-4 | ○ | ON | 4.4634 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 6.3435 |  |  |  | ○ | ON | A40 Rack#1, R4-1-4
RTX Rack#5, R2-2-4 | ○ | ON |  | 7.172 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 6.9704 |  |  | ○ | ON | A40 Rack#2, R4-2-4
RTX Rack#6, R2-3-4 | ○ | ON |  |  | 5.3723 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 1.4594 |  | ○ | ON | NetApp FAS#1, R4-3-4
RTX Rack#7, R2-4-4 | ○ | ON | 5.0662 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 1.9136 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-4
DGX Rack#1, R5-1-4 | ○ | ON |  | 4.0154 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 7.4035 |  |  | ○ | OFF | 예비Rack#1, R6-1-4
DGX Rack#2, R5-2-4 | ○ | ON |  |  | 3.6848 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 5.2239 |  | ○ | OFF | 예비Rack#2, R6-2-4
DGX Rack#3, R5-3-4 | ○ | ON | 4.1795 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 1.2915 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-4
| X | OFF |  | 0 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 1.1181 |  |  | ○ | OFF | 예비Rack#4, R6-4-4
| X | OFF |  |  | 4.1441 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 35.2783 | 37.5433 | 24.2788
5층 TR룸
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
PDU-8 (A) | O | ON |  |  |  |  | 3P 200A | #08 | Singtel | Singtel | #08 | 3P 200A |  |  |  |  | O | ON | PDU-8 (B)
텔스트라 정류기 A1 | O | ON |  |  |  |  | 3P 30A | #03 | C2C | C2C | #04 | 3P 30A |  |  |  |  | O | ON | 텔스트라 정류기 A2
텔스트라 정류기 B1 | O | ON |  |  |  |  | 3P 30A | #05 | C2C | C2C | #06 | 3P 30A |  |  |  |  | O | ON | 텔스트라 정류기 B2
|  |  | 사용량 | 배분
| IDC |  | 538.5825 | 51.65% | [7 empty] | 5-1-A1 | 35.0055 | 39.8719 | 28.4479
| 텔스트라 |  | 43.9589 | 4.216% | [7 empty] | 5-1-B1 | 34.0047 | 37.4394 | 29.9416
| 텔스트라 정류기 |  | 0 | 0% | [7 empty] | 5-1-A2 | 27.9258 | 18.6343 | 14.8715
| singtel PDU-8-A |  | 15.2235 | 1.46% | [7 empty] | 6-1-B2 | 25.4878 | 15.7406 | 14.6967
| singtel PDU-8-B |  | 11.0171 | 1.057% | =>합계 | 2.517% | [5 empty] | 5-1-A3 | 0 | 0 | 0
| singtel (기타) |  | 15.0689 | 1.445% | [7 empty] | 5-1-B3 | 0 | 0 | 0
| LG CNS |  | 418.8752 | 40.17% | [7 empty] | 5-1-A4 | 8.8108 | 1.2814 | 0.77117
함계 | IDC |  | 1042.7261 | 100% | [7 empty] | 5-1-B4 | 6.5314 | 1.4019 | 1.35
[12 empty] | 5-1-A5 | 0 | 0 | 0
[12 empty] | 5-1-B5 | 0 | 0 | 0
[12 empty] | 5-1-A6 | 15.8838 | 10.0183 | 10.3376
[12 empty] | 5-1-B6 | 21.3888 | 13.6218 | 14.3956
[12 empty] | 5-1-A7 | 12.8314 | 18.848 | 14.5257
| C2C | [10 empty] | 5-1-B7 | 13.7101 | 11.3969 | 7.477
[12 empty] | 5-1-A8 | 19.7178 | 13.2707 | 14.9248
[12 empty] | 5-1-B8 | 21.1531 | 12.3878 | 16.2666
[12 empty] | 5-1-A9 | 5.62 | 7.2041 | 2.3994 | 15.2235
[12 empty] | 5-1-B9 | 4.7887 | 5.0029 | 1.2255 | 11.0171
[12 empty] | 5-1-A10 | 42.1361 | 44.6923 | 25.5256
|  |  |  | 복도 | [7 empty] | 5-1-B10 | 36.2298 | 38.4124 | 24.1504
[12 empty] | 5-1-A11 | 42.394 | 41.7426 | 26.4917
[12 empty] | 5-1-B11 | 35.2783 | 37.5433 | 24.2788 |  | 418.8752
|  |  |  | ▼ | [8 empty] | 408.8978 | 368.5107 | 272.0776 | 1049.4861
0
1049.4861
[5 empty] | Singtel-1 |  | Singtel-2 |  | Pacnet
Note on A226: 이현상: 계약전류 10A/랙 ? 초과시 AM연락 필요! (임영호팀장/장우창M/장태영M)
Note on A274: 이현상: 계약전류 10A/랙 ? 초과시 AM연락 필요 (임영호팀장/장우창M/장태영M)

## 4층_부하량(월간_MIN)
Date : 2024-01-01 ~ 2024-01-31
4-DaHall 1-PDU-02 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B1 |  |  |  | 4-DaHall 1-PDU-04 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B2
|  | MAIN 계측값 : | 73.5 | 46 | 65.4 | <- 실측값 | [5 empty] | MAIN 계측값 : | 70.2 | 42.2 | 22.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
정류기 1호기 | O | ON | 0.58 | 0.49 | 0.72 |  | 4P 100A | #01 | 코어룸 |  | X | OFF | 0 | 0 | 0 |  | 4P 100A | #01
POP E(상) | O | ON | 34.83 |  |  |  | 2P 100A | #02 | 코어룸 | POP F(상) | O | ON | 38.59 |  |  |  | 2P 100A | #02 | 코어룸
POP B(상) | O | ON |  | 31.82 |  |  | 2P 100A | #03 | 코어룸 | IDC 1구역 B(상) | O | ON |  | 27.97 |  |  | 2P 100A | #03 | 코어룸
POP C(상) | O | ON |  |  | 35.69 |  | 2P 100A | #04 | 코어룸 | IDC 1구역 C(상) | X | OFF |  |  | 0 |  | 2P 100A | #04 | 코어룸
POP D(상) | O | ON | 40.41 |  |  |  | 2P 100A | #05 | 코어룸 | IDC 1구역 D(상) | O | ON | 9.55 |  |  |  | 2P 100A | #05 | 코로케션
IDC 2구역 I(상) | O | ON |  | 11.85 |  |  | 2P 100A | #06 | 코로케션 | IDC 1구역 E(상) | O | ON |  | 13.85 |  |  | 2P 100A | #06 | 코로케션
IDC 2구역 H(상) | O | ON |  |  | 28.4 |  | 2P 100A | #07 | 코로케션 | IDC 1구역 F(상) | O | ON |  |  | 20.29 |  | 2P 100A | #07 | 코로케션
| X | OFF | 0 |  |  |  | 2P 100A | #08 |  | IDC 1구역 G(상) | O | ON | 21.11 |  |  |  | 2P 100A | #08 | 코로케션
| X | OFF |  | 0 |  |  | 2P 100A | #09 |  |  | X | OFF |  | 0 |  |  | 2P 100A | #09
|  | 합계: | 75.82 | 44.16 | 64.81 | [6 empty] | 합계: | 69.25 | 41.82 | 20.29
4-DaHall 1-PDU-06 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B3 |  |  |  | 4-DaHall 1-PDU-08 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B4
|  | MAIN 계측값 : | 67 | 32.4 | 27 | <- 실측값 | [5 empty] | MAIN 계측값 : | 44.8 | 68.4 | 18 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
IDC 2구역 J(상) | O | ON | 9.9 |  |  |  | 2P 100A | #01 | 코로케션 | K 2-1-상 | O | ON | 22.22 |  |  |  | 2P 100A | #01 | 세틀뱅크(구 시스케어)
IDC 2구역 K(상) | O | ON |  | 0 |  |  | 2P 100A | #02 | 코로케션 | K 3-1 상 | O | ON |  | 32.59 |  |  | 2P 100A | #02 | 미디어꾼(구)윈텔)
IDC 2구역 L(상) | O | ON |  |  | 8.86 |  | 2P 100A | #03 | 코로케션 | K 2-2-상 | O | ON |  |  | 5.28 |  | 2P 100A | #03 | 세틀뱅크(구 시스케어)
IDC 2구역 M(상) | O | ON | 6.84 |  |  |  | 2P 100A | #04 | 코로케션 | K 3-2 상 | O | ON | 9.27 |  |  |  | 2P 100A | #04 | 미디어꾼(구)윈텔)
IDC 3구역 N(상) | O | ON |  | 0 |  |  | 2P 100A | #05 | 코로케션 | K 2-3-상 | O | ON |  | 7.35 |  |  | 2P 100A | #05 | 세틀뱅크(구 시스케어)
IDC 3구역 O(상) | O | ON |  |  | 0 |  | 2P 100A | #06 | 코로케션 | K 3-3 상 | O | ON |  |  | 10.78 |  | 2P 100A | #06 | 미디어꾼(구)윈텔)
IDC 3구역 P(상) | O | ON | 8.1 |  |  |  | 2P 100A | #07 | 코로케션 | K 2-4 상 | O | ON | 12.97 |  |  |  | 2P 100A | #07 | 세틀뱅크(구 시스케어)
IDC 3구역 Q(상) | O | ON |  | 13.6 |  |  | 2P 100A | #08 | 코로케션 | K 3-4 상 | O | ON |  | 23.6 |  |  | 2P 100A | #08 | 미디어꾼(구)윈텔)
IDC 3구역 R(상) | O | OFF |  |  | 0 |  | 2P 100A | #09 | 코로케션 | K 1-1 상 | O | ON |  |  | 0 |  | 2P 100A | #09 | BMW
IDC 3구역 S(상) | O | ON | 37.76 |  |  |  | 2P 100A | #10 | 코로케션 | K 1-2 상 | O | ON | 0 |  |  |  | 2P 100A | #10 | 세종시스템케이지
| X | OFF |  | 0 |  |  | 2P 100A | #11 |  |  | X | OFF |  | 0 |  |  | 2P 100A | #11
| X | OFF |  |  | 0 |  | 2P 100A | #12 |  |  | X | OFF |  |  | 0 |  | 2P 100A | #12
|  | 합계: | 62.6 | 13.6 | 8.86 | [6 empty] | 합계: | 44.46 | 63.54 | 16.06
4-DaHall 1-PDU-10 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B5 |  |  |  | 4-DaHall 1-PDU-01 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A1
|  | MAIN 계측값 : | 46.5 | 43.9 | 43.5 | <- 실측값 | [5 empty] | MAIN 계측값 : | 77.6 | 59.1 | 50.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
라온 - 철거 | O | OFF | 0 | 0 | 0 |  | 4P 200A | #01 |  | 정류기 2호기 | O | ON | 1.2 | 0.96 | 1.4 |  | 4P 100A | #01 | 코어룸
CRAC 4E-1호기(20RT) | O | ON | 29.41 | 26.75 | 28.35 |  | 4P 200A | #02 | 항온 | POP E(하) | O | ON | 37.17 |  |  |  | 2P 100A | #02 | 코어룸
CRAC 4E-2호기(20RT) | O | ON | 2.92 | 2.63 | 3.19 |  | 4P 200A | #03 | 항온 | POP B(하) | O | ON |  | 33.35 |  |  | 2P 100A | #03 | 코어룸
|  | 합계: | 32.33 | 29.38 | 31.54 | 0 |  |  |  | POP C(하) | O | ON |  |  | 36.92 |  | 2P 100A | #04 | 코어룸
[10 empty] | POP D(하) | O | ON | 41.05 |  |  |  | 2P 100A | #05 | 코어룸
[10 empty] | IDC 2구역 I(하) | O | ON |  | 23.03 |  |  | 2P 100A | #06 | 코로케션
[10 empty] | IDC 2구역 H(하) | O | ON |  |  | 12.37 |  | 2P 100A | #07 | 코로케션
[11 empty] | X | OFF | 0 |  |  |  | 2P 100A | #08
[11 empty] | X | OFF |  | 0 |  |  | 2P 100A | #09
[12 empty] | 합계: | 79.42 | 57.34 | 50.69
4-DaHall 1-PDU-03 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A2 |  |  |  | 4-DaHall 1-PDU-05 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A3
|  | MAIN 계측값 : | 57.4 | 38.8 | 25.4 | <- 실측값 | [5 empty] | MAIN 계측값 : | 59.5 | 27.6 | 25.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
| X | OFF | 0 | 0 | 0 |  | 4P 100A | #01 |  | IDC 2구역 J(하) | O | ON | 8.14 |  |  |  | 2P 100A | #01 | 코로케션
POP F(하) | O | ON | 29.71 |  |  |  | 2P 100A | #02 | 코어룸 | IDC 2구역 K(하) | O | ON |  | 0 |  |  | 2P 100A | #02 | 코로케션
IDC 1구역 B(하) | O | ON |  | 27.78 |  |  | 2P 100A | #03 | 코어룸 | IDC 2구역 L(하) | O | ON |  |  | 7.67 |  | 2P 100A | #03 | 코로케션
IDC 1구역 C(하) | X | OFF |  |  | 0 |  | 2P 100A | #04 | 코어룸 | IDC 2구역 M(하) | O | ON | 7.14 |  |  |  | 2P 100A | #04 | 코로케션
IDC 1구역 D(하) | O | ON | 6.2 |  |  |  | 2P 100A | #05 | 코로케션 | IDC 3구역 N(하) | O | ON |  | 0 |  |  | 2P 100A | #05 | 코로케션
IDC 1구역 E(하) | O | ON |  | 9.8 |  |  | 2P 100A | #06 | 코로케션 | IDC 3구역 O(하) | O | ON |  |  | 12.67 |  | 2P 100A | #06 | 코로케션
IDC 1구역 F(하) | O | ON |  |  | 27.76 |  | 2P 100A | #07 | 코로케션 | IDC 3구역 P(하) | O | ON | 6.52 |  |  |  | 2P 100A | #07 | 코로케션
IDC 1구역 G(하) | O | ON | 17.47 |  |  |  | 2P 100A | #08 | 코로케션 | IDC 3구역 Q(하) | O | ON |  | 12.19 |  |  | 2P 100A | #08 | 코로케션
| X | OFF |  | 0 |  |  | 2P 100A | #09 |  | IDC 3구역 R(하) | O | OFF |  |  | 0 |  | 2P 100A | #09 | 코로케션
|  | 합계: | 53.38 | 37.58 | 27.76 |  |  |  |  | IDC 3구역 S(하) | O | ON | 31.49 |  |  |  | 2P 100A | #10 | 코로케션
[11 empty] | X | OFF |  | 0 |  |  | 2P 100A | #11
[11 empty] | X | OFF |  |  | 0 |  | 2P 100A | #12
[12 empty] | 합계: | 53.29 | 12.19 | 20.34
4-DaHall 1-PDU-07 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A4 |  |  |  | 4-DaHall 1-PDU-09 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A5
|  | MAIN 계측값 : | 44.7 | 76.7 | 22 | <- 실측값 | [5 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 2-1-하 | O | ON | 20.1 |  |  |  | 2P 100A | #01 | 세틀뱅크(구 시스케어) | 라온(상)- 철거 | X | OFF | 0 | 0 | 0 |  | 4P 200A | #01
K 3-1-하 | O | ON |  | 32.83 |  |  | 2P 100A | #02 | 미디어꾼(구)윈텔) |  | X | OFF | 0 | 0 | 0 |  | 4P 200A | #02
K 2-2-하 | O | ON |  |  | 5.19 |  | 2P 100A | #03 | 세틀뱅크(구 시스케어) |  | X | OFF | 0 | 0 | 0 |  | 4P 200A | #03
K 3-2-하 | O | ON | 10.11 |  |  |  | 2P 100A | #04 | 미디어꾼(구)윈텔) |  |  | 합계: | 0 | 0 | 0
K 2-3-하 | O | ON |  | 5.95 |  |  | 2P 100A | #05 | 세틀뱅크(구 시스케어) | TR Room A,B
K 3-3-하 | O | ON |  |  | 14.28 |  | 2P 100A | #06 | 미디어꾼(구)윈텔) | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 2-4-하 | O | ON | 13.74 |  |  |  | 2P 100A | #07 | 세틀뱅크(구 시스케어) | KB증권 DR(A) - 철거 | X | OFF |  |  |  |  | 4P 320A | #07
K 3-4-하 | O | ON |  | 31.44 |  |  | 2P 100A | #08 | 미디어꾼(구)윈텔)
K 1-1-하 | O | ON |  |  | 0 |  | 2P 100A | #09 | BMW | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 1-2-하 | O | ON | 0 |  |  |  | 2P 100A | #10 | 세종시스템케이지 | KB증권 DR(B) - 철거 | X | OFF |  |  |  |  | 4P 320A | #07
| X | OFF |  | 0 |  |  | 2P 100A | #11
| X | OFF |  |  | 0 |  | 2P 100A | #12
|  | 합계: | 43.95 | 70.22 | 19.47
4-DaHall 1-PDU-11 | [8 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RPP-01 | ○ | ON | 0.44 | 0.34 | 0.34 |  | 4P 125A | #01 |  |  | #02 | 2P 50A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 0 |  | X | OFF
A401_A | ○ | ON | 0 |  |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A | 0 |  |  |  | ○ | ON | A402_A1
A403_A | ○ | ON |  | 0 |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  | 0 |  |  | ○ | ON | A404_A1
A405_A | ○ | ON |  |  | 0 |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  |  | 0 |  | ○ | ON | A406_A1
A407_A | ○ | ON | 0 |  |  |  | 2P 30A | #13 |  |  | #14 | 2P 30A | 0 |  |  |  | ○ | ON | A408_A1
A409_A | ○ | ON |  | 0 |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A |  | 0 |  |  | ○ | ON | A410_A
A501_A | ○ | ON |  |  | 0 |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  |  | 0 |  | ○ | ON | A502_A
A503_A1 | ○ | ON | 0 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 30A | 0 |  |  |  | ○ | ON | A504_A
A505_A | ○ | ON |  | 0 |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A |  | 0 |  |  | ○ | ON | A506_A1
A507_A | ○ | ON |  |  | 0 |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  |  | 0 |  | ○ | ON | A508_A
A509_A | ○ | ON | 0 |  |  |  | 2P 30A | #25 |  |  | #26 | 2P 30A | 0 |  |  |  | ○ | ON | A510_A
A601_A | ○ | ON |  | 0.28 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0.22 |  |  | ○ | ON | A602_A
A603_A | ○ | ON |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | ○ | ON | A604_A
A605_A | ○ | ON | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | ○ | ON | A606_A
A607_A | ○ | ON |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | ○ | ON | A608_A
A609_A | ○ | ON |  |  | 0 |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  |  | 0 |  | ○ | ON | A610_A
A402_A2 | ○ | ON | 0 |  |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A | 0 |  |  |  | ○ | ON | A503_A2
A506_A2 | ○ | ON |  | 0 |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  | 0 |  |  | ○ | OFF | 08_A
07_A | ○ | OFF |  |  | 0 |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  |  | 0 |  | ○ | OFF | 06_A
05_A | ○ | OFF | 0 |  |  |  | 2P 30A | #43 |  |  | #44 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0.44 | 0.84 | 0.34
4-DaHall 1-PDU-12 | [8 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RPP-01 | ○ | ON | 0.44 | 0.2 | 0 |  | 4P 125A | #01 |  |  | #02 | 2P 50A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 0 |  | X | OFF
A401_B | ○ | ON | 0 |  |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A | 0 |  |  |  | ○ | ON | A402_B1
A403_B | ○ | ON |  | 0 |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  | 0 |  |  | ○ | ON | A404_B1
A405_B | ○ | ON |  |  | 0 |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  |  | 0 |  | ○ | ON | A406_B1
A407_B | ○ | ON | 0 |  |  |  | 2P 30A | #13 |  |  | #14 | 2P 30A | 0 |  |  |  | ○ | ON | A408_B1
A409_B | ○ | ON |  | 0 |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A |  | 0 |  |  | ○ | ON | A410_B
A501_B | ○ | ON |  |  | 0 |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  |  | 0 |  | ○ | ON | A502_B
A503_B1 | ○ | ON | 0 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 30A | 0 |  |  |  | ○ | ON | A504_B
A505_B | ○ | ON |  | 0 |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A |  | 0 |  |  | ○ | ON | A506_B1
A507_B | ○ | ON |  |  | 0 |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  |  | 0 |  | ○ | ON | A508_B
A509_B | ○ | ON | 0 |  |  |  | 2P 30A | #25 |  |  | #26 | 2P 30A | 0 |  |  |  | ○ | ON | A510_B
A601_B | ○ | ON |  | 2.17 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0.94 |  |  | ○ | ON | A602_B
A603_B | ○ | ON |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | ○ | ON | A604_B
A605_B | ○ | ON | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | ○ | ON | A606_B
A607_B | ○ | ON |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | ○ | ON | A608_B
A609_B | ○ | ON |  |  | 0 |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  |  | 0 |  | ○ | ON | A610_B
A402_B2 | ○ | ON | 0 |  |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A | 0 |  |  |  | ○ | ON | A503_B2
A506_B2 | ○ | ON |  | 0 |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  | 0 |  |  | ○ | OFF | 08_B
07_B | ○ | OFF |  |  | 0 |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  |  | 0 |  | ○ | OFF | 06_B
05_B | ○ | OFF | 0 |  |  |  | 2P 30A | #43 |  |  | #44 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0.44 | 3.31 | 0
4-DaHall 1-PDU-13 | [8 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 0 |  |  | X | OFF
A701_A1 | ○ | ON |  |  | 0 |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  |  | 0 |  | ○ | ON | A701_A2
A702_A1 | ○ | ON | 0 |  |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A | 0 |  |  |  | ○ | ON | A702_A2
A703_A | ○ | ON |  | 0 |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  | 0 |  |  | ○ | ON | A704_A
A705_A | ○ | ON |  |  | 0 |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  |  | 0 |  | ○ | ON | A706_A1
A707_A | ○ | ON | 0 |  |  |  | 2P 30A | #13 |  |  | #14 | 2P 30A | 0 |  |  |  | ○ | ON | A708_A
A709_A | ○ | ON |  | 0 |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A |  | 0 |  |  | ○ | ON | A710_A
A801_A | ○ | ON |  |  | 0 |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  |  | 0 |  | ○ | ON | A802_A
A803_A | ○ | ON | 0 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 30A | 0 |  |  |  | ○ | ON | A805_A1
A805_A2 | ○ | ON |  | 0 |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A |  | 0 |  |  | ○ | ON | A806_A1
A807_A | ○ | ON |  |  | 0 |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  |  | 0 |  | ○ | ON | A808_A
A809_A | ○ | ON | 0 |  |  |  | 2P 30A | #25 |  |  | #26 | 2P 30A | 0 |  |  |  | ○ | ON | A810_A
A901_A | ○ | ON |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | ○ | ON | A907_A2
A902_A | ○ | ON |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | ○ | ON | A903_A
A904_A | ○ | ON | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | ○ | ON | A905_A
A906_A | ○ | ON |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | ○ | ON | A907_A1
A908_A | ○ | ON |  |  | 0 |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  |  | 0 |  | ○ | ON | A909_A
A910_A | ○ | ON | 0 |  |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A | 0 |  |  |  | ○ | ON | A706_A2
A806_A2 | ○ | ON |  | 0 |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  | 0 |  |  | ○ | ON | 04_A
03_A | ○ | ON |  |  | 0 |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  |  | 0 |  | ○ | ON | 02_A
01_A | ○ | ON | 0 |  |  |  | 2P 30A | #43 |  |  | #44 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
4-DaHall 1-PDU-14 | [8 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 0 |  |  | X | OFF
A701_B1 | ○ | ON |  |  | 0 |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  |  | 0 |  | ○ | ON | A701_B2
A702_B1 | ○ | ON | 0 |  |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A | 0 |  |  |  | ○ | ON | A702_B2
A703_B | ○ | ON |  | 0 |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  | 0 |  |  | ○ | ON | A704_B
A705_B | ○ | ON |  |  | 0 |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  |  | 0 |  | ○ | ON | A706_B1
A707_B | ○ | ON | 0 |  |  |  | 2P 30A | #13 |  |  | #14 | 2P 30A | 0 |  |  |  | ○ | ON | A708_B
A709_B | ○ | ON |  | 0 |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A |  | 0 |  |  | ○ | ON | A710_B
A801_B | ○ | ON |  |  | 0 |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  |  | 0 |  | ○ | ON | A802_B
A803_B | ○ | ON | 0 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 30A | 0 |  |  |  | ○ | ON | A805_B1
A805_B2 | ○ | ON |  | 0 |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A |  | 0 |  |  | ○ | ON | A806_B1
A807_B | ○ | ON |  |  | 0 |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  |  | 0 |  | ○ | ON | A808_B
A809_B | ○ | ON | 0 |  |  |  | 2P 30A | #25 |  |  | #26 | 2P 30A | 0 |  |  |  | ○ | ON | A810_B
A901_B | ○ | ON |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | ○ | ON | A907_B2
A902_B | ○ | ON |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | ○ | ON | A903_B
A904_B | ○ | ON | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | ○ | ON | A905_B
A906_B | ○ | ON |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | ○ | ON | A907_B1
A908_B | ○ | ON |  |  | 0 |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  |  | 0 |  | ○ | ON | A909_B
A910_B | ○ | ON | 0 |  |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A | 0 |  |  |  | ○ | ON | A706_B2
A806_B2 | ○ | ON |  | 0 |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  | 0 |  |  | ○ | ON | 04_B
03_B | ○ | ON |  |  | 0 |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  |  | 0 |  | ○ | ON | 02_B
01_B | ○ | ON | 0 |  |  |  | 2P 30A | #43 |  |  | #44 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
4-DaHall 1-RPP-01 |  |  | Main CB 3P 125A | [6 empty] | 4-DaHall 1-RPP-02 |  |  | Main CB 3P 125A
|  | MAIN 계측값 : |  |  |  | <- 실측값 | [5 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
A404_A2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #01 |  | A404_B2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #01
A406_A2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #02 |  | A406_B2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #02
A408_A2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #03 |  | A408_B2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #03
A804_A | O | ON | 0 | 0 | 0 |  | 3P 30A | #04 |  | A804_B | O | ON | 0 | 0 | 0 |  | 3P 30A | #04
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #05 |  |  | X | OFF | 0 | 0 | 0 |  | 3P 30A | #05
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #06 |  |  | X | OFF | 0 | 0 | 0 |  | 3P 30A | #06
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #07 |  |  | X | OFF | 0 | 0 | 0 |  | 3P 30A | #07
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #08 |  |  | X | OFF | 0 | 0 | 0 |  | 3P 30A | #08
|  | 합계: | 0 | 0 | 0 | [6 empty] | 합계: | 0 | 0 | 0
|  |  |  | 사용량 | 층당 분배
4층 | IDC | IDC |  | 630.26 | 59.97%
| IP | 세종 시스템 |  | 0 | 0%
| 공통 | 세종 시스템
| IP | core room |  | 420.64 | 40.03%
총합 |  |  |  | 1050.9 | 100%
4층 항온항습기 비상 (4층 5RT x 3대, 10RT x 1대) | [8 empty] | Main CB 3P 150A
[11 empty] | MAIN 계측값 : | 24.1 | 22 | 21.9 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | 부하명 | CB 용량 | R | S | T | N | 배선연결 | ON/OFF |  | NO.
4-1 호 | O | ON |  |  |  |  | 3P 50A |  |  | 4-4호 | 3P 50A |  |  |  |  | O | ON
4-2 호 | O | ON |  |  |  | 0 | 3P 50A |  |  |  | 3P 50A |  |  |  |  | X | OFF
4-3 호 | O | ON |  |  |  | 0.1 | 3P 50A |  |  |  | 3P 50A |  |  |  |  | X | OFF
[11 empty] | 합계: | 0 | 0 | 0

## 4층_부하량(월간_MAX)
Date : 2024-01-01 ~ 2024-01-31
4-DaHall 1-PDU-02 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B1 |  |  |  | 4-DaHall 1-PDU-04 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B2
|  | MAIN 계측값 : | 73.5 | 46 | 65.4 | <- 실측값 | [5 empty] | MAIN 계측값 : | 70.2 | 42.2 | 22.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
정류기 1호기 | O | ON | 0.96 | 0.73 | 1.12 |  | 4P 100A | #01 | 코어룸 |  | X | OFF | 0 | 0 | 0 |  | 4P 100A | #01
POP E(상) | O | ON | 35.29 |  |  |  | 2P 100A | #02 | 코어룸 | POP F(상) | O | ON | 42.02 |  |  |  | 2P 100A | #02 | 코어룸
POP B(상) | O | ON |  | 32.92 |  |  | 2P 100A | #03 | 코어룸 | IDC 1구역 B(상) | O | ON |  | 29.53 |  |  | 2P 100A | #03 | 코어룸
POP C(상) | O | ON |  |  | 36.12 |  | 2P 100A | #04 | 코어룸 | IDC 1구역 C(상) | X | OFF |  |  | 0 |  | 2P 100A | #04 | 코어룸
POP D(상) | O | ON | 41.95 |  |  |  | 2P 100A | #05 | 코어룸 | IDC 1구역 D(상) | O | ON | 10 |  |  |  | 2P 100A | #05 | 코로케션
IDC 2구역 I(상) | O | ON |  | 12.58 |  |  | 2P 100A | #06 | 코로케션 | IDC 1구역 E(상) | O | ON |  | 15.11 |  |  | 2P 100A | #06 | 코로케션
IDC 2구역 H(상) | O | ON |  |  | 30.05 |  | 2P 100A | #07 | 코로케션 | IDC 1구역 F(상) | O | ON |  |  | 22.62 |  | 2P 100A | #07 | 코로케션
| X | OFF | 0 |  |  |  | 2P 100A | #08 |  | IDC 1구역 G(상) | O | ON | 23.54 |  |  |  | 2P 100A | #08 | 코로케션
| X | OFF |  | 0 |  |  | 2P 100A | #09 |  |  | X | OFF |  | 0 |  |  | 2P 100A | #09
|  | 합계: | 78.2 | 46.23 | 67.29 | [6 empty] | 합계: | 75.56 | 44.64 | 22.62
4-DaHall 1-PDU-06 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B3 |  |  |  | 4-DaHall 1-PDU-08 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B4
|  | MAIN 계측값 : | 67 | 32.4 | 27 | <- 실측값 | [5 empty] | MAIN 계측값 : | 44.8 | 68.4 | 18 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
IDC 2구역 J(상) | O | ON | 11.71 |  |  |  | 2P 100A | #01 | 코로케션 | K 2-1-상 | O | ON | 24.7 |  |  |  | 2P 100A | #01 | 세틀뱅크(구 시스케어)
IDC 2구역 K(상) | O | ON |  | 0 |  |  | 2P 100A | #02 | 코로케션 | K 3-1 상 | O | ON |  | 35.2 |  |  | 2P 100A | #02 | 미디어꾼(구)윈텔)
IDC 2구역 L(상) | O | ON |  |  | 9.15 |  | 2P 100A | #03 | 코로케션 | K 2-2-상 | O | ON |  |  | 5.59 |  | 2P 100A | #03 | 세틀뱅크(구 시스케어)
IDC 2구역 M(상) | O | ON | 7.55 |  |  |  | 2P 100A | #04 | 코로케션 | K 3-2 상 | O | ON | 9.95 |  |  |  | 2P 100A | #04 | 미디어꾼(구)윈텔)
IDC 3구역 N(상) | O | ON |  | 0 |  |  | 2P 100A | #05 | 코로케션 | K 2-3-상 | O | ON |  | 7.89 |  |  | 2P 100A | #05 | 세틀뱅크(구 시스케어)
IDC 3구역 O(상) | O | ON |  |  | 0 |  | 2P 100A | #06 | 코로케션 | K 3-3 상 | O | ON |  |  | 13.9 |  | 2P 100A | #06 | 미디어꾼(구)윈텔)
IDC 3구역 P(상) | O | ON | 9.31 |  |  |  | 2P 100A | #07 | 코로케션 | K 2-4 상 | O | ON | 13.12 |  |  |  | 2P 100A | #07 | 세틀뱅크(구 시스케어)
IDC 3구역 Q(상) | O | ON |  | 14.92 |  |  | 2P 100A | #08 | 코로케션 | K 3-4 상 | O | ON |  | 33.38 |  |  | 2P 100A | #08 | 미디어꾼(구)윈텔)
IDC 3구역 R(상) | O | OFF |  |  | 0 |  | 2P 100A | #09 | 코로케션 | K 1-1 상 | O | ON |  |  | 0 |  | 2P 100A | #09 | BMW
IDC 3구역 S(상) | O | ON | 39.49 |  |  |  | 2P 100A | #10 | 코로케션 | K 1-2 상 | O | ON | 0 |  |  |  | 2P 100A | #10 | 세종시스템케이지
| X | OFF |  | 0 |  |  | 2P 100A | #11 |  |  | X | OFF |  | 0 |  |  | 2P 100A | #11
| X | OFF |  |  | 0 |  | 2P 100A | #12 |  |  | X | OFF |  |  | 0 |  | 2P 100A | #12
|  | 합계: | 68.06 | 14.92 | 9.15 | [6 empty] | 합계: | 47.77 | 76.47 | 19.49
4-DaHall 1-PDU-10 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B5 |  |  |  | 4-DaHall 1-PDU-01 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A1
|  | MAIN 계측값 : | 46.5 | 43.9 | 43.5 | <- 실측값 | [5 empty] | MAIN 계측값 : | 77.6 | 59.1 | 50.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
라온 - 철거 | O | OFF | 0 | 0 | 0 |  | 4P 200A | #01 |  | 정류기 2호기 | O | ON | 1.48 | 1.18 | 1.65 |  | 4P 100A | #01 | 코어룸
CRAC 4E-1호기(20RT) | O | ON | 33.72 | 31.18 | 32.47 |  | 4P 200A | #02 | 항온 | POP E(하) | O | ON | 37.75 |  |  |  | 2P 100A | #02 | 코어룸
CRAC 4E-2호기(20RT) | O | ON | 28.8 | 27.98 | 27.64 |  | 4P 200A | #03 | 항온 | POP B(하) | O | ON |  | 34.72 |  |  | 2P 100A | #03 | 코어룸
|  | 합계: | 62.52 | 59.16 | 60.11 | 0 |  |  |  | POP C(하) | O | ON |  |  | 37.32 |  | 2P 100A | #04 | 코어룸
[10 empty] | POP D(하) | O | ON | 42.44 |  |  |  | 2P 100A | #05 | 코어룸
[10 empty] | IDC 2구역 I(하) | O | ON |  | 24.92 |  |  | 2P 100A | #06 | 코로케션
[10 empty] | IDC 2구역 H(하) | O | ON |  |  | 13.07 |  | 2P 100A | #07 | 코로케션
[11 empty] | X | OFF | 0 |  |  |  | 2P 100A | #08
[11 empty] | X | OFF |  | 0 |  |  | 2P 100A | #09
[12 empty] | 합계: | 81.67 | 60.82 | 52.04
4-DaHall 1-PDU-03 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A2 |  |  |  | 4-DaHall 1-PDU-05 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A3
|  | MAIN 계측값 : | 57.4 | 38.8 | 25.4 | <- 실측값 | [5 empty] | MAIN 계측값 : | 59.5 | 27.6 | 25.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
| X | OFF | 0 | 0 | 0 |  | 4P 100A | #01 |  | IDC 2구역 J(하) | O | ON | 9.93 |  |  |  | 2P 100A | #01 | 코로케션
POP F(하) | O | ON | 33.49 |  |  |  | 2P 100A | #02 | 코어룸 | IDC 2구역 K(하) | O | ON |  | 0 |  |  | 2P 100A | #02 | 코로케션
IDC 1구역 B(하) | O | ON |  | 28.49 |  |  | 2P 100A | #03 | 코어룸 | IDC 2구역 L(하) | O | ON |  |  | 7.76 |  | 2P 100A | #03 | 코로케션
IDC 1구역 C(하) | X | OFF |  |  | 0 |  | 2P 100A | #04 | 코어룸 | IDC 2구역 M(하) | O | ON | 7.51 |  |  |  | 2P 100A | #04 | 코로케션
IDC 1구역 D(하) | O | ON | 6.6 |  |  |  | 2P 100A | #05 | 코로케션 | IDC 3구역 N(하) | O | ON |  | 0 |  |  | 2P 100A | #05 | 코로케션
IDC 1구역 E(하) | O | ON |  | 10.62 |  |  | 2P 100A | #06 | 코로케션 | IDC 3구역 O(하) | O | ON |  |  | 13.74 |  | 2P 100A | #06 | 코로케션
IDC 1구역 F(하) | O | ON |  |  | 30.88 |  | 2P 100A | #07 | 코로케션 | IDC 3구역 P(하) | O | ON | 7.67 |  |  |  | 2P 100A | #07 | 코로케션
IDC 1구역 G(하) | O | ON | 20 |  |  |  | 2P 100A | #08 | 코로케션 | IDC 3구역 Q(하) | O | ON |  | 13.92 |  |  | 2P 100A | #08 | 코로케션
| X | OFF |  | 0 |  |  | 2P 100A | #09 |  | IDC 3구역 R(하) | O | OFF |  |  | 0 |  | 2P 100A | #09 | 코로케션
|  | 합계: | 60.09 | 39.11 | 30.88 |  |  |  |  | IDC 3구역 S(하) | O | ON | 33.02 |  |  |  | 2P 100A | #10 | 코로케션
[11 empty] | X | OFF |  | 0 |  |  | 2P 100A | #11
[11 empty] | X | OFF |  |  | 0 |  | 2P 100A | #12
[12 empty] | 합계: | 58.13 | 13.92 | 21.5
4-DaHall 1-PDU-07 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A4 |  |  |  | 4-DaHall 1-PDU-09 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A5
|  | MAIN 계측값 : | 44.7 | 76.7 | 22 | <- 실측값 | [5 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 2-1-하 | O | ON | 21.93 |  |  |  | 2P 100A | #01 | 세틀뱅크(구 시스케어) | 라온(상)- 철거 | X | OFF | 0 | 0 | 0 |  | 4P 200A | #01
K 3-1-하 | O | ON |  | 35.53 |  |  | 2P 100A | #02 | 미디어꾼(구)윈텔) |  | X | OFF | 0 | 0 | 0 |  | 4P 200A | #02
K 2-2-하 | O | ON |  |  | 5.52 |  | 2P 100A | #03 | 세틀뱅크(구 시스케어) |  | X | OFF | 0 | 0 | 0 |  | 4P 200A | #03
K 3-2-하 | O | ON | 10.84 |  |  |  | 2P 100A | #04 | 미디어꾼(구)윈텔) |  |  | 합계: | 0 | 0 | 0
K 2-3-하 | O | ON |  | 6.44 |  |  | 2P 100A | #05 | 세틀뱅크(구 시스케어) | TR Room A,B
K 3-3-하 | O | ON |  |  | 17.48 |  | 2P 100A | #06 | 미디어꾼(구)윈텔) | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 2-4-하 | O | ON | 13.9 |  |  |  | 2P 100A | #07 | 세틀뱅크(구 시스케어) | KB증권 DR(A) - 철거 | X | OFF |  |  |  |  | 4P 320A | #07
K 3-4-하 | O | ON |  | 37.6 |  |  | 2P 100A | #08 | 미디어꾼(구)윈텔)
K 1-1-하 | O | ON |  |  | 0 |  | 2P 100A | #09 | BMW | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 1-2-하 | O | ON | 0 |  |  |  | 2P 100A | #10 | 세종시스템케이지 | KB증권 DR(B) - 철거 | X | OFF |  |  |  |  | 4P 320A | #07
| X | OFF |  | 0 |  |  | 2P 100A | #11
| X | OFF |  |  | 0 |  | 2P 100A | #12
|  | 합계: | 46.67 | 79.57 | 23
4-DaHall 1-PDU-11 | [8 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RPP-01 | ○ | ON | 0.44 | 0.35 | 0.35 |  | 4P 125A | #01 |  |  | #02 | 2P 50A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 0 |  | X | OFF
A401_A | ○ | ON | 0 |  |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A | 0 |  |  |  | ○ | ON | A402_A1
A403_A | ○ | ON |  | 0 |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  | 0 |  |  | ○ | ON | A404_A1
A405_A | ○ | ON |  |  | 0 |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  |  | 0 |  | ○ | ON | A406_A1
A407_A | ○ | ON | 0 |  |  |  | 2P 30A | #13 |  |  | #14 | 2P 30A | 0 |  |  |  | ○ | ON | A408_A1
A409_A | ○ | ON |  | 0 |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A |  | 0 |  |  | ○ | ON | A410_A
A501_A | ○ | ON |  |  | 0 |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  |  | 0 |  | ○ | ON | A502_A
A503_A1 | ○ | ON | 0 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 30A | 0 |  |  |  | ○ | ON | A504_A
A505_A | ○ | ON |  | 0 |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A |  | 0 |  |  | ○ | ON | A506_A1
A507_A | ○ | ON |  |  | 0 |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  |  | 0 |  | ○ | ON | A508_A
A509_A | ○ | ON | 0 |  |  |  | 2P 30A | #25 |  |  | #26 | 2P 30A | 0 |  |  |  | ○ | ON | A510_A
A601_A | ○ | ON |  | 0.28 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0.25 |  |  | ○ | ON | A602_A
A603_A | ○ | ON |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | ○ | ON | A604_A
A605_A | ○ | ON | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | ○ | ON | A606_A
A607_A | ○ | ON |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | ○ | ON | A608_A
A609_A | ○ | ON |  |  | 0 |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  |  | 0 |  | ○ | ON | A610_A
A402_A2 | ○ | ON | 0 |  |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A | 0 |  |  |  | ○ | ON | A503_A2
A506_A2 | ○ | ON |  | 0 |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  | 0 |  |  | ○ | OFF | 08_A
07_A | ○ | OFF |  |  | 0 |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  |  | 0 |  | ○ | OFF | 06_A
05_A | ○ | OFF | 0 |  |  |  | 2P 30A | #43 |  |  | #44 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0.44 | 0.88 | 0.35
4-DaHall 1-PDU-12 | [8 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RPP-01 | ○ | ON | 0.44 | 0.2 | 0 |  | 4P 125A | #01 |  |  | #02 | 2P 50A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 0 |  | X | OFF
A401_B | ○ | ON | 0 |  |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A | 0 |  |  |  | ○ | ON | A402_B1
A403_B | ○ | ON |  | 0 |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  | 0 |  |  | ○ | ON | A404_B1
A405_B | ○ | ON |  |  | 0 |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  |  | 0 |  | ○ | ON | A406_B1
A407_B | ○ | ON | 0 |  |  |  | 2P 30A | #13 |  |  | #14 | 2P 30A | 0 |  |  |  | ○ | ON | A408_B1
A409_B | ○ | ON |  | 0 |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A |  | 0 |  |  | ○ | ON | A410_B
A501_B | ○ | ON |  |  | 0 |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  |  | 0 |  | ○ | ON | A502_B
A503_B1 | ○ | ON | 0 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 30A | 0 |  |  |  | ○ | ON | A504_B
A505_B | ○ | ON |  | 0 |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A |  | 0 |  |  | ○ | ON | A506_B1
A507_B | ○ | ON |  |  | 0 |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  |  | 0 |  | ○ | ON | A508_B
A509_B | ○ | ON | 0 |  |  |  | 2P 30A | #25 |  |  | #26 | 2P 30A | 0 |  |  |  | ○ | ON | A510_B
A601_B | ○ | ON |  | 2.18 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0.99 |  |  | ○ | ON | A602_B
A603_B | ○ | ON |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | ○ | ON | A604_B
A605_B | ○ | ON | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | ○ | ON | A606_B
A607_B | ○ | ON |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | ○ | ON | A608_B
A609_B | ○ | ON |  |  | 0 |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  |  | 0 |  | ○ | ON | A610_B
A402_B2 | ○ | ON | 0 |  |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A | 0 |  |  |  | ○ | ON | A503_B2
A506_B2 | ○ | ON |  | 0 |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  | 0 |  |  | ○ | OFF | 08_B
07_B | ○ | OFF |  |  | 0 |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  |  | 0 |  | ○ | OFF | 06_B
05_B | ○ | OFF | 0 |  |  |  | 2P 30A | #43 |  |  | #44 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0.44 | 3.37 | 0
4-DaHall 1-PDU-13 | [8 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 0 |  |  | X | OFF
A701_A1 | ○ | ON |  |  | 0 |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  |  | 0 |  | ○ | ON | A701_A2
A702_A1 | ○ | ON | 0 |  |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A | 0 |  |  |  | ○ | ON | A702_A2
A703_A | ○ | ON |  | 0 |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  | 0 |  |  | ○ | ON | A704_A
A705_A | ○ | ON |  |  | 0 |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  |  | 0 |  | ○ | ON | A706_A1
A707_A | ○ | ON | 0 |  |  |  | 2P 30A | #13 |  |  | #14 | 2P 30A | 0 |  |  |  | ○ | ON | A708_A
A709_A | ○ | ON |  | 0 |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A |  | 0 |  |  | ○ | ON | A710_A
A801_A | ○ | ON |  |  | 0 |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  |  | 0 |  | ○ | ON | A802_A
A803_A | ○ | ON | 0 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 30A | 0 |  |  |  | ○ | ON | A805_A1
A805_A2 | ○ | ON |  | 0 |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A |  | 0 |  |  | ○ | ON | A806_A1
A807_A | ○ | ON |  |  | 0 |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  |  | 0 |  | ○ | ON | A808_A
A809_A | ○ | ON | 0 |  |  |  | 2P 30A | #25 |  |  | #26 | 2P 30A | 0 |  |  |  | ○ | ON | A810_A
A901_A | ○ | ON |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | ○ | ON | A907_A2
A902_A | ○ | ON |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | ○ | ON | A903_A
A904_A | ○ | ON | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | ○ | ON | A905_A
A906_A | ○ | ON |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | ○ | ON | A907_A1
A908_A | ○ | ON |  |  | 0 |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  |  | 0 |  | ○ | ON | A909_A
A910_A | ○ | ON | 0 |  |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A | 0 |  |  |  | ○ | ON | A706_A2
A806_A2 | ○ | ON |  | 0 |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  | 0 |  |  | ○ | ON | 04_A
03_A | ○ | ON |  |  | 0 |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  |  | 0 |  | ○ | ON | 02_A
01_A | ○ | ON | 0 |  |  |  | 2P 30A | #43 |  |  | #44 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
4-DaHall 1-PDU-14 | [8 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 0 |  |  | X | OFF
A701_B1 | ○ | ON |  |  | 0 |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  |  | 0 |  | ○ | ON | A701_B2
A702_B1 | ○ | ON | 0 |  |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A | 0 |  |  |  | ○ | ON | A702_B2
A703_B | ○ | ON |  | 0 |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  | 0 |  |  | ○ | ON | A704_B
A705_B | ○ | ON |  |  | 0 |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  |  | 0 |  | ○ | ON | A706_B1
A707_B | ○ | ON | 0.65 |  |  |  | 2P 30A | #13 |  |  | #14 | 2P 30A | 0 |  |  |  | ○ | ON | A708_B
A709_B | ○ | ON |  | 0 |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A |  | 0 |  |  | ○ | ON | A710_B
A801_B | ○ | ON |  |  | 0 |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  |  | 0 |  | ○ | ON | A802_B
A803_B | ○ | ON | 0 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 30A | 0 |  |  |  | ○ | ON | A805_B1
A805_B2 | ○ | ON |  | 0 |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A |  | 0 |  |  | ○ | ON | A806_B1
A807_B | ○ | ON |  |  | 0 |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  |  | 0 |  | ○ | ON | A808_B
A809_B | ○ | ON | 0 |  |  |  | 2P 30A | #25 |  |  | #26 | 2P 30A | 0 |  |  |  | ○ | ON | A810_B
A901_B | ○ | ON |  | 5.85 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | ○ | ON | A907_B2
A902_B | ○ | ON |  |  | 5.99 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | ○ | ON | A903_B
A904_B | ○ | ON | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | ○ | ON | A905_B
A906_B | ○ | ON |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | ○ | ON | A907_B1
A908_B | ○ | ON |  |  | 0 |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  |  | 0 |  | ○ | ON | A909_B
A910_B | ○ | ON | 0 |  |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A | 5.8 |  |  |  | ○ | ON | A706_B2
A806_B2 | ○ | ON |  | 0 |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  | 1.26 |  |  | ○ | ON | 04_B
03_B | ○ | ON |  |  | 5.95 |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  |  | 0 |  | ○ | ON | 02_B
01_B | ○ | ON | 0 |  |  |  | 2P 30A | #43 |  |  | #44 | 2P 30A | 6.05 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A |  | 5.86 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 12.5 | 12.97 | 11.94
4-DaHall 1-RPP-01 |  |  | Main CB 3P 125A | [6 empty] | 4-DaHall 1-RPP-02 |  |  | Main CB 3P 125A
|  | MAIN 계측값 : |  |  |  | <- 실측값 | [5 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
A404_A2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #01 |  | A404_B2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #01
A406_A2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #02 |  | A406_B2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #02
A408_A2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #03 |  | A408_B2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #03
A804_A | O | ON | 0 | 0 | 0 |  | 3P 30A | #04 |  | A804_B | O | ON | 0 | 0 | 0 |  | 3P 30A | #04
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #05 |  |  | X | OFF | 0 | 0 | 0 |  | 3P 30A | #05
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #06 |  |  | X | OFF | 0 | 0 | 0 |  | 3P 30A | #06
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #07 |  |  | X | OFF | 0 | 0 | 0 |  | 3P 30A | #07
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #08 |  |  | X | OFF | 0 | 0 | 0 |  | 3P 30A | #08
|  | 합계: | 0 | 0 | 0 | [6 empty] | 합계: | 0 | 0 | 0
|  |  |  | 사용량 | 층당 분배
4층 | IDC | IDC |  | 698.64 | 61.4%
| IP | 세종 시스템 |  | 0 | 0%
| 공통 | 세종 시스템
| IP | core room |  | 439.16 | 38.6%
총합 |  |  |  | 1137.8 | 100%
4층 항온항습기 비상 (4층 5RT x 3대, 10RT x 1대) | [8 empty] | Main CB 3P 150A
[11 empty] | MAIN 계측값 : | 24.1 | 22 | 21.9 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | 부하명 | CB 용량 | R | S | T | N | 배선연결 | ON/OFF |  | NO.
4-1 호 | O | ON |  |  |  |  | 3P 50A |  |  | 4-4호 | 3P 50A |  |  |  |  | O | ON
4-2 호 | O | ON |  |  |  | 0 | 3P 50A |  |  |  | 3P 50A |  |  |  |  | X | OFF
4-3 호 | O | ON |  |  |  | 0.1 | 3P 50A |  |  |  | 3P 50A |  |  |  |  | X | OFF
[11 empty] | 합계: | 0 | 0 | 0

## 4층_부하량(월간_AVG)
Date : 2024-01-01 ~ 2024-01-31
4-DaHall 1-PDU-02 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B1 |  |  |  | 4-DaHall 1-PDU-04 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B2
|  | MAIN 계측값 : | 73.5 | 46 | 65.4 | <- 실측값 | [5 empty] | MAIN 계측값 : | 70.2 | 42.2 | 22.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
정류기 1호기 | O | ON | 0.76489 | 0.62691 | 0.93398 |  | 4P 100A | #01 | 코어룸 |  | X | OFF | 0 | 0 | 0 |  | 4P 100A | #01
POP E(상) | O | ON | 35.0725 |  |  |  | 2P 100A | #02 | 코어룸 | POP F(상) | O | ON | 39.458 |  |  |  | 2P 100A | #02 | 코어룸
POP B(상) | O | ON |  | 32.4505 |  |  | 2P 100A | #03 | 코어룸 | IDC 1구역 B(상) | O | ON |  | 28.4812 |  |  | 2P 100A | #03 | 코어룸
POP C(상) | O | ON |  |  | 35.8779 |  | 2P 100A | #04 | 코어룸 | IDC 1구역 C(상) | X | OFF |  |  | 0 |  | 2P 100A | #04 | 코어룸
POP D(상) | O | ON | 40.9814 |  |  |  | 2P 100A | #05 | 코어룸 | IDC 1구역 D(상) | O | ON | 9.7623 |  |  |  | 2P 100A | #05 | 코로케션
IDC 2구역 I(상) | O | ON |  | 12.237 |  |  | 2P 100A | #06 | 코로케션 | IDC 1구역 E(상) | O | ON |  | 14.2855 |  |  | 2P 100A | #06 | 코로케션
IDC 2구역 H(상) | O | ON |  |  | 28.9762 |  | 2P 100A | #07 | 코로케션 | IDC 1구역 F(상) | O | ON |  |  | 21.233 |  | 2P 100A | #07 | 코로케션
| X | OFF | 0 |  |  |  | 2P 100A | #08 |  | IDC 1구역 G(상) | O | ON | 22.1764 |  |  |  | 2P 100A | #08 | 코로케션
| X | OFF |  | 0 |  |  | 2P 100A | #09 |  |  | X | OFF |  | 0 |  |  | 2P 100A | #09
|  | 합계: | 76.8188 | 45.3144 | 65.7881 | [6 empty] | 합계: | 71.3967 | 42.7667 | 21.233
4-DaHall 1-PDU-06 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B3 |  |  |  | 4-DaHall 1-PDU-08 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B4
|  | MAIN 계측값 : | 67 | 32.4 | 27 | <- 실측값 | [5 empty] | MAIN 계측값 : | 44.8 | 68.4 | 18 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
IDC 2구역 J(상) | O | ON | 10.5706 |  |  |  | 2P 100A | #01 | 코로케션 | K 2-1-상 | O | ON | 22.8002 |  |  |  | 2P 100A | #01 | 세틀뱅크(구 시스케어)
IDC 2구역 K(상) | O | ON |  | 0 |  |  | 2P 100A | #02 | 코로케션 | K 3-1 상 | O | ON |  | 33.2786 |  |  | 2P 100A | #02 | 미디어꾼(구)윈텔)
IDC 2구역 L(상) | O | ON |  |  | 8.9381 |  | 2P 100A | #03 | 코로케션 | K 2-2-상 | O | ON |  |  | 5.3758 |  | 2P 100A | #03 | 세틀뱅크(구 시스케어)
IDC 2구역 M(상) | O | ON | 6.9198 |  |  |  | 2P 100A | #04 | 코로케션 | K 3-2 상 | O | ON | 9.4757 |  |  |  | 2P 100A | #04 | 미디어꾼(구)윈텔)
IDC 3구역 N(상) | O | ON |  | 0 |  |  | 2P 100A | #05 | 코로케션 | K 2-3-상 | O | ON |  | 7.4283 |  |  | 2P 100A | #05 | 세틀뱅크(구 시스케어)
IDC 3구역 O(상) | O | ON |  |  | 0 |  | 2P 100A | #06 | 코로케션 | K 3-3 상 | O | ON |  |  | 12.136 |  | 2P 100A | #06 | 미디어꾼(구)윈텔)
IDC 3구역 P(상) | O | ON | 8.5589 |  |  |  | 2P 100A | #07 | 코로케션 | K 2-4 상 | O | ON | 13.0373 |  |  |  | 2P 100A | #07 | 세틀뱅크(구 시스케어)
IDC 3구역 Q(상) | O | ON |  | 13.8972 |  |  | 2P 100A | #08 | 코로케션 | K 3-4 상 | O | ON |  | 26.6682 |  |  | 2P 100A | #08 | 미디어꾼(구)윈텔)
IDC 3구역 R(상) | O | OFF |  |  | 0 |  | 2P 100A | #09 | 코로케션 | K 1-1 상 | O | ON |  |  | 0 |  | 2P 100A | #09 | BMW
IDC 3구역 S(상) | O | ON | 38.5282 |  |  |  | 2P 100A | #10 | 코로케션 | K 1-2 상 | O | ON | 0 |  |  |  | 2P 100A | #10 | 세종시스템케이지
| X | OFF |  | 0 |  |  | 2P 100A | #11 |  |  | X | OFF |  | 0 |  |  | 2P 100A | #11
| X | OFF |  |  | 0 |  | 2P 100A | #12 |  |  | X | OFF |  |  | 0 |  | 2P 100A | #12
|  | 합계: | 64.5776 | 13.8972 | 8.9381 | [6 empty] | 합계: | 45.3131 | 67.3751 | 17.5118
4-DaHall 1-PDU-10 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B5 |  |  |  | 4-DaHall 1-PDU-01 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A1
|  | MAIN 계측값 : | 46.5 | 43.9 | 43.5 | <- 실측값 | [5 empty] | MAIN 계측값 : | 77.6 | 59.1 | 50.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
라온 - 철거 | O | OFF | 0 | 0 | 0 |  | 4P 200A | #01 |  | 정류기 2호기 | O | ON | 1.3729 | 1.0805 | 1.5629 |  | 4P 100A | #01 | 코어룸
CRAC 4E-1호기(20RT) | O | ON | 30.907 | 28.3418 | 29.8349 |  | 4P 200A | #02 | 항온 | POP E(하) | O | ON | 37.4027 |  |  |  | 2P 100A | #02 | 코어룸
CRAC 4E-2호기(20RT) | O | ON | 15.2903 | 14.9519 | 14.7226 |  | 4P 200A | #03 | 항온 | POP B(하) | O | ON |  | 34.2061 |  |  | 2P 100A | #03 | 코어룸
|  | 합계: | 46.1973 | 43.2937 | 44.5575 | 0 |  |  |  | POP C(하) | O | ON |  |  | 37.1317 |  | 2P 100A | #04 | 코어룸
[10 empty] | POP D(하) | O | ON | 41.454 |  |  |  | 2P 100A | #05 | 코어룸
[10 empty] | IDC 2구역 I(하) | O | ON |  | 23.6876 |  |  | 2P 100A | #06 | 코로케션
[10 empty] | IDC 2구역 H(하) | O | ON |  |  | 12.6612 |  | 2P 100A | #07 | 코로케션
[11 empty] | X | OFF | 0 |  |  |  | 2P 100A | #08
[11 empty] | X | OFF |  | 0 |  |  | 2P 100A | #09
[12 empty] | 합계: | 80.2296 | 58.9742 | 51.3558
4-DaHall 1-PDU-03 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A2 |  |  |  | 4-DaHall 1-PDU-05 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A3
|  | MAIN 계측값 : | 57.4 | 38.8 | 25.4 | <- 실측값 | [5 empty] | MAIN 계측값 : | 59.5 | 27.6 | 25.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
| X | OFF | 0 | 0 | 0 |  | 4P 100A | #01 |  | IDC 2구역 J(하) | O | ON | 8.9845 |  |  |  | 2P 100A | #01 | 코로케션
POP F(하) | O | ON | 32.2014 |  |  |  | 2P 100A | #02 | 코어룸 | IDC 2구역 K(하) | O | ON |  | 0 |  |  | 2P 100A | #02 | 코로케션
IDC 1구역 B(하) | O | ON |  | 28.08 |  |  | 2P 100A | #03 | 코어룸 | IDC 2구역 L(하) | O | ON |  |  | 7.7143 |  | 2P 100A | #03 | 코로케션
IDC 1구역 C(하) | X | OFF |  |  | 0 |  | 2P 100A | #04 | 코어룸 | IDC 2구역 M(하) | O | ON | 7.2079 |  |  |  | 2P 100A | #04 | 코로케션
IDC 1구역 D(하) | O | ON | 6.394 |  |  |  | 2P 100A | #05 | 코로케션 | IDC 3구역 N(하) | O | ON |  | 0 |  |  | 2P 100A | #05 | 코로케션
IDC 1구역 E(하) | O | ON |  | 10.2225 |  |  | 2P 100A | #06 | 코로케션 | IDC 3구역 O(하) | O | ON |  |  | 12.8443 |  | 2P 100A | #06 | 코로케션
IDC 1구역 F(하) | O | ON |  |  | 28.9908 |  | 2P 100A | #07 | 코로케션 | IDC 3구역 P(하) | O | ON | 6.7918 |  |  |  | 2P 100A | #07 | 코로케션
IDC 1구역 G(하) | O | ON | 18.4772 |  |  |  | 2P 100A | #08 | 코로케션 | IDC 3구역 Q(하) | O | ON |  | 13.3068 |  |  | 2P 100A | #08 | 코로케션
| X | OFF |  | 0 |  |  | 2P 100A | #09 |  | IDC 3구역 R(하) | O | OFF |  |  | 0 |  | 2P 100A | #09 | 코로케션
|  | 합계: | 57.0726 | 38.3025 | 28.9908 |  |  |  |  | IDC 3구역 S(하) | O | ON | 31.9029 |  |  |  | 2P 100A | #10 | 코로케션
[11 empty] | X | OFF |  | 0 |  |  | 2P 100A | #11
[11 empty] | X | OFF |  |  | 0 |  | 2P 100A | #12
[12 empty] | 합계: | 54.8871 | 13.3068 | 20.5587
4-DaHall 1-PDU-07 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A4 |  |  |  | 4-DaHall 1-PDU-09 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A5
|  | MAIN 계측값 : | 44.7 | 76.7 | 22 | <- 실측값 | [5 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 2-1-하 | O | ON | 20.5084 |  |  |  | 2P 100A | #01 | 세틀뱅크(구 시스케어) | 라온(상)- 철거 | X | OFF | 0 | 0 | 0 |  | 4P 200A | #01
K 3-1-하 | O | ON |  | 33.5524 |  |  | 2P 100A | #02 | 미디어꾼(구)윈텔) |  | X | OFF | 0 | 0 | 0 |  | 4P 200A | #02
K 2-2-하 | O | ON |  |  | 5.2835 |  | 2P 100A | #03 | 세틀뱅크(구 시스케어) |  | X | OFF | 0 | 0 | 0 |  | 4P 200A | #03
K 3-2-하 | O | ON | 10.3815 |  |  |  | 2P 100A | #04 | 미디어꾼(구)윈텔) |  |  | 합계: | 0 | 0 | 0
K 2-3-하 | O | ON |  | 6.0018 |  |  | 2P 100A | #05 | 세틀뱅크(구 시스케어) | TR Room A,B
K 3-3-하 | O | ON |  |  | 15.8815 |  | 2P 100A | #06 | 미디어꾼(구)윈텔) | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 2-4-하 | O | ON | 13.8157 |  |  |  | 2P 100A | #07 | 세틀뱅크(구 시스케어) | KB증권 DR(A) - 철거 | X | OFF |  |  |  |  | 4P 320A | #07
K 3-4-하 | O | ON |  | 34.5307 |  |  | 2P 100A | #08 | 미디어꾼(구)윈텔)
K 1-1-하 | O | ON |  |  | 0 |  | 2P 100A | #09 | BMW | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 1-2-하 | O | ON | 0 |  |  |  | 2P 100A | #10 | 세종시스템케이지 | KB증권 DR(B) - 철거 | X | OFF |  |  |  |  | 4P 320A | #07
| X | OFF |  | 0 |  |  | 2P 100A | #11
| X | OFF |  |  | 0 |  | 2P 100A | #12
|  | 합계: | 44.7055 | 74.0849 | 21.165
4-DaHall 1-PDU-11 | [8 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RPP-01 | ○ | ON | 0.44 | 0.34959 | 0.34999 |  | 4P 125A | #01 |  |  | #02 | 2P 50A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 0 |  | X | OFF
A401_A | ○ | ON | 0 |  |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A | 0 |  |  |  | ○ | ON | A402_A1
A403_A | ○ | ON |  | 0 |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  | 0 |  |  | ○ | ON | A404_A1
A405_A | ○ | ON |  |  | 0 |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  |  | 0 |  | ○ | ON | A406_A1
A407_A | ○ | ON | 0 |  |  |  | 2P 30A | #13 |  |  | #14 | 2P 30A | 0 |  |  |  | ○ | ON | A408_A1
A409_A | ○ | ON |  | 0 |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A |  | 0 |  |  | ○ | ON | A410_A
A501_A | ○ | ON |  |  | 0 |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  |  | 0 |  | ○ | ON | A502_A
A503_A1 | ○ | ON | 0 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 30A | 0 |  |  |  | ○ | ON | A504_A
A505_A | ○ | ON |  | 0 |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A |  | 0 |  |  | ○ | ON | A506_A1
A507_A | ○ | ON |  |  | 0 |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  |  | 0 |  | ○ | ON | A508_A
A509_A | ○ | ON | 0 |  |  |  | 2P 30A | #25 |  |  | #26 | 2P 30A | 0 |  |  |  | ○ | ON | A510_A
A601_A | ○ | ON |  | 0.28 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0.22021 |  |  | ○ | ON | A602_A
A603_A | ○ | ON |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | ○ | ON | A604_A
A605_A | ○ | ON | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | ○ | ON | A606_A
A607_A | ○ | ON |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | ○ | ON | A608_A
A609_A | ○ | ON |  |  | 0 |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  |  | 0 |  | ○ | ON | A610_A
A402_A2 | ○ | ON | 0 |  |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A | 0 |  |  |  | ○ | ON | A503_A2
A506_A2 | ○ | ON |  | 0 |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  | 0 |  |  | ○ | OFF | 08_A
07_A | ○ | OFF |  |  | 0 |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  |  | 0 |  | ○ | OFF | 06_A
05_A | ○ | OFF | 0 |  |  |  | 2P 30A | #43 |  |  | #44 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0.44 | 0.84979 | 0.34999
4-DaHall 1-PDU-12 | [8 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RPP-01 | ○ | ON | 0.44 | 0.2 | 0 |  | 4P 125A | #01 |  |  | #02 | 2P 50A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 0 |  | X | OFF
A401_B | ○ | ON | 0 |  |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A | 0 |  |  |  | ○ | ON | A402_B1
A403_B | ○ | ON |  | 0 |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  | 0 |  |  | ○ | ON | A404_B1
A405_B | ○ | ON |  |  | 0 |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  |  | 0 |  | ○ | ON | A406_B1
A407_B | ○ | ON | 0 |  |  |  | 2P 30A | #13 |  |  | #14 | 2P 30A | 0 |  |  |  | ○ | ON | A408_B1
A409_B | ○ | ON |  | 0 |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A |  | 0 |  |  | ○ | ON | A410_B
A501_B | ○ | ON |  |  | 0 |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  |  | 0 |  | ○ | ON | A502_B
A503_B1 | ○ | ON | 0 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 30A | 0 |  |  |  | ○ | ON | A504_B
A505_B | ○ | ON |  | 0 |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A |  | 0 |  |  | ○ | ON | A506_B1
A507_B | ○ | ON |  |  | 0 |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  |  | 0 |  | ○ | ON | A508_B
A509_B | ○ | ON | 0 |  |  |  | 2P 30A | #25 |  |  | #26 | 2P 30A | 0 |  |  |  | ○ | ON | A510_B
A601_B | ○ | ON |  | 2.1701 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0.94375 |  |  | ○ | ON | A602_B
A603_B | ○ | ON |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | ○ | ON | A604_B
A605_B | ○ | ON | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | ○ | ON | A606_B
A607_B | ○ | ON |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | ○ | ON | A608_B
A609_B | ○ | ON |  |  | 0 |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  |  | 0 |  | ○ | ON | A610_B
A402_B2 | ○ | ON | 0 |  |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A | 0 |  |  |  | ○ | ON | A503_B2
A506_B2 | ○ | ON |  | 0 |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  | 0 |  |  | ○ | OFF | 08_B
07_B | ○ | OFF |  |  | 0 |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  |  | 0 |  | ○ | OFF | 06_B
05_B | ○ | OFF | 0 |  |  |  | 2P 30A | #43 |  |  | #44 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0.44 | 3.3139 | 0
4-DaHall 1-PDU-13 | [8 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 0 |  |  | X | OFF
A701_A1 | ○ | ON |  |  | 0 |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  |  | 0 |  | ○ | ON | A701_A2
A702_A1 | ○ | ON | 0 |  |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A | 0 |  |  |  | ○ | ON | A702_A2
A703_A | ○ | ON |  | 0 |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  | 0 |  |  | ○ | ON | A704_A
A705_A | ○ | ON |  |  | 0 |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  |  | 0 |  | ○ | ON | A706_A1
A707_A | ○ | ON | 0 |  |  |  | 2P 30A | #13 |  |  | #14 | 2P 30A | 0 |  |  |  | ○ | ON | A708_A
A709_A | ○ | ON |  | 0 |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A |  | 0 |  |  | ○ | ON | A710_A
A801_A | ○ | ON |  |  | 0 |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  |  | 0 |  | ○ | ON | A802_A
A803_A | ○ | ON | 0 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 30A | 0 |  |  |  | ○ | ON | A805_A1
A805_A2 | ○ | ON |  | 0 |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A |  | 0 |  |  | ○ | ON | A806_A1
A807_A | ○ | ON |  |  | 0 |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  |  | 0 |  | ○ | ON | A808_A
A809_A | ○ | ON | 0 |  |  |  | 2P 30A | #25 |  |  | #26 | 2P 30A | 0 |  |  |  | ○ | ON | A810_A
A901_A | ○ | ON |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | ○ | ON | A907_A2
A902_A | ○ | ON |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | ○ | ON | A903_A
A904_A | ○ | ON | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | ○ | ON | A905_A
A906_A | ○ | ON |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | ○ | ON | A907_A1
A908_A | ○ | ON |  |  | 0 |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  |  | 0 |  | ○ | ON | A909_A
A910_A | ○ | ON | 0 |  |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A | 0 |  |  |  | ○ | ON | A706_A2
A806_A2 | ○ | ON |  | 0 |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  | 0 |  |  | ○ | ON | 04_A
03_A | ○ | ON |  |  | 0 |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  |  | 0 |  | ○ | ON | 02_A
01_A | ○ | ON | 0 |  |  |  | 2P 30A | #43 |  |  | #44 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
4-DaHall 1-PDU-14 | [8 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 0 |  |  | X | OFF
A701_B1 | ○ | ON |  |  | 0 |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  |  | 0 |  | ○ | ON | A701_B2
A702_B1 | ○ | ON | 0 |  |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A | 0 |  |  |  | ○ | ON | A702_B2
A703_B | ○ | ON |  | 0 |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  | 0 |  |  | ○ | ON | A704_B
A705_B | ○ | ON |  |  | 0 |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  |  | 0 |  | ○ | ON | A706_B1
A707_B | ○ | ON | 0.00045139 |  |  |  | 2P 30A | #13 |  |  | #14 | 2P 30A | 0 |  |  |  | ○ | ON | A708_B
A709_B | ○ | ON |  | 0 |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A |  | 0 |  |  | ○ | ON | A710_B
A801_B | ○ | ON |  |  | 0 |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  |  | 0 |  | ○ | ON | A802_B
A803_B | ○ | ON | 0 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 30A | 0 |  |  |  | ○ | ON | A805_B1
A805_B2 | ○ | ON |  | 0 |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A |  | 0 |  |  | ○ | ON | A806_B1
A807_B | ○ | ON |  |  | 0 |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  |  | 0 |  | ○ | ON | A808_B
A809_B | ○ | ON | 0 |  |  |  | 2P 30A | #25 |  |  | #26 | 2P 30A | 0 |  |  |  | ○ | ON | A810_B
A901_B | ○ | ON |  | 0.0040625 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | ○ | ON | A907_B2
A902_B | ○ | ON |  |  | 0.0041626 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | ○ | ON | A903_B
A904_B | ○ | ON | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | ○ | ON | A905_B
A906_B | ○ | ON |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | ○ | ON | A907_B1
A908_B | ○ | ON |  |  | 0 |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  |  | 0 |  | ○ | ON | A909_B
A910_B | ○ | ON | 0 |  |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A | 0.0040306 |  |  |  | ○ | ON | A706_B2
A806_B2 | ○ | ON |  | 0 |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  | 0.00087561 |  |  | ○ | ON | 04_B
03_B | ○ | ON |  |  | 0.0041319 |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  |  | 0 |  | ○ | ON | 02_B
01_B | ○ | ON | 0 |  |  |  | 2P 30A | #43 |  |  | #44 | 2P 30A | 0.0082557 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A |  | 0.0040694 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 0.012738 | 0.0090076 | 0.0082946
4-DaHall 1-RPP-01 |  |  | Main CB 3P 125A | [6 empty] | 4-DaHall 1-RPP-02 |  |  | Main CB 3P 125A
|  | MAIN 계측값 : |  |  |  | <- 실측값 | [5 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
A404_A2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #01 |  | A404_B2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #01
A406_A2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #02 |  | A406_B2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #02
A408_A2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #03 |  | A408_B2 | O | ON | 0 | 0 | 0 |  | 3P 30A | #03
A804_A | O | ON | 0 | 0 | 0 |  | 3P 30A | #04 |  | A804_B | O | ON | 0 | 0 | 0 |  | 3P 30A | #04
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #05 |  |  | X | OFF | 0 | 0 | 0 |  | 3P 30A | #05
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #06 |  |  | X | OFF | 0 | 0 | 0 |  | 3P 30A | #06
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #07 |  |  | X | OFF | 0 | 0 | 0 |  | 3P 30A | #07
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #08 |  |  | X | OFF | 0 | 0 | 0 |  | 3P 30A | #08
|  | 합계: | 0 | 0 | 0 | [6 empty] | 합계: | 0 | 0 | 0
|  |  |  | 사용량 | 층당 분배
4층 | IDC | IDC |  | 655.4243 | 60.43%
| IP | 세종 시스템 |  | 0 | 0%
| 공통 | 세종 시스템
| IP | core room |  | 429.1395 | 39.57%
총합 |  |  |  | 1084.5638 | 100%
4층 항온항습기 비상 (4층 5RT x 3대, 10RT x 1대) | [8 empty] | Main CB 3P 150A
[11 empty] | MAIN 계측값 : | 24.1 | 22 | 21.9 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | 부하명 | CB 용량 | R | S | T | N | 배선연결 | ON/OFF |  | NO.
4-1 호 | O | ON |  |  |  |  | 3P 50A |  |  | 4-4호 | 3P 50A |  |  |  |  | O | ON
4-2 호 | O | ON |  |  |  | 0 | 3P 50A |  |  |  | 3P 50A |  |  |  |  | X | OFF
4-3 호 | O | ON |  |  |  | 0.1 | 3P 50A |  |  |  | 3P 50A |  |  |  |  | X | OFF
[11 empty] | 합계: | 0 | 0 | 0

## 7층_부하량
장비명 | 분기번호 | MIN |  |  | MAX |  |  | AVG
|  | R | S | T | R | S | T | R | S | T
7-DaHall 1-RPP-01 | 1 | 0 |  |  | 0
7-DaHall 1-RPP-01 | 2 | 0 |  |  | 0
7-DaHall 1-RPP-01 | 3 |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 4 |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 5 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 6 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 7 | 0 |  |  | 0
7-DaHall 1-RPP-01 | 8 | 2.38 |  |  | 2.4 |  |  | 2.39
7-DaHall 1-RPP-01 | 9 |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 10 |  | 1.67 |  |  | 1.68 |  |  | 1.6797
7-DaHall 1-RPP-01 | 11 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 12 |  |  | 3.36 |  |  | 5.58 |  |  | 4.1494
7-DaHall 1-RPP-01 | 13 | 0 |  |  | 0
7-DaHall 1-RPP-01 | 14 | 6.26 |  |  | 7.19 |  |  | 6.4544
7-DaHall 1-RPP-01 | 15 |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 16 |  | 2.54 |  |  | 2.66 |  |  | 2.6061
7-DaHall 1-RPP-01 | 17 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 18 |  |  | 1.28 |  |  | 2.04 |  |  | 1.5619
7-DaHall 1-RPP-01 | 19 | 0.99 |  |  | 1.04 |  |  | 1.0023
7-DaHall 1-RPP-01 | 20 | 1.48 |  |  | 1.51 |  |  | 1.4935
7-DaHall 1-RPP-01 | 21 |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 22 |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 23 |  |  | 1.44 |  |  | 2.12 |  |  | 1.5585
7-DaHall 1-RPP-01 | 24 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 25 | 1.5 |  |  | 1.53 |  |  | 1.5116
7-DaHall 1-RPP-01 | 26 | 1.52 |  |  | 4.54 |  |  | 3.3147
7-DaHall 1-RPP-01 | 27 |  | 2.96 |  |  | 3.53 |  |  | 3.1544
7-DaHall 1-RPP-01 | 28 |  | 0.87 |  |  | 4.32 |  |  | 1.6154
7-DaHall 1-RPP-01 | 29 |  |  | 3.94 |  |  | 4.6 |  |  | 4.1315
7-DaHall 1-RPP-01 | 30 |  |  | 3.74 |  |  | 5.83 |  |  | 4.2718
7-DaHall 1-RPP-01 | 31 | 5.38 |  |  | 6.61 |  |  | 5.7882
7-DaHall 1-RPP-01 | 32 | 0 |  |  | 0
7-DaHall 1-RPP-01 | 33 |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 34 |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 35 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 36 |  |  | 3.17 |  |  | 4.03 |  |  | 3.4232
7-DaHall 1-RPP-01 | 37 | 5.47 |  |  | 7.12 |  |  | 6.1548
7-DaHall 1-RPP-01 | 38 | 2.16 |  |  | 2.29 |  |  | 2.2006
7-DaHall 1-RPP-01 | 39 |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 40 |  | 4.7 |  |  | 5 |  |  | 4.7992
7-DaHall 1-PDU-02 | 1 |  | 0 |  |  | 0
7-DaHall 1-PDU-02 | 2 |  | 0 |  |  | 0
7-DaHall 1-PDU-02 | 3 |  |  | 5.13 |  |  | 5.27 |  |  | 5.2018
7-DaHall 1-PDU-02 | 4 |  |  | 0 |  |  | 0
7-DaHall 1-PDU-02 | 5 | 0 |  |  | 0
7-DaHall 1-PDU-02 | 6 | 0 |  |  | 0
7-DaHall 1-PDU-02 | 7 |  | 5.7 |  |  | 6.34 |  |  | 5.7373
7-DaHall 1-PDU-02 | 8 |  | 0 |  |  | 0
7-DaHall 1-PDU-02 | 9 |  |  | 4.45 |  |  | 6.04 |  |  | 5.8618
7-DaHall 1-PDU-02 | 10 |  |  | 2.26 |  |  | 4.45 |  |  | 3.4529
7-DaHall 1-PDU-02 | 11 | 5.67 |  |  | 5.72 |  |  | 5.6908
7-DaHall 1-PDU-02 | 12 | 0 |  |  | 0
7-DaHall 1-PDU-02 | 13 |  | 5.22 |  |  | 5.27 |  |  | 5.2444
7-DaHall 1-PDU-02 | 14 |  | 3.06 |  |  | 3.16 |  |  | 3.0858
7-DaHall 1-PDU-02 | 15 |  |  | 1.08 |  |  | 1.09 |  |  | 1.08
7-DaHall 1-PDU-02 | 16 |  |  | 2.92 |  |  | 3.11 |  |  | 2.958
7-DaHall 1-PDU-02 | 17 | 3.27 |  |  | 3.67 |  |  | 3.3793
7-DaHall 1-PDU-02 | 18 | 1.32 |  |  | 2.1 |  |  | 1.7399
7-DaHall 1-PDU-02 | 19 |  | 8.82 |  |  | 9.23 |  |  | 8.9772
7-DaHall 1-PDU-02 | 20 |  | 1.97 |  |  | 3.06 |  |  | 1.9885
7-DaHall 1-PDU-02 | 21 |  |  | 3.85 |  |  | 4.46 |  |  | 4.0522
7-DaHall 1-PDU-02 | 22 |  |  | 1.19 |  |  | 1.98 |  |  | 1.9621
7-DaHall 1-PDU-02 | 23 | 2.54 |  |  | 2.89 |  |  | 2.6319
7-DaHall 1-PDU-02 | 24 | 2.21 |  |  | 2.7 |  |  | 2.2777
7-DaHall 1-PDU-02 | 25 |  | 1.72 |  |  | 1.77 |  |  | 1.7329
7-DaHall 1-PDU-02 | 26 |  | 3.57 |  |  | 3.65 |  |  | 3.6147
7-DaHall 1-PDU-02 | 27 |  |  | 3.55 |  |  | 4.23 |  |  | 3.7863
7-DaHall 1-PDU-02 | 28 |  |  | 5.73 |  |  | 5.84 |  |  | 5.7776
7-DaHall 1-PDU-02 | 29 | 1.47 |  |  | 2.48 |  |  | 1.8013
7-DaHall 1-PDU-02 | 30 | 0.51 |  |  | 0.68 |  |  | 0.56793
7-DaHall 1-PDU-02 | 31 |  | 3.65 |  |  | 3.79 |  |  | 3.712
7-DaHall 1-PDU-02 | 32 |  | 1.89 |  |  | 1.91 |  |  | 1.8987
7-DaHall 1-PDU-02 | 33 |  |  | 8.26 |  |  | 8.6 |  |  | 8.3825
7-DaHall 1-PDU-02 | 34 |  |  | 0 |  |  | 0
7-DaHall 1-PDU-02 | 35 | 6.45 |  |  | 6.72 |  |  | 6.5469
7-DaHall 1-PDU-02 | 36 | 0 |  |  | 0
7-DaHall 1-PDU-02 | 37 |  | 0 |  |  | 0.69 |  |  | 0.0040889
7-DaHall 1-PDU-02 | 38 |  | 3.82 |  |  | 4.08 |  |  | 3.8721
7-DaHall 1-PDU-02 | 39 |  |  | 1.83 |  |  | 1.87 |  |  | 1.8556
7-DaHall 1-PDU-02 | 40 |  |  | 2.93 |  |  | 3.34 |  |  | 3.0254
7-DaHall 1-PDU-02 | 41 | 0 |  |  | 0
7-DaHall 1-PDU-02 | 42 | 4.42 |  |  | 4.96 |  |  | 4.4681
7-DaHall 1-PDU-02 | 43 |  | 0 |  |  | 0
7-DaHall 1-PDU-02 | 44 |  | 1.34 |  |  | 3.42 |  |  | 2.3385
7-DaHall 1-PDU-02 | 45 |  |  | 0 |  |  | 0
7-DaHall 1-PDU-02 | 46 |  |  | 0 |  |  | 0
7-DaHall 1-PDU-02 | 47 | 0 |  |  | 0
7-DaHall 1-PDU-02 | 48 | 1.36 |  |  | 3.57 |  |  | 2.6815
7-DaHall 1-PDU-02 | 49 |  | 0.88 |  |  | 0.93 |  |  | 0.90141
7-DaHall 1-PDU-02 | 50 |  | 2.06 |  |  | 3.82 |  |  | 3.5322
7-DaHall 1-PDU-02 | 51 |  |  | 0.55 |  |  | 0.56 |  |  | 0.55004
7-DaHall 1-PDU-02 | 52 |  |  | 0 |  |  | 0
7-DaHall 1-PDU-02 | 53 | 0.23 |  |  | 0.24 |  |  | 0.23004
7-DaHall 1-PDU-02 | 54 | 0 |  |  | 0
7-DaHall 1-PDU-01 | 1 |  | 0 |  |  | 0
7-DaHall 1-PDU-01 | 2 |  | 0 |  |  | 0
7-DaHall 1-PDU-01 | 3 |  |  | 2.07 |  |  | 3.01 |  |  | 2.4923
7-DaHall 1-PDU-01 | 4 |  |  | 0 |  |  | 0
7-DaHall 1-PDU-01 | 5 | 4.91 |  |  | 5.12 |  |  | 4.9726
7-DaHall 1-PDU-01 | 6 | 0 |  |  | 0
7-DaHall 1-PDU-01 | 7 |  | 5.94 |  |  | 6.22 |  |  | 5.9719
7-DaHall 1-PDU-01 | 8 |  | 1.53 |  |  | 2.29 |  |  | 1.8243
7-DaHall 1-PDU-01 | 9 |  |  | 5.7 |  |  | 7.42 |  |  | 5.8963
7-DaHall 1-PDU-01 | 10 |  |  | 1.48 |  |  | 2.84 |  |  | 2.39
7-DaHall 1-PDU-01 | 11 | 6.79 |  |  | 6.92 |  |  | 6.8332
7-DaHall 1-PDU-01 | 12 | 0 |  |  | 0
7-DaHall 1-PDU-01 | 13 |  | 6.58 |  |  | 6.72 |  |  | 6.6294
7-DaHall 1-PDU-01 | 14 |  | 4.11 |  |  | 4.61 |  |  | 4.2837
7-DaHall 1-PDU-01 | 15 |  |  | 0.78 |  |  | 0.79 |  |  | 0.78998
7-DaHall 1-PDU-01 | 16 |  |  | 2.28 |  |  | 2.45 |  |  | 2.3023
7-DaHall 1-PDU-01 | 17 | 2.73 |  |  | 3.24 |  |  | 2.9146
7-DaHall 1-PDU-01 | 18 | 1.33 |  |  | 2.14 |  |  | 1.7558
7-DaHall 1-PDU-01 | 19 |  | 3.87 |  |  | 4.21 |  |  | 3.9278
7-DaHall 1-PDU-01 | 20 |  | 0.9 |  |  | 1.88 |  |  | 1.8689
7-DaHall 1-PDU-01 | 21 |  |  | 3.87 |  |  | 4.12 |  |  | 3.95
7-DaHall 1-PDU-01 | 22 |  |  | 1.7 |  |  | 1.77 |  |  | 1.7334
7-DaHall 1-PDU-01 | 23 | 1.74 |  |  | 2.09 |  |  | 1.8176
7-DaHall 1-PDU-01 | 24 | 2.58 |  |  | 3.18 |  |  | 2.7407
7-DaHall 1-PDU-01 | 25 |  | 1.44 |  |  | 1.65 |  |  | 1.4568
7-DaHall 1-PDU-01 | 26 |  | 3.35 |  |  | 3.46 |  |  | 3.4165
7-DaHall 1-PDU-01 | 27 |  |  | 3.21 |  |  | 3.58 |  |  | 3.2932
7-DaHall 1-PDU-01 | 28 |  |  | 5.5 |  |  | 5.63 |  |  | 5.5626
7-DaHall 1-PDU-01 | 29 | 0 |  |  | 0.4 |  |  | 0.003338
7-DaHall 1-PDU-01 | 30 | 0.34 |  |  | 0.35 |  |  | 0.34967
7-DaHall 1-PDU-01 | 31 |  | 4.44 |  |  | 4.59 |  |  | 4.519
7-DaHall 1-PDU-01 | 32 |  | 2.09 |  |  | 2.21 |  |  | 2.1083
7-DaHall 1-PDU-01 | 33 |  |  | 8.55 |  |  | 8.96 |  |  | 8.6702
7-DaHall 1-PDU-01 | 34 |  |  | 0 |  |  | 0
7-DaHall 1-PDU-01 | 35 | 6.51 |  |  | 7.11 |  |  | 6.7996
7-DaHall 1-PDU-01 | 36 | 0 |  |  | 0
7-DaHall 1-PDU-01 | 37 |  | 0 |  |  | 0
7-DaHall 1-PDU-01 | 38 |  | 2.75 |  |  | 3.02 |  |  | 2.808
7-DaHall 1-PDU-01 | 39 |  |  | 1.03 |  |  | 1.06 |  |  | 1.0399
7-DaHall 1-PDU-01 | 40 |  |  | 3.31 |  |  | 3.67 |  |  | 3.3906
7-DaHall 1-PDU-01 | 41 | 1.05 |  |  | 1.07 |  |  | 1.0602
7-DaHall 1-PDU-01 | 42 | 3.32 |  |  | 3.48 |  |  | 3.3412
7-DaHall 1-PDU-01 | 43 |  | 0 |  |  | 0
7-DaHall 1-PDU-01 | 44 |  | 5.57 |  |  | 8.03 |  |  | 6.7731
7-DaHall 1-PDU-01 | 45 |  |  | 0 |  |  | 0
7-DaHall 1-PDU-01 | 46 |  |  | 0 |  |  | 0
7-DaHall 1-PDU-01 | 47 | 0 |  |  | 0
7-DaHall 1-PDU-01 | 48 | 1 |  |  | 2.9 |  |  | 2.2292
7-DaHall 1-PDU-01 | 49 |  | 0 |  |  | 0
7-DaHall 1-PDU-01 | 50 |  | 0 |  |  | 0
7-DaHall 1-PDU-01 | 51 |  |  | 0 |  |  | 0
7-DaHall 1-PDU-01 | 52 |  |  | 0 |  |  | 0
7-DaHall 1-PDU-01 | 53 | 0 |  |  | 0
7-DaHall 1-PDU-01 | 54 | 0.34 |  |  | 0.35 |  |  | 0.34008
7-DaHall 1-RPP-02 | 1 | 0.87 |  |  | 1.09 |  |  | 0.9106
7-DaHall 1-RPP-02 | 2 | 0 |  |  | 17.49 |  |  | 0.28097
7-DaHall 1-RPP-02 | 3 |  | 0.54 |  |  | 0.8 |  |  | 0.55027
7-DaHall 1-RPP-02 | 4 |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 5 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 6 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 7 | 1.12 |  |  | 1.13 |  |  | 1.1224
7-DaHall 1-RPP-02 | 8 | 5.83 |  |  | 6.67 |  |  | 6.0969
7-DaHall 1-RPP-02 | 9 |  | 0.85 |  |  | 1.57 |  |  | 1.1694
7-DaHall 1-RPP-02 | 10 |  | 0.66 |  |  | 0.71 |  |  | 0.66886
7-DaHall 1-RPP-02 | 11 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 12 |  |  | 3.06 |  |  | 4.69 |  |  | 4.3486
7-DaHall 1-RPP-02 | 13 | 2.84 |  |  | 2.92 |  |  | 2.8659
7-DaHall 1-RPP-02 | 14 | 12.97 |  |  | 15.69 |  |  | 14.0604
7-DaHall 1-RPP-02 | 15 |  | 1.76 |  |  | 1.77 |  |  | 1.7634
7-DaHall 1-RPP-02 | 16 |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 17 |  |  | 2.44 |  |  | 4.59 |  |  | 3.0968
7-DaHall 1-RPP-02 | 18 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 19 | 0 |  |  | 0
7-DaHall 1-RPP-02 | 20 | 0 |  |  | 1.2 |  |  | 0.6567
7-DaHall 1-RPP-02 | 21 |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 22 |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 23 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 24 |  |  | 1.42 |  |  | 4.45 |  |  | 2.2591
7-DaHall 1-RPP-02 | 25 | 0 |  |  | 0
7-DaHall 1-RPP-02 | 26 | 0.28 |  |  | 0.45 |  |  | 0.42936
7-DaHall 1-RPP-02 | 27 |  | 5.65 |  |  | 6.39 |  |  | 5.8135
7-DaHall 1-RPP-02 | 28 |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 29 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 30 |  |  | 1.7 |  |  | 2.4 |  |  | 1.8465
7-DaHall 1-RPP-02 | 31 | 0 |  |  | 0
7-DaHall 1-RPP-02 | 32 | 3.33 |  |  | 3.73 |  |  | 3.4779
7-DaHall 1-RPP-02 | 33 |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 34 |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 35 |  |  | 2.4 |  |  | 3.11 |  |  | 2.539
7-DaHall 1-RPP-02 | 36 |  |  | 6.81 |  |  | 8.22 |  |  | 7.3429
7-DaHall 1-RPP-02 | 37 | 5.44 |  |  | 6.52 |  |  | 5.8492
7-DaHall 1-RPP-02 | 38 | 4.79 |  |  | 5.12 |  |  | 4.9175
7-DaHall 1-RPP-02 | 39 |  | 2.72 |  |  | 14.65 |  |  | 3.1025
7-DaHall 1-RPP-02 | 40 |  | 0 |  |  | 0
7-DaHall 1-RPP-03 | 1 | 0 |  |  | 1.19 |  |  | 1.1335
7-DaHall 1-RPP-03 | 2 | 0.81 |  |  | 1.19 |  |  | 0.88832
7-DaHall 1-RPP-03 | 3 |  | 2.76 |  |  | 2.87 |  |  | 2.7946
7-DaHall 1-RPP-03 | 4 |  | 0 |  |  | 0
7-DaHall 1-RPP-03 | 5 |  |  | 3.36 |  |  | 3.47 |  |  | 3.4057
7-DaHall 1-RPP-03 | 6 |  |  | 1.55 |  |  | 1.72 |  |  | 1.584
7-DaHall 1-RPP-03 | 7 | 2.48 |  |  | 2.61 |  |  | 2.5091
7-DaHall 1-RPP-03 | 8 | 1.94 |  |  | 2.08 |  |  | 1.9716
7-DaHall 1-RPP-03 | 9 |  | 2.72 |  |  | 2.99 |  |  | 2.7464
7-DaHall 1-RPP-03 | 10 |  | 2.57 |  |  | 2.78 |  |  | 2.6123
7-DaHall 1-RPP-04 | 1 | 0 |  |  | 6.2 |  |  | 1.0665
7-DaHall 1-RPP-04 | 2 | 1.55 |  |  | 1.9 |  |  | 1.744
7-DaHall 1-RPP-04 | 3 |  | 3.32 |  |  | 3.39 |  |  | 3.3461
7-DaHall 1-RPP-04 | 4 |  | 0 |  |  | 0
7-DaHall 1-RPP-04 | 5 |  |  | 4.45 |  |  | 4.55 |  |  | 4.4897
7-DaHall 1-RPP-04 | 6 |  |  | 1.19 |  |  | 1.33 |  |  | 1.2212
7-DaHall 1-RPP-04 | 7 | 4.09 |  |  | 4.23 |  |  | 4.1687
7-DaHall 1-RPP-04 | 8 | 1.91 |  |  | 2.07 |  |  | 1.9433
7-DaHall 1-RPP-04 | 9 |  | 1.61 |  |  | 1.77 |  |  | 1.6301
7-DaHall 1-RPP-04 | 10 |  | 2.8 |  |  | 3.01 |  |  | 2.8519
7-DaHall 1-PDU-03 | 1 | 26.65 | 12.11 | 16.87 | 30.18 | 15.55 | 21.14 | 28.6837 | 12.8868 | 18.4604
7-DaHall 1-PDU-03 | 2 | 3.05 | 2.49 | 7.22 | 4.42 | 4.19 | 9.23 | 3.5694 | 2.9388 | 8.0101
7-DaHall 1-PDU-03 | 3 | 5.27 | 7.93 | 4.91 | 6.81 | 8.24 | 5.12 | 6.3958 | 8.0085 | 4.9588
7-DaHall 1-PDU-03 | 4 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-03 | 5 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-03 | 6 | 50.79 | 51.45 | 53.94 | 52.53 | 53.02 | 55.71 | 51.759 | 52.3709 | 54.9917
7-DaHall 1-PDU-03 | 7 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-03 | 8 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-03 | 9 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-03 | 10 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-04 | 1 | 44.75 | 45.63 | 47.97 | 46.47 | 47.22 | 49.94 | 45.7119 | 46.5412 | 49.1551
7-DaHall 1-PDU-04 | 2 | 37.09 | 11.58 | 17.88 | 54.64 | 23.85 | 23.85 | 38.6346 | 12.134 | 20.6119
7-DaHall 1-PDU-04 | 3 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-04 | 4 | 7.78 | 7.57 | 5.59 | 9.11 | 7.82 | 5.78 | 8.8396 | 7.6418 | 5.6394
7-DaHall 1-PDU-04 | 5 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-04 | 6 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-04 | 7 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-04 | 8 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-04 | 9 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-04 | 10 | 0 | 0 | 0 | 0 | 0 | 0

## 6층_부하량
장비명 | 분기번호 | MIN |  |  | MAX |  |  | AVG
|  | R | S | T | R | S | T | R | S | T
6-DaHall 1-CEP-05 | 1 | 0 | 0.75 | 0.68 | 58.76 | 59.71 | 58.23 | 0.25451 | 0.78783 | 0.70159
6-DaHall 1-CEP-05 | 2 | 0 | 0 | 0 | 23.54 | 22.01 | 23.9 | 0.059666 | 0.056372 | 0.061049
6-DaHall 1-CEP-05 | 3 | 0 | 0 | 0 | 0 | 0 | 0
6-DaHall 1-CEP-05 | 4 | 0 | 0 | 0 | 0 | 0 | 0
6-DaHall 1-CEP-05 | 5 | 0 | 0 | 0 | 0 | 0 | 0
6-DaHall 1-CEP-05 | 6 | 0 | 0 | 0 | 0 | 0 | 0
6-DaHall 1-CEP-05 | 7 | 0 | 0 | 0 | 0 | 0 | 0
6-DaHall 1-CEP-05 | 8 | 0 | 0 | 0 | 0 | 0 | 0
6-DaHall 1-CEP-05 | 9 | 0 | 0 | 0 | 0 | 0 | 0
6-DaHall 1-CEP-05 | 10 | 0 | 0 | 0 | 0 | 0 | 0
6-DaHall 1-CEP-05 | 11 | 2.19 | 1.81 | 3.13 | 54.47 | 61.14 | 63.87 | 6.4556 | 11.9344 | 12.1109
6-DaHall 1-CEP-05 | 12 | 0 |  |  | 0
6-DaHall 1-CEP-05 | 13 | 0 |  |  | 0
6-DaHall 1-CEP-05 | 14 |  | 0 |  |  | 0
6-DaHall 1-CEP-05 | 15 |  | 5.15 |  |  | 15.22 |  |  | 9.9254
6-DaHall 1-CEP-05 | 16 |  |  | 0 |  |  | 0
6-DaHall 1-CEP-05 | 17 |  |  | 6.93 |  |  | 22.31 |  |  | 9.5847
6-DaHall 1-PDU-13 | 1 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 2 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 3 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 4 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 5 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 6 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 7 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 8 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 9 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 10 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 11 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 12 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 13 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 14 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 15 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 16 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 17 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 18 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 19 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 20 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 21 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 22 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 23 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 24 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 25 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 26 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 27 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 28 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 29 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 30 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 31 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 32 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 33 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 34 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 35 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 36 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 37 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 38 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 39 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 40 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 41 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 42 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 43 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 44 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 45 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 46 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 47 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 48 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 49 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 50 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 51 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 52 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 53 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 54 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 1 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 2 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 3 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 4 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 5 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 6 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 7 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 8 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 9 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 10 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 11 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 12 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 13 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 14 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 15 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 16 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 17 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 18 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 19 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 20 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 21 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 22 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 23 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 24 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 25 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 26 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 27 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 28 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 29 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 30 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 31 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 32 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 33 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 34 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 35 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 36 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 37 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 38 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 39 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 40 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 41 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 42 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 43 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 44 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 45 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 46 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 47 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 48 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 49 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 50 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 51 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 52 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 53 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 54 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 1 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 2 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 3 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 4 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 5 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 6 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 7 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 8 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 9 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 10 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 11 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 12 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 13 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 14 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 15 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 16 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 17 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 18 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 19 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 20 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 21 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 22 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 23 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 24 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 25 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 26 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 27 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 28 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 29 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 30 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 31 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 32 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 33 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 34 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 35 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 36 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 37 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 38 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 39 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 40 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 41 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 42 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 43 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 44 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 45 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 46 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 47 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 48 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 49 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 50 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 1 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 2 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 3 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 4 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 5 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 6 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 7 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 8 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 9 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 10 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 11 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 12 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 13 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 14 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 15 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 16 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 17 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 18 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 19 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 20 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 21 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 22 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 23 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 24 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 25 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 26 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 27 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 28 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 29 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 30 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 31 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 32 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 33 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 34 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 35 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 36 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 37 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 38 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 39 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 40 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 41 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 42 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 43 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 44 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 45 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 46 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 47 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 48 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 49 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 50 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 1 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 2 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 3 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 4 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 5 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 6 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 7 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 8 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 9 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 10 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 11 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 12 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 13 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 14 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 15 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 16 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 17 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 18 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 19 | 4.92 |  |  | 6.15 |  |  | 5.355
6-DaHall 1-PDU-11 | 20 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 21 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 22 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 23 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 24 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 25 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 26 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 27 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 28 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 29 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 30 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 31 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 32 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 33 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 34 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 35 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 36 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 37 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 38 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 39 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 40 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 41 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 42 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 43 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 44 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 45 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 46 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 47 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 48 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 49 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 50 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 1 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 2 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 3 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 4 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 5 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 6 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 7 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 8 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 9 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 10 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 11 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 12 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 13 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 14 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 15 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 16 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 17 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 18 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 19 | 4.84 |  |  | 6.04 |  |  | 5.2948
6-DaHall 1-PDU-12 | 20 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 21 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 22 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 23 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 24 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 25 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 26 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 27 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 28 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 29 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 30 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 31 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 32 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 33 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 34 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 35 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 36 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 37 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 38 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 39 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 40 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 41 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 42 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 43 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 44 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 45 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 46 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 47 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 48 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 49 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 50 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 1 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 2 | 1.95 |  |  | 2 |  |  | 1.9684
6-DaHall 1-PDU-01 | 3 |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 4 |  | 2.28 |  |  | 8.94 |  |  | 3.5632
6-DaHall 1-PDU-01 | 5 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 6 |  |  | 2.95 |  |  | 3.16 |  |  | 3.0188
6-DaHall 1-PDU-01 | 7 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 8 | 4.83 |  |  | 4.97 |  |  | 4.8658
6-DaHall 1-PDU-01 | 9 |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 10 |  | 5.89 |  |  | 8.89 |  |  | 7.4314
6-DaHall 1-PDU-01 | 11 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 12 |  |  | 6.93 |  |  | 8.31 |  |  | 7.4215
6-DaHall 1-PDU-01 | 13 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 14 | 4.67 |  |  | 6.61 |  |  | 5.4139
6-DaHall 1-PDU-01 | 15 |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 16 |  | 4.73 |  |  | 6.84 |  |  | 5.6209
6-DaHall 1-PDU-01 | 17 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 18 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 19 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 20 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 21 |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 22 |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 23 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 24 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 25 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 26 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 27 |  | 2.24 |  |  | 2.29 |  |  | 2.2737
6-DaHall 1-PDU-01 | 28 |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 29 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 30 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 31 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 32 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 33 |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 34 |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 35 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 36 |  |  | 0.28 |  |  | 2.78 |  |  | 0.95324
6-DaHall 1-PDU-01 | 37 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 38 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 39 |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 40 |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 41 |  |  | 0.64 |  |  | 1.03 |  |  | 0.82312
6-DaHall 1-PDU-01 | 42 |  |  | 3.62 |  |  | 4.52 |  |  | 3.9927
6-DaHall 1-PDU-01 | 43 | 2.78 |  |  | 5.6 |  |  | 3.7276
6-DaHall 1-PDU-01 | 44 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 45 |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 46 |  | 0.55 |  |  | 0.66 |  |  | 0.55708
6-DaHall 1-PDU-01 | 47 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 48 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 49 | 3.14 |  |  | 10.24 |  |  | 8.1177
6-DaHall 1-PDU-01 | 50 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 1 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 2 | 1.47 |  |  | 1.5 |  |  | 1.4818
6-DaHall 1-PDU-02 | 3 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 4 |  | 1.78 |  |  | 7.19 |  |  | 2.5643
6-DaHall 1-PDU-02 | 5 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 6 |  |  | 4.93 |  |  | 5.31 |  |  | 5.0794
6-DaHall 1-PDU-02 | 7 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 8 | 3.32 |  |  | 3.46 |  |  | 3.3518
6-DaHall 1-PDU-02 | 9 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 10 |  | 5.63 |  |  | 8.75 |  |  | 7.1668
6-DaHall 1-PDU-02 | 11 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 12 |  |  | 8.9 |  |  | 10.46 |  |  | 9.4983
6-DaHall 1-PDU-02 | 13 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 14 | 6.23 |  |  | 8.49 |  |  | 7.2019
6-DaHall 1-PDU-02 | 15 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 16 |  | 4.81 |  |  | 5.49 |  |  | 5.1897
6-DaHall 1-PDU-02 | 17 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 18 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 19 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 20 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 21 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 22 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 23 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 24 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 25 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 26 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 27 |  | 1.33 |  |  | 1.37 |  |  | 1.3432
6-DaHall 1-PDU-02 | 28 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 29 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 30 |  |  | 3.16 |  |  | 10.32 |  |  | 8.0599
6-DaHall 1-PDU-02 | 31 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 32 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 33 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 34 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 35 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 36 |  |  | 1.05 |  |  | 3.57 |  |  | 1.393
6-DaHall 1-PDU-02 | 37 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 38 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 39 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 40 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 41 |  |  | 0.48 |  |  | 0.8 |  |  | 0.62934
6-DaHall 1-PDU-02 | 42 |  |  | 3.76 |  |  | 4.55 |  |  | 4.105
6-DaHall 1-PDU-02 | 43 | 3.3 |  |  | 6.12 |  |  | 3.7623
6-DaHall 1-PDU-02 | 44 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 45 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 46 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 47 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 48 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 49 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 50 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 1 | 2.74 |  |  | 7.67 |  |  | 5.0595
6-DaHall 1-PDU-03 | 2 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 3 |  | 2.14 |  |  | 6.74 |  |  | 4.2526
6-DaHall 1-PDU-03 | 4 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 5 |  |  | 0.88 |  |  | 0.94 |  |  | 0.90176
6-DaHall 1-PDU-03 | 6 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 7 | 3.73 |  |  | 4.2 |  |  | 3.8382
6-DaHall 1-PDU-03 | 8 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 9 |  | 2.82 |  |  | 3.56 |  |  | 2.9847
6-DaHall 1-PDU-03 | 10 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 11 |  |  | 1.4 |  |  | 4.27 |  |  | 3.1839
6-DaHall 1-PDU-03 | 12 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 13 | 3.05 |  |  | 6.95 |  |  | 4.4701
6-DaHall 1-PDU-03 | 14 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 15 |  | 3.88 |  |  | 4.31 |  |  | 4.0322
6-DaHall 1-PDU-03 | 16 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 17 |  |  | 2.03 |  |  | 2.12 |  |  | 2.0482
6-DaHall 1-PDU-03 | 18 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 19 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 20 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 21 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 22 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 23 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 24 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 25 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 26 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 27 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 28 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 29 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 30 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 31 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 32 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 33 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 34 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 35 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 36 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 37 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 38 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 39 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 40 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 41 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 42 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 43 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 44 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 45 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 46 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 47 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 48 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 49 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 50 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 1 | 2.25 |  |  | 6.64 |  |  | 4.0983
6-DaHall 1-PDU-04 | 2 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 3 |  | 2.65 |  |  | 7.45 |  |  | 4.8921
6-DaHall 1-PDU-04 | 4 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 5 |  |  | 0.85 |  |  | 1.5 |  |  | 1.1937
6-DaHall 1-PDU-04 | 6 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 7 | 3.97 |  |  | 4.36 |  |  | 4.0589
6-DaHall 1-PDU-04 | 8 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 9 |  | 3.27 |  |  | 4.07 |  |  | 3.4325
6-DaHall 1-PDU-04 | 10 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 11 |  |  | 2.05 |  |  | 4.94 |  |  | 3.8195
6-DaHall 1-PDU-04 | 12 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 13 | 1.37 |  |  | 5.41 |  |  | 2.8435
6-DaHall 1-PDU-04 | 14 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 15 |  | 3.61 |  |  | 3.98 |  |  | 3.7444
6-DaHall 1-PDU-04 | 16 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 17 |  |  | 1.82 |  |  | 1.91 |  |  | 1.8518
6-DaHall 1-PDU-04 | 18 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 19 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 20 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 21 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 22 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 23 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 24 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 25 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 26 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 27 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 28 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 29 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 30 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 31 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 32 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 33 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 34 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 35 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 36 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 37 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 38 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 39 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 40 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 41 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 42 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 43 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 44 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 45 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 46 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 47 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 48 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 49 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 50 | 0 |  |  | 0
6-DaHall 1-PDU-05 | 1 |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 2 |  | 11.01 |  |  | 13.13 |  |  | 11.5171
6-DaHall 1-PDU-05 | 3 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 4 |  |  | 5.03 |  |  | 5.65 |  |  | 5.2189
6-DaHall 1-PDU-05 | 5 | 0 |  |  | 0
6-DaHall 1-PDU-05 | 6 | 0.71 |  |  | 0.72 |  |  | 0.71
6-DaHall 1-PDU-05 | 7 |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 8 |  | 2.42 |  |  | 3.83 |  |  | 2.7817
6-DaHall 1-PDU-05 | 9 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 10 |  |  | 1 |  |  | 1.08 |  |  | 1.007
6-DaHall 1-PDU-05 | 11 | 1.72 |  |  | 2.35 |  |  | 1.81
6-DaHall 1-PDU-05 | 12 | 1.38 |  |  | 1.48 |  |  | 1.4167
6-DaHall 1-PDU-05 | 13 |  | 1.99 |  |  | 2.16 |  |  | 2.0275
6-DaHall 1-PDU-05 | 14 |  | 4.76 |  |  | 5.56 |  |  | 4.9341
6-DaHall 1-PDU-05 | 15 |  |  | 3.55 |  |  | 3.93 |  |  | 3.7039
6-DaHall 1-PDU-05 | 16 |  |  | 3.19 |  |  | 3.71 |  |  | 3.3747
6-DaHall 1-PDU-05 | 17 | 0.87 |  |  | 1.13 |  |  | 0.95682
6-DaHall 1-PDU-05 | 18 | 0 |  |  | 0
6-DaHall 1-PDU-05 | 19 |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 20 |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 21 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 22 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 23 | 0 |  |  | 0
6-DaHall 1-PDU-05 | 24 | 0 |  |  | 0
6-DaHall 1-PDU-05 | 25 |  | 3.28 |  |  | 12.11 |  |  | 3.7772
6-DaHall 1-PDU-05 | 26 |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 27 |  |  | 3.63 |  |  | 5.5 |  |  | 3.8393
6-DaHall 1-PDU-05 | 28 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 29 | 0 |  |  | 0
6-DaHall 1-PDU-05 | 30 | 0 |  |  | 0
6-DaHall 1-PDU-05 | 31 |  | 1.52 |  |  | 1.63 |  |  | 1.5458
6-DaHall 1-PDU-05 | 32 |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 33 |  |  | 1.11 |  |  | 1.13 |  |  | 1.1197
6-DaHall 1-PDU-05 | 34 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 35 | 0.67 |  |  | 0.68 |  |  | 0.68
6-DaHall 1-PDU-05 | 36 | 0 |  |  | 0
6-DaHall 1-PDU-05 | 37 |  | 0 |  |  | 8.43 |  |  | 3.4826
6-DaHall 1-PDU-05 | 38 |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 39 |  |  | 2.09 |  |  | 2.2 |  |  | 2.0972
6-DaHall 1-PDU-05 | 40 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 41 | 1.26 |  |  | 2.15 |  |  | 1.4414
6-DaHall 1-PDU-05 | 42 | 0 |  |  | 0
6-DaHall 1-PDU-05 | 43 |  | 5.67 |  |  | 6.33 |  |  | 5.7522
6-DaHall 1-PDU-05 | 44 |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 45 |  |  | 4.74 |  |  | 5.42 |  |  | 5.0127
6-DaHall 1-PDU-05 | 46 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 47 | 2.54 |  |  | 5.11 |  |  | 3.5945
6-DaHall 1-PDU-05 | 48 | 0 |  |  | 0
6-DaHall 1-PDU-05 | 49 |  | 7.55 |  |  | 9.14 |  |  | 8.1769
6-DaHall 1-PDU-05 | 50 |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 51 |  |  | 2.05 |  |  | 5.08 |  |  | 3.594
6-DaHall 1-PDU-05 | 52 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 53 | 2.04 |  |  | 6.63 |  |  | 4.3507
6-DaHall 1-PDU-05 | 54 | 4.17 |  |  | 4.5 |  |  | 4.2693
6-DaHall 1-PDU-06 | 1 |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 2 |  | 9.9 |  |  | 11.95 |  |  | 10.4239
6-DaHall 1-PDU-06 | 3 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 4 |  |  | 3.88 |  |  | 4.54 |  |  | 4.0793
6-DaHall 1-PDU-06 | 5 | 0 |  |  | 0
6-DaHall 1-PDU-06 | 6 | 0.69 |  |  | 0.72 |  |  | 0.69123
6-DaHall 1-PDU-06 | 7 |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 8 |  | 3.16 |  |  | 4.53 |  |  | 3.4827
6-DaHall 1-PDU-06 | 9 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 10 |  |  | 0.54 |  |  | 0.55 |  |  | 0.54039
6-DaHall 1-PDU-06 | 11 | 1.89 |  |  | 1.93 |  |  | 1.9057
6-DaHall 1-PDU-06 | 12 | 0 |  |  | 0
6-DaHall 1-PDU-06 | 13 |  | 3.42 |  |  | 3.86 |  |  | 3.5289
6-DaHall 1-PDU-06 | 14 |  | 3.15 |  |  | 3.53 |  |  | 3.2451
6-DaHall 1-PDU-06 | 15 |  |  | 3.1 |  |  | 3.4 |  |  | 3.177
6-DaHall 1-PDU-06 | 16 |  |  | 3.81 |  |  | 4.58 |  |  | 4.0675
6-DaHall 1-PDU-06 | 17 | 0.82 |  |  | 1.03 |  |  | 0.91132
6-DaHall 1-PDU-06 | 18 | 0 |  |  | 0
6-DaHall 1-PDU-06 | 19 |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 20 |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 21 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 22 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 23 | 0 |  |  | 0
6-DaHall 1-PDU-06 | 24 | 0 |  |  | 0
6-DaHall 1-PDU-06 | 25 |  | 3.53 |  |  | 7.95 |  |  | 4.4484
6-DaHall 1-PDU-06 | 26 |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 27 |  |  | 2.91 |  |  | 7.03 |  |  | 3.1651
6-DaHall 1-PDU-06 | 28 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 29 | 0 |  |  | 0
6-DaHall 1-PDU-06 | 30 | 0 |  |  | 0
6-DaHall 1-PDU-06 | 31 |  | 0.38 |  |  | 0.39 |  |  | 0.38038
6-DaHall 1-PDU-06 | 32 |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 33 |  |  | 1.18 |  |  | 1.2 |  |  | 1.18
6-DaHall 1-PDU-06 | 34 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 35 | 0.39 |  |  | 0.39 |  |  | 0.39
6-DaHall 1-PDU-06 | 36 | 0 |  |  | 0
6-DaHall 1-PDU-06 | 37 |  | 0.98 |  |  | 10.92 |  |  | 3.5799
6-DaHall 1-PDU-06 | 38 |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 39 |  |  | 1.9 |  |  | 2.12 |  |  | 1.9107
6-DaHall 1-PDU-06 | 40 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 41 | 0.33 |  |  | 1.23 |  |  | 0.81301
6-DaHall 1-PDU-06 | 42 | 0 |  |  | 0
6-DaHall 1-PDU-06 | 43 |  | 4.8 |  |  | 5.49 |  |  | 4.891
6-DaHall 1-PDU-06 | 44 |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 45 |  |  | 4.84 |  |  | 5.45 |  |  | 5.1112
6-DaHall 1-PDU-06 | 46 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 47 | 2.32 |  |  | 4.91 |  |  | 3.2764
6-DaHall 1-PDU-06 | 48 | 0 |  |  | 0
6-DaHall 1-PDU-06 | 49 |  | 1.29 |  |  | 1.51 |  |  | 1.341
6-DaHall 1-PDU-06 | 50 |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 51 |  |  | 2.62 |  |  | 5.68 |  |  | 4.159
6-DaHall 1-PDU-06 | 52 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 53 | 0.56 |  |  | 0.9 |  |  | 0.59047
6-DaHall 1-PDU-06 | 54 | 2.34 |  |  | 2.71 |  |  | 2.4015
6-DaHall 1-PDU-07 | 1 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 2 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 3 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 4 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 5 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 6 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 7 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 8 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 9 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 10 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 11 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 12 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 13 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 14 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 15 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 16 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 17 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 18 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 19 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 20 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 21 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 22 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 23 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 24 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 25 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 26 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 27 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 28 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 29 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 30 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 31 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 32 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 33 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 34 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 35 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 36 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 37 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 38 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 39 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 40 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 41 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 42 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 43 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 44 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 45 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 46 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 47 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 48 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 49 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 50 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 51 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 52 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 53 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 54 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 1 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 2 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 3 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 4 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 5 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 6 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 7 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 8 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 9 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 10 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 11 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 12 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 13 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 14 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 15 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 16 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 17 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 18 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 19 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 20 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 21 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 22 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 23 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 24 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 25 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 26 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 27 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 28 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 29 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 30 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 31 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 32 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 33 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 34 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 35 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 36 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 37 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 38 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 39 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 40 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 41 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 42 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 43 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 44 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 45 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 46 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 47 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 48 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 49 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 50 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 51 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 52 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 53 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 54 | 0 |  |  | 0

## 5층_부하량
장비명 | 분기번호 | MIN |  |  | MAX |  |  | AVG
|  | R | S | T | R | S | T | R | S | T
5-DaHall 1-CEP-05 | 1 | 0 | 0 | 0 | 11.7 | 11.38 | 12.76 | 0.07166 | 0.06934 | 0.078111
5-DaHall 1-CEP-05 | 2 | 0 | 0 | 0 | 11.31 | 12.15 | 11.74 | 0.062509 | 0.066942 | 0.064941
5-DaHall 1-CEP-05 | 3 | 0 | 0 | 0 | 21.34 | 21.44 | 21.11 | 0.067326 | 0.067576 | 0.067472
5-DaHall 1-CEP-05 | 4 | 0 | 0 | 0 | 23.39 | 23.54 | 23.26 | 18.4935 | 18.7089 | 18.3071
5-DaHall 1-CEP-05 | 5 | 0 | 0 | 0 | 22.15 | 22.3 | 22.01 | 0.055622 | 0.055907 | 0.05581
5-DaHall 1-CEP-05 | 6 | 0 | 0 | 0 | 23.91 | 23.6 | 24.02 | 18.8825 | 18.5658 | 18.8317
5-DaHall 1-CEP-05 | 7 | 0 | 0 | 0 | 24.27 | 24.43 | 23.99 | 18.3005 | 18.3892 | 17.9394
5-DaHall 1-CEP-05 | 8 | 0 | 0 | 0 | 24.15 | 24.64 | 24.11 | 12.941 | 13.148 | 12.9276
5-DaHall 1-CEP-05 | 9 | 0 | 0 | 0 | 21.51 | 21.7 | 21.25 | 1.2625 | 1.278 | 1.2543
5-DaHall 1-CEP-05 | 10 | 0 | 0 | 0 | 20.25 | 20.59 | 20.22 | 0.061327 | 0.062265 | 0.061974
5-DaHall 1-CEP-05 | 11 | 0 | 0 | 0 | 25 | 25.64 | 24.92 | 0.061369 | 0.06271 | 0.06196
5-DaHall 1-CEP-05 | 12 | 0 | 0 | 0 | 23.79 | 21.74 | 23.56 | 0.057938 | 0.052778 | 0.057076
5-DaHall 1-CEP-05 | 13 | 0 |  |  | 0
5-DaHall 1-CEP-05 | 14 | 0 |  |  | 0
5-DaHall 1-CEP-05 | 15 |  | 0 |  |  | 0
5-DaHall 1-CEP-05 | 16 |  | 0 |  |  | 18.29 |  |  | 12.8881
5-DaHall 1-CEP-05 | 17 |  |  | 0 |  |  | 0
5-DaHall 1-CEP-05 | 18 |  |  | 5.85 |  |  | 16.37 |  |  | 8.3019
5-DaHall 1-CEP-06 | 1 | 0.24 | 0 | 0.24 | 20.41 | 19.9 | 19.59 | 0.24568 | 0.12391 | 0.2488
5-DaHall 1-CEP-06 | 2 | 0.24 | 0 | 0.24 | 20.72 | 20.36 | 20.2 | 0.24447 | 0.071929 | 0.24801
5-DaHall 1-CEP-06 | 3 | 0.24 | 0 | 0.23 | 19.99 | 19.59 | 19.6 | 0.24546 | 0.061563 | 0.23486
5-DaHall 1-CEP-06 | 4 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-01 | 1 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-01 | 2 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 3 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 4 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 5 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 6 |  | 9.36 |  |  | 14.02 |  |  | 12.4089
5-DaHall 1-PDU-01 | 7 |  |  | 7.99 |  |  | 12.56 |  |  | 11.186
5-DaHall 1-PDU-01 | 8 | 9.85 |  |  | 15.26 |  |  | 13.2166
5-DaHall 1-PDU-01 | 9 |  | 0 |  |  | 6.65 |  |  | 3.1842
5-DaHall 1-PDU-01 | 10 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 11 | 1.03 |  |  | 1.05 |  |  | 1.0387
5-DaHall 1-PDU-01 | 12 |  | 1.38 |  |  | 1.54 |  |  | 1.4715
5-DaHall 1-PDU-01 | 13 |  |  | 1.48 |  |  | 1.58 |  |  | 1.5393
5-DaHall 1-PDU-01 | 14 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 15 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 16 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 17 | 8.93 |  |  | 11.9 |  |  | 11.1759
5-DaHall 1-PDU-01 | 18 |  | 7.39 |  |  | 10.86 |  |  | 9.8387
5-DaHall 1-PDU-01 | 19 |  |  | 8.93 |  |  | 12.82 |  |  | 11.6822
5-DaHall 1-PDU-01 | 20 | 6.8 |  |  | 10.49 |  |  | 9.5743
5-DaHall 1-PDU-01 | 21 |  | 8.81 |  |  | 13.25 |  |  | 11.7622
5-DaHall 1-PDU-01 | 22 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 23 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 24 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 25 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 26 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 55 | 0 | 0.57 | 0.72 | 0 | 0.59 | 0.74 |  | 0.58627 | 0.72983
5-DaHall 1-PDU-01 | 56 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 57 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 58 |  |  | 1.52 |  |  | 2.15 |  |  | 1.5779
5-DaHall 1-PDU-01 | 59 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 60 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 61 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 62 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 63 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 64 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 65 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 66 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 67 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 68 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 69 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 70 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 71 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 72 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 73 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 74 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 75 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 76 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 77 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 78 |  | 0.61 |  |  | 0.65 |  |  | 0.62005
5-DaHall 1-PDU-01 | 79 |  |  | 1.1 |  |  | 1.75 |  |  | 1.7327
5-DaHall 1-PDU-01 | 80 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 1 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-02 | 2 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 3 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 4 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 5 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 6 |  | 7.84 |  |  | 11.73 |  |  | 10.4156
5-DaHall 1-PDU-02 | 7 |  |  | 9.25 |  |  | 14.33 |  |  | 12.7078
5-DaHall 1-PDU-02 | 8 | 7.97 |  |  | 12.61 |  |  | 10.9951
5-DaHall 1-PDU-02 | 9 |  | 0 |  |  | 6.29 |  |  | 3.0387
5-DaHall 1-PDU-02 | 10 |  |  | 0 |  |  | 6.72 |  |  | 3.0577
5-DaHall 1-PDU-02 | 11 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 12 |  | 1.53 |  |  | 1.71 |  |  | 1.6336
5-DaHall 1-PDU-02 | 13 |  |  | 1.26 |  |  | 1.34 |  |  | 1.3191
5-DaHall 1-PDU-02 | 14 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 15 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 16 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 17 | 9.59 |  |  | 13.16 |  |  | 11.5619
5-DaHall 1-PDU-02 | 18 |  | 8.63 |  |  | 12.74 |  |  | 11.5925
5-DaHall 1-PDU-02 | 19 |  |  | 7.25 |  |  | 10.69 |  |  | 9.714
5-DaHall 1-PDU-02 | 20 | 7.7 |  |  | 12.61 |  |  | 11.4477
5-DaHall 1-PDU-02 | 21 |  | 6.93 |  |  | 10.61 |  |  | 9.4716
5-DaHall 1-PDU-02 | 22 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 23 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 24 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 25 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 26 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 55 | 0 | 0.65 | 0.72 | 0 | 0.66 | 0.74 |  | 0.65712 | 0.73016
5-DaHall 1-PDU-02 | 56 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 57 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 58 |  |  | 1.25 |  |  | 1.92 |  |  | 1.308
5-DaHall 1-PDU-02 | 59 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 60 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 61 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 62 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 63 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 64 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 65 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 66 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 67 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 68 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 69 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 70 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 71 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 72 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 73 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 74 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 75 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 76 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 77 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 78 |  | 0.61 |  |  | 0.65 |  |  | 0.63018
5-DaHall 1-PDU-02 | 79 |  |  | 0.53 |  |  | 1.15 |  |  | 1.1048
5-DaHall 1-PDU-02 | 80 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 1 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-03 | 2 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 3 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 4 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 5 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 6 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 7 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 8 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 9 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 10 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 11 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 12 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 13 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 14 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 15 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 16 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 17 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 18 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 19 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 20 | 2.59 |  |  | 4.35 |  |  | 3.2319
5-DaHall 1-PDU-03 | 21 |  | 1.66 |  |  | 2.21 |  |  | 1.7992
5-DaHall 1-PDU-03 | 22 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 23 | 2.18 |  |  | 3.31 |  |  | 2.432
5-DaHall 1-PDU-03 | 24 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 25 |  |  | 3.95 |  |  | 4.61 |  |  | 4.0531
5-DaHall 1-PDU-03 | 26 | 5.59 |  |  | 6.52 |  |  | 5.7896
5-DaHall 1-PDU-03 | 55 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-03 | 56 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 57 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 58 |  |  | 0.53 |  |  | 0.68 |  |  | 0.56762
5-DaHall 1-PDU-03 | 59 | 1.27 |  |  | 1.75 |  |  | 1.4476
5-DaHall 1-PDU-03 | 60 |  | 2.05 |  |  | 4.52 |  |  | 3.56
5-DaHall 1-PDU-03 | 61 |  |  | 1.73 |  |  | 2.02 |  |  | 1.7723
5-DaHall 1-PDU-03 | 62 | 0.34 |  |  | 0.39 |  |  | 0.35264
5-DaHall 1-PDU-03 | 63 |  | 3.74 |  |  | 4.45 |  |  | 3.9112
5-DaHall 1-PDU-03 | 64 |  |  | 0.84 |  |  | 0.86 |  |  | 0.84995
5-DaHall 1-PDU-03 | 65 | 2.73 |  |  | 2.96 |  |  | 2.8169
5-DaHall 1-PDU-03 | 66 |  | 2.75 |  |  | 3.16 |  |  | 2.8763
5-DaHall 1-PDU-03 | 67 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 68 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 69 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 70 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 71 | 2.46 |  |  | 2.56 |  |  | 2.4823
5-DaHall 1-PDU-03 | 72 |  | 2.14 |  |  | 2.53 |  |  | 2.2286
5-DaHall 1-PDU-03 | 73 |  |  | 2.15 |  |  | 2.2 |  |  | 2.1677
5-DaHall 1-PDU-03 | 74 | 2.32 |  |  | 2.38 |  |  | 2.3507
5-DaHall 1-PDU-03 | 75 |  | 1.35 |  |  | 1.39 |  |  | 1.366
5-DaHall 1-PDU-03 | 76 |  |  | 1.77 |  |  | 1.86 |  |  | 1.7853
5-DaHall 1-PDU-03 | 77 | 2.83 |  |  | 3.21 |  |  | 2.9196
5-DaHall 1-PDU-03 | 78 |  | 2.82 |  |  | 3.18 |  |  | 2.893
5-DaHall 1-PDU-03 | 79 |  |  | 3.39 |  |  | 4 |  |  | 3.6755
5-DaHall 1-PDU-03 | 80 | 3.81 |  |  | 4.67 |  |  | 4.1026
5-DaHall 1-PDU-04 | 1 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-04 | 2 | 0 |  |  | 0
5-DaHall 1-PDU-04 | 3 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 4 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 5 | 0 |  |  | 0
5-DaHall 1-PDU-04 | 6 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 7 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 8 | 0 |  |  | 0
5-DaHall 1-PDU-04 | 9 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 10 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 11 | 0 |  |  | 0
5-DaHall 1-PDU-04 | 12 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 13 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 14 | 0 |  |  | 0
5-DaHall 1-PDU-04 | 15 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 16 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 17 | 0 |  |  | 0
5-DaHall 1-PDU-04 | 18 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 19 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 20 | 3.21 |  |  | 5 |  |  | 3.9333
5-DaHall 1-PDU-04 | 21 |  | 1.1 |  |  | 1.59 |  |  | 1.2236
5-DaHall 1-PDU-04 | 22 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 23 | 2.27 |  |  | 3.36 |  |  | 2.4836
5-DaHall 1-PDU-04 | 24 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 25 |  |  | 4.29 |  |  | 4.97 |  |  | 4.4097
5-DaHall 1-PDU-04 | 26 | 5.3 |  |  | 6.32 |  |  | 5.5645
5-DaHall 1-PDU-04 | 55 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-04 | 56 | 0 |  |  | 0
5-DaHall 1-PDU-04 | 57 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 58 |  |  | 0.53 |  |  | 0.69 |  |  | 0.56844
5-DaHall 1-PDU-04 | 59 | 1.57 |  |  | 2.05 |  |  | 1.7486
5-DaHall 1-PDU-04 | 60 |  | 1.94 |  |  | 4.45 |  |  | 3.5361
5-DaHall 1-PDU-04 | 61 |  |  | 1.78 |  |  | 2.06 |  |  | 1.8126
5-DaHall 1-PDU-04 | 62 | 0.4 |  |  | 1.02 |  |  | 0.65122
5-DaHall 1-PDU-04 | 63 |  | 3.67 |  |  | 4.35 |  |  | 3.8372
5-DaHall 1-PDU-04 | 64 |  |  | 0.85 |  |  | 0.92 |  |  | 0.85023
5-DaHall 1-PDU-04 | 65 | 1.78 |  |  | 1.89 |  |  | 1.8217
5-DaHall 1-PDU-04 | 66 |  | 2.99 |  |  | 3.31 |  |  | 3.0523
5-DaHall 1-PDU-04 | 67 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 68 | 0 |  |  | 0
5-DaHall 1-PDU-04 | 69 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 70 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 71 | 0.26 |  |  | 0.75 |  |  | 0.27073
5-DaHall 1-PDU-04 | 72 |  | 0.28 |  |  | 0.29 |  |  | 0.28991
5-DaHall 1-PDU-04 | 73 |  |  | 2.27 |  |  | 2.31 |  |  | 2.2841
5-DaHall 1-PDU-04 | 74 | 2.46 |  |  | 2.96 |  |  | 2.759
5-DaHall 1-PDU-04 | 75 |  | 1.43 |  |  | 2.33 |  |  | 1.4517
5-DaHall 1-PDU-04 | 76 |  |  | 1.57 |  |  | 1.6 |  |  | 1.582
5-DaHall 1-PDU-04 | 77 | 2.25 |  |  | 2.5 |  |  | 2.3193
5-DaHall 1-PDU-04 | 78 |  | 2.29 |  |  | 2.5 |  |  | 2.3497
5-DaHall 1-PDU-04 | 79 |  |  | 2.94 |  |  | 3.77 |  |  | 3.1896
5-DaHall 1-PDU-04 | 80 | 3.62 |  |  | 4.46 |  |  | 3.9358
5-DaHall 1-PDU-05 | 1 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 2 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 3 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 4 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 5 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 6 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 7 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 8 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 9 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 10 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 11 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 12 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 13 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 14 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 15 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 16 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 17 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 18 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 19 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 20 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 21 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 22 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 23 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 24 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 25 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 26 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 27 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 28 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 29 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 30 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 31 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 32 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 33 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 34 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 35 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 36 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 37 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 38 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 39 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 40 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 41 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 42 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 43 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 44 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 45 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 46 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 47 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 48 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 49 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 50 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 51 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 52 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 53 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 54 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 1 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 2 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 3 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 4 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 5 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 6 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 7 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 8 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 9 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 10 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 11 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 12 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 13 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 14 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 15 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 16 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 17 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 18 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 19 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 20 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 21 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 22 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 23 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 24 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 25 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 26 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 27 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 28 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 29 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 30 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 31 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 32 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 33 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 34 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 35 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 36 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 37 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 38 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 39 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 40 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 41 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 42 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 43 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 44 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 45 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 46 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 47 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 48 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 49 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 50 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 51 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 52 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 53 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 54 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 1 | 7.64 |  |  | 8 |  |  | 7.8089
5-DaHall 1-PDU-07 | 2 | 0.99 |  |  | 1.07 |  |  | 1.0019
5-DaHall 1-PDU-07 | 3 |  | 1.19 |  |  | 1.45 |  |  | 1.2814
5-DaHall 1-PDU-07 | 4 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 5 |  |  | 0.4 |  |  | 0.4 |  |  | 0.4
5-DaHall 1-PDU-07 | 6 |  |  | 0.34 |  |  | 0.39 |  |  | 0.37117
5-DaHall 1-PDU-07 | 7 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 8 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 9 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 10 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 11 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 12 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 13 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 14 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 15 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 16 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 17 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 18 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 19 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 20 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 21 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 22 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 23 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 24 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 25 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 26 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 27 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 28 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 29 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 30 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 31 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 32 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 33 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 34 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 35 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 36 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-09 | 1
5-DaHall 1-PDU-09 | 2
5-DaHall 1-PDU-09 | 3
5-DaHall 1-PDU-09 | 4
5-DaHall 1-PDU-09 | 5
5-DaHall 1-PDU-09 | 6
5-DaHall 1-PDU-09 | 7
5-DaHall 1-PDU-09 | 8
5-DaHall 1-PDU-09 | 9
5-DaHall 1-PDU-09 | 10
5-DaHall 1-PDU-09 | 11
5-DaHall 1-PDU-09 | 12
5-DaHall 1-PDU-09 | 13
5-DaHall 1-PDU-09 | 14
5-DaHall 1-PDU-09 | 15
5-DaHall 1-PDU-09 | 16
5-DaHall 1-PDU-09 | 17
5-DaHall 1-PDU-09 | 18
5-DaHall 1-PDU-09 | 19
5-DaHall 1-PDU-09 | 20
5-DaHall 1-PDU-09 | 21
5-DaHall 1-PDU-09 | 22
5-DaHall 1-PDU-09 | 23
5-DaHall 1-PDU-09 | 24
5-DaHall 1-PDU-09 | 25
5-DaHall 1-PDU-09 | 26
5-DaHall 1-PDU-09 | 27
5-DaHall 1-PDU-09 | 28
5-DaHall 1-PDU-09 | 29
5-DaHall 1-PDU-09 | 30
5-DaHall 1-PDU-09 | 31
5-DaHall 1-PDU-09 | 32
5-DaHall 1-PDU-09 | 33
5-DaHall 1-PDU-09 | 34
5-DaHall 1-PDU-09 | 35
5-DaHall 1-PDU-09 | 36
5-DaHall 1-PDU-09 | 37
5-DaHall 1-PDU-09 | 38
5-DaHall 1-PDU-08 | 1 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 2 | 1.13 |  |  | 1.25 |  |  | 1.1675
5-DaHall 1-PDU-08 | 3 |  | 1.26 |  |  | 1.49 |  |  | 1.4019
5-DaHall 1-PDU-08 | 4 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 5 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 6 |  |  | 1.33 |  |  | 1.38 |  |  | 1.35
5-DaHall 1-PDU-08 | 7 | 5.28 |  |  | 5.43 |  |  | 5.3639
5-DaHall 1-PDU-08 | 8 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 9 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 10 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 11 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 12 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 13 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 14 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 15 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 16 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 17 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 18 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 19 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 20 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 21 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 22 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 23 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 24 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 25 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 26 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 27 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 28 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 29 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 30 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 31 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 32 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 33 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 34 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 35 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 36 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-10 | 1
5-DaHall 1-PDU-10 | 2
5-DaHall 1-PDU-10 | 3
5-DaHall 1-PDU-10 | 4
5-DaHall 1-PDU-10 | 5
5-DaHall 1-PDU-10 | 6
5-DaHall 1-PDU-10 | 7
5-DaHall 1-PDU-10 | 8
5-DaHall 1-PDU-10 | 9
5-DaHall 1-PDU-10 | 10
5-DaHall 1-PDU-10 | 11
5-DaHall 1-PDU-10 | 12
5-DaHall 1-PDU-10 | 13
5-DaHall 1-PDU-10 | 14
5-DaHall 1-PDU-10 | 15
5-DaHall 1-PDU-10 | 16
5-DaHall 1-PDU-10 | 17
5-DaHall 1-PDU-10 | 18
5-DaHall 1-PDU-10 | 19
5-DaHall 1-PDU-10 | 20
5-DaHall 1-PDU-10 | 21
5-DaHall 1-PDU-10 | 22
5-DaHall 1-PDU-10 | 23
5-DaHall 1-PDU-10 | 24
5-DaHall 1-PDU-10 | 25
5-DaHall 1-PDU-10 | 26
5-DaHall 1-PDU-10 | 27
5-DaHall 1-PDU-10 | 28
5-DaHall 1-PDU-10 | 29
5-DaHall 1-PDU-10 | 30
5-DaHall 1-PDU-10 | 31
5-DaHall 1-PDU-10 | 32
5-DaHall 1-PDU-10 | 33
5-DaHall 1-PDU-10 | 34
5-DaHall 1-PDU-10 | 35
5-DaHall 1-PDU-10 | 36
5-DaHall 1-PDU-10 | 37
5-DaHall 1-PDU-10 | 38
5-DaHall 1-PDU-11 | 1 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-11 | 2 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-11 | 3 | 0 |  |  | 0
5-DaHall 1-PDU-11 | 4 | 0 |  |  | 0
5-DaHall 1-PDU-11 | 5 |  | 0 |  |  | 0
5-DaHall 1-PDU-11 | 6 |  | 1.97 |  |  | 2.1 |  |  | 2.0275
5-DaHall 1-PDU-11 | 7 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-11 | 8 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-11 | 9 | 5.19 |  |  | 5.3 |  |  | 5.2395
5-DaHall 1-PDU-11 | 10 | 0 |  |  | 0
5-DaHall 1-PDU-11 | 11 |  | 0 |  |  | 0
5-DaHall 1-PDU-11 | 12 |  | 0 |  |  | 0
5-DaHall 1-PDU-11 | 13 |  |  | 1.94 |  |  | 2 |  |  | 1.9565
5-DaHall 1-PDU-11 | 14 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-11 | 15 | 0 |  |  | 0
5-DaHall 1-PDU-11 | 16 | 0 |  |  | 0
5-DaHall 1-PDU-11 | 17 |  | 0 |  |  | 0
5-DaHall 1-PDU-11 | 18 |  | 2.39 |  |  | 3.56 |  |  | 3.0799
5-DaHall 1-PDU-11 | 19 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-11 | 20 |  |  | 2.88 |  |  | 3.09 |  |  | 2.9135
5-DaHall 1-PDU-11 | 21 | 2.48 |  |  | 2.7 |  |  | 2.554
5-DaHall 1-PDU-11 | 22 | 0 |  |  | 0
5-DaHall 1-PDU-11 | 23 |  | 4.82 |  |  | 5.62 |  |  | 4.9109
5-DaHall 1-PDU-11 | 24 |  | 0 |  |  | 0
5-DaHall 1-PDU-11 | 25 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-11 | 26 |  |  | 5.41 |  |  | 5.54 |  |  | 5.4676
5-DaHall 1-PDU-11 | 27 | 2.55 |  |  | 2.81 |  |  | 2.6574
5-DaHall 1-PDU-11 | 28 | 5.27 |  |  | 5.63 |  |  | 5.4329
5-DaHall 1-PDU-11 | 29 |  | 0 |  |  | 0
5-DaHall 1-PDU-11 | 30 |  | 0 |  |  | 0
5-DaHall 1-PDU-11 | 31 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-11 | 32 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 1 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-13 | 2 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-13 | 3 | 5.29 |  |  | 6.41 |  |  | 5.6571
5-DaHall 1-PDU-13 | 4 | 0 |  |  | 0
5-DaHall 1-PDU-13 | 5 |  | 3.9 |  |  | 6.05 |  |  | 3.9416
5-DaHall 1-PDU-13 | 6 |  | 5.81 |  |  | 6.3 |  |  | 5.8641
5-DaHall 1-PDU-13 | 7 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 8 |  |  | 4.05 |  |  | 4.75 |  |  | 4.2161
5-DaHall 1-PDU-13 | 9 | 0 |  |  | 0
5-DaHall 1-PDU-13 | 10 | 0 |  |  | 0
5-DaHall 1-PDU-13 | 11 |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 12 |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 13 |  |  | 0.7 |  |  | 0.73 |  |  | 0.70734
5-DaHall 1-PDU-13 | 14 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 15 | 0 |  |  | 0
5-DaHall 1-PDU-13 | 16 | 3.83 |  |  | 3.94 |  |  | 3.8811
5-DaHall 1-PDU-13 | 17 |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 18 |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 19 |  |  | 5.1 |  |  | 5.51 |  |  | 5.2271
5-DaHall 1-PDU-13 | 20 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 21 | 3.16 |  |  | 3.69 |  |  | 3.2932
5-DaHall 1-PDU-13 | 22 | 0 |  |  | 0
5-DaHall 1-PDU-13 | 23 |  | 8.64 |  |  | 10.05 |  |  | 9.0422
5-DaHall 1-PDU-13 | 24 |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 25 |  |  | 2.46 |  |  | 2.59 |  |  | 2.4993
5-DaHall 1-PDU-13 | 26 |  |  | 1.79 |  |  | 2.03 |  |  | 1.8758
5-DaHall 1-PDU-13 | 27 | 0 |  |  | 0
5-DaHall 1-PDU-13 | 28 | 0 |  |  | 0
5-DaHall 1-PDU-13 | 29 |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 30 |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 31 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 32 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-15 | 1 | 5.97 | 1.24 | 7.84 | 6.07 | 1.28 | 8.16 | 6.0238 | 1.2489 | 7.9433
5-DaHall 1-PDU-15 | 2 | 3.36 | 2.77 | 1.94 | 3.43 | 2.84 | 2.16 | 3.391 | 2.7951 | 1.9974
5-DaHall 1-PDU-15 | 3 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-15 | 4 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-15 | 5 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-15 | 6 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-15 | 7 | 3.76 |  |  | 3.88 |  |  | 3.7956
5-DaHall 1-PDU-15 | 8 | 4.29 |  |  | 4.34 |  |  | 4.3115
5-DaHall 1-PDU-15 | 9 |  | 1.74 |  |  | 1.77 |  |  | 1.7567
5-DaHall 1-PDU-15 | 10 |  | 6.7 |  |  | 6.92 |  |  | 6.7601
5-DaHall 1-PDU-15 | 11 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-15 | 12 |  |  | 2.3 |  |  | 2.33 |  |  | 2.312
5-DaHall 1-PDU-15 | 13 | 0.59 |  |  | 0.64 |  |  | 0.61654
5-DaHall 1-PDU-15 | 14 | 1.56 |  |  | 1.59 |  |  | 1.5793
5-DaHall 1-PDU-15 | 15 |  | 0 |  |  | 0
5-DaHall 1-PDU-15 | 16 |  | 0 |  |  | 0
5-DaHall 1-PDU-15 | 17 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-15 | 18 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-15 | 19 | 0 |  |  | 0
5-DaHall 1-PDU-15 | 20 | 0 |  |  | 0
5-DaHall 1-PDU-15 | 21 |  | 0 |  |  | 0
5-DaHall 1-PDU-15 | 22 |  | 0 |  |  | 0
5-DaHall 1-PDU-15 | 23 |  |  | 2.3 |  |  | 2.33 |  |  | 2.3094
5-DaHall 1-PDU-15 | 24 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-15 | 25 | 0 |  |  | 0
5-DaHall 1-PDU-15 | 26 | 0 |  |  | 0
5-DaHall 1-PDU-15 | 27 |  | 0 |  |  | 0
5-DaHall 1-PDU-15 | 28 |  | 0.71 |  |  | 0.72 |  |  | 0.71001
5-DaHall 1-PDU-15 | 29 |  |  | 0.36 |  |  | 0.37 |  |  | 0.36265
5-DaHall 1-PDU-15 | 30 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 1 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-12 | 2 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-12 | 3 | 0 |  |  | 0
5-DaHall 1-PDU-12 | 4 | 1.89 |  |  | 1.96 |  |  | 1.9205
5-DaHall 1-PDU-12 | 5 |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 6 |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 7 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 8 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 9 | 2.92 |  |  | 2.97 |  |  | 2.9366
5-DaHall 1-PDU-12 | 10 | 0 |  |  | 0
5-DaHall 1-PDU-12 | 11 |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 12 |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 13 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 14 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 15 | 0 |  |  | 0
5-DaHall 1-PDU-12 | 16 | 5.41 |  |  | 6.75 |  |  | 6.1695
5-DaHall 1-PDU-12 | 17 |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 18 |  | 3.59 |  |  | 3.68 |  |  | 3.6126
5-DaHall 1-PDU-12 | 19 |  |  | 2.92 |  |  | 3.16 |  |  | 2.9717
5-DaHall 1-PDU-12 | 20 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 21 | 4.44 |  |  | 5.37 |  |  | 4.5562
5-DaHall 1-PDU-12 | 22 | 0 |  |  | 0
5-DaHall 1-PDU-12 | 23 |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 24 |  | 3.46 |  |  | 3.56 |  |  | 3.5013
5-DaHall 1-PDU-12 | 25 |  |  | 3.3 |  |  | 3.76 |  |  | 3.4098
5-DaHall 1-PDU-12 | 26 |  |  | 4.96 |  |  | 5.04 |  |  | 5.0065
5-DaHall 1-PDU-12 | 27 | 0 |  |  | 0
5-DaHall 1-PDU-12 | 28 | 5.66 |  |  | 5.99 |  |  | 5.806
5-DaHall 1-PDU-12 | 29 |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 30 |  | 6.46 |  |  | 6.56 |  |  | 6.5079
5-DaHall 1-PDU-12 | 31 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 32 |  |  | 2.88 |  |  | 3.31 |  |  | 3.0076
5-DaHall 1-PDU-14 | 1 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-14 | 2 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-14 | 3 | 1.39 |  |  | 3.3 |  |  | 3.2547
5-DaHall 1-PDU-14 | 4 | 6.69 |  |  | 7.81 |  |  | 7.0524
5-DaHall 1-PDU-14 | 5 |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 6 |  | 2.75 |  |  | 3.09 |  |  | 2.8166
5-DaHall 1-PDU-14 | 7 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 8 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 9 | 0 |  |  | 0
5-DaHall 1-PDU-14 | 10 | 0 |  |  | 0
5-DaHall 1-PDU-14 | 11 |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 12 |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 13 |  |  | 1.72 |  |  | 1.82 |  |  | 1.7295
5-DaHall 1-PDU-14 | 14 |  |  | 3.17 |  |  | 3.25 |  |  | 3.2013
5-DaHall 1-PDU-14 | 15 | 0 |  |  | 0
5-DaHall 1-PDU-14 | 16 | 0 |  |  | 0
5-DaHall 1-PDU-14 | 17 |  | 0.94 |  |  | 1.06 |  |  | 0.96051
5-DaHall 1-PDU-14 | 18 |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 19 |  |  | 2.18 |  |  | 2.66 |  |  | 2.5462
5-DaHall 1-PDU-14 | 20 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 21 | 3.34 |  |  | 3.72 |  |  | 3.403
5-DaHall 1-PDU-14 | 22 | 0 |  |  | 0
5-DaHall 1-PDU-14 | 23 |  | 2.51 |  |  | 2.64 |  |  | 2.5495
5-DaHall 1-PDU-14 | 24 |  | 4.1 |  |  | 5.72 |  |  | 5.0704
5-DaHall 1-PDU-14 | 25 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 26 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 27 | 0 |  |  | 0
5-DaHall 1-PDU-14 | 28 | 0 |  |  | 0
5-DaHall 1-PDU-14 | 29 |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 30 |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 31 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 32 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-16 | 1 | 4.67 | 1.33 | 6.03 | 4.76 | 1.35 | 6.11 | 4.7003 | 1.3374 | 6.0648
5-DaHall 1-PDU-16 | 2 | 3.12 | 3.12 | 1.85 | 3.19 | 3.18 | 1.92 | 3.1513 | 3.1408 | 1.8705
5-DaHall 1-PDU-16 | 3 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-16 | 4 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-16 | 5 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-16 | 6 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-16 | 7 | 3.95 |  |  | 4.09 |  |  | 4.01
5-DaHall 1-PDU-16 | 8 | 4.86 |  |  | 4.9 |  |  | 4.877
5-DaHall 1-PDU-16 | 9 |  | 1.79 |  |  | 1.83 |  |  | 1.8033
5-DaHall 1-PDU-16 | 10 |  | 0.99 |  |  | 1.03 |  |  | 0.99968
5-DaHall 1-PDU-16 | 11 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-16 | 12 |  |  | 2.55 |  |  | 2.59 |  |  | 2.5684
5-DaHall 1-PDU-16 | 13 | 1.65 |  |  | 1.69 |  |  | 1.6658
5-DaHall 1-PDU-16 | 14 | 1.71 |  |  | 1.74 |  |  | 1.7262
5-DaHall 1-PDU-16 | 15 |  | 0.42 |  |  | 3.29 |  |  | 2.4403
5-DaHall 1-PDU-16 | 16 |  | 0 |  |  | 0
5-DaHall 1-PDU-16 | 17 |  |  | 0.39 |  |  | 3.28 |  |  | 1.5901
5-DaHall 1-PDU-16 | 18 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-16 | 19 | 0 |  |  | 0
5-DaHall 1-PDU-16 | 20 | 0.59 |  |  | 0.62 |  |  | 0.59852
5-DaHall 1-PDU-16 | 21 |  | 0.27 |  |  | 0.64 |  |  | 0.29432
5-DaHall 1-PDU-16 | 22 |  | 0.58 |  |  | 0.59 |  |  | 0.58994
5-DaHall 1-PDU-16 | 23 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-16 | 24 |  |  | 0.58 |  |  | 3.5 |  |  | 1.4604
5-DaHall 1-PDU-16 | 25 | 0.42 |  |  | 0.43 |  |  | 0.42399
5-DaHall 1-PDU-16 | 26 | 0 |  |  | 0
5-DaHall 1-PDU-16 | 27 |  | 1.48 |  |  | 1.49 |  |  | 1.4873
5-DaHall 1-PDU-16 | 28 |  | 0.29 |  |  | 0.31 |  |  | 0.29488
5-DaHall 1-PDU-16 | 29 |  |  | 2.21 |  |  | 2.23 |  |  | 2.2198
5-DaHall 1-PDU-16 | 30 |  |  | 0.48 |  |  | 0.5 |  |  | 0.49261
5-DaHall 1-PDU-17 | 1 | 0.59 |  |  | 0.72 |  |  | 0.71105
5-DaHall 1-PDU-17 | 2 | 0.83 |  |  | 0.84 |  |  | 0.83544
5-DaHall 1-PDU-17 | 3 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 4 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 5 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 6 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 7 | 0 |  |  | 0
5-DaHall 1-PDU-17 | 8 | 2.19 |  |  | 2.43 |  |  | 2.2542
5-DaHall 1-PDU-17 | 9 |  | 7.17 |  |  | 7.33 |  |  | 7.2041
5-DaHall 1-PDU-17 | 10 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 11 |  |  | 0.53 |  |  | 0.54 |  |  | 0.53
5-DaHall 1-PDU-17 | 12 |  |  | 1.11 |  |  | 1.12 |  |  | 1.1137
5-DaHall 1-PDU-17 | 13 | 0 |  |  | 0
5-DaHall 1-PDU-17 | 14 | 0 |  |  | 0
5-DaHall 1-PDU-17 | 15 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 16 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 17 |  |  | 0.75 |  |  | 0.77 |  |  | 0.75576
5-DaHall 1-PDU-17 | 18 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 19 | 0 |  |  | 0
5-DaHall 1-PDU-17 | 20 | 0 |  |  | 0
5-DaHall 1-PDU-17 | 21 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 22 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 23 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 24 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 25 | 1.81 |  |  | 1.83 |  |  | 1.8193
5-DaHall 1-PDU-17 | 26 | 0 |  |  | 0
5-DaHall 1-PDU-17 | 27 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 28 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 29 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 30 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 31 | 0 |  |  | 0
5-DaHall 1-PDU-17 | 32 | 0 |  |  | 0
5-DaHall 1-PDU-17 | 33 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 34 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 1 | 0.82 |  |  | 1.12 |  |  | 0.82156
5-DaHall 1-PDU-18 | 2 | 0.77 |  |  | 0.79 |  |  | 0.77978
5-DaHall 1-PDU-18 | 3 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 4 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 5 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 6 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 7 | 0 |  |  | 0
5-DaHall 1-PDU-18 | 8 | 2.14 |  |  | 2.27 |  |  | 2.1771
5-DaHall 1-PDU-18 | 9 |  | 4.96 |  |  | 5.05 |  |  | 5.0029
5-DaHall 1-PDU-18 | 10 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 11 |  |  | 0.41 |  |  | 0.42 |  |  | 0.41774
5-DaHall 1-PDU-18 | 12 |  |  | 0.8 |  |  | 0.81 |  |  | 0.80779
5-DaHall 1-PDU-18 | 13 | 0 |  |  | 0
5-DaHall 1-PDU-18 | 14 | 0 |  |  | 0
5-DaHall 1-PDU-18 | 15 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 16 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 17 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 18 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 19 | 0 |  |  | 0
5-DaHall 1-PDU-18 | 20 | 0 |  |  | 0
5-DaHall 1-PDU-18 | 21 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 22 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 23 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 24 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 25 | 1 |  |  | 1.02 |  |  | 1.0102
5-DaHall 1-PDU-18 | 26 | 0 |  |  | 0
5-DaHall 1-PDU-18 | 27 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 28 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 29 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 30 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 31 | 0 |  |  | 0
5-DaHall 1-PDU-18 | 32 | 0 |  |  | 0
5-DaHall 1-PDU-18 | 33 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 34 |  | 0 |  |  | 0
5-DaHall 1-PDU-19 | 1 | 3.8 |  |  | 4.31 |  |  | 3.9418
5-DaHall 1-PDU-19 | 2 | 2.85 |  |  | 11.86 |  |  | 5.3191
5-DaHall 1-PDU-19 | 3 |  | 4.02 |  |  | 8.04 |  |  | 5.3769
5-DaHall 1-PDU-19 | 4 |  | 3.31 |  |  | 10.64 |  |  | 4.9033
5-DaHall 1-PDU-19 | 5 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-19 | 6 |  |  | 2.78 |  |  | 4.04 |  |  | 2.9076
5-DaHall 1-PDU-19 | 7 | 3.45 |  |  | 12.58 |  |  | 7.7593
5-DaHall 1-PDU-19 | 8 | 4.58 |  |  | 8.53 |  |  | 5.7051
5-DaHall 1-PDU-19 | 9 |  | 3.38 |  |  | 13.86 |  |  | 5.6386
5-DaHall 1-PDU-19 | 10 |  | 4.24 |  |  | 10.7 |  |  | 5.9452
5-DaHall 1-PDU-19 | 11 |  |  | 3.96 |  |  | 9.01 |  |  | 5.1847
5-DaHall 1-PDU-19 | 12 |  |  | 3.98 |  |  | 4.17 |  |  | 4.0221
5-DaHall 1-PDU-19 | 13 | 3.33 |  |  | 12.88 |  |  | 5.4222
5-DaHall 1-PDU-19 | 14 | 1.38 |  |  | 1.53 |  |  | 1.459
5-DaHall 1-PDU-19 | 15 |  | 2.93 |  |  | 10.02 |  |  | 6.0915
5-DaHall 1-PDU-19 | 16 |  | 4.51 |  |  | 15.36 |  |  | 8.4182
5-DaHall 1-PDU-19 | 17 |  |  | 2.7 |  |  | 6.31 |  |  | 3.5638
5-DaHall 1-PDU-19 | 18 |  |  | 4.48 |  |  | 8.98 |  |  | 5.7545
5-DaHall 1-PDU-19 | 19 | 1.91 |  |  | 7.41 |  |  | 3.357
5-DaHall 1-PDU-19 | 20 | 5.98 |  |  | 11.5 |  |  | 9.1726
5-DaHall 1-PDU-19 | 21 |  | 0 |  |  | 0
5-DaHall 1-PDU-19 | 22 |  | 5.76 |  |  | 11.78 |  |  | 8.3185
5-DaHall 1-PDU-19 | 23 |  |  | 2.28 |  |  | 6.52 |  |  | 4.093
5-DaHall 1-PDU-19 | 24 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-20 | 1 | 4.82 |  |  | 5.62 |  |  | 5.046
5-DaHall 1-PDU-20 | 2 | 3.34 |  |  | 12.76 |  |  | 5.5928
5-DaHall 1-PDU-20 | 3 |  | 3.76 |  |  | 8.56 |  |  | 5.4173
5-DaHall 1-PDU-20 | 4 |  | 3.15 |  |  | 10.55 |  |  | 4.7785
5-DaHall 1-PDU-20 | 5 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-20 | 6 |  |  | 1.81 |  |  | 3.7 |  |  | 1.907
5-DaHall 1-PDU-20 | 7 | 4.08 |  |  | 12.2 |  |  | 8.0418
5-DaHall 1-PDU-20 | 8 | 4.5 |  |  | 8.93 |  |  | 5.8267
5-DaHall 1-PDU-20 | 9 |  | 3.29 |  |  | 14.09 |  |  | 5.5045
5-DaHall 1-PDU-20 | 10 |  | 4.02 |  |  | 10.8 |  |  | 5.8635
5-DaHall 1-PDU-20 | 11 |  |  | 3.34 |  |  | 8.3 |  |  | 4.603
5-DaHall 1-PDU-20 | 12 |  |  | 3.88 |  |  | 4.07 |  |  | 3.9181
5-DaHall 1-PDU-20 | 13 | 3.03 |  |  | 12.57 |  |  | 5.0315
5-DaHall 1-PDU-20 | 14 | 1.24 |  |  | 1.4 |  |  | 1.3219
5-DaHall 1-PDU-20 | 15 |  | 4.12 |  |  | 10.98 |  |  | 7.227
5-DaHall 1-PDU-20 | 16 |  | 4.63 |  |  | 15.9 |  |  | 8.5019
5-DaHall 1-PDU-20 | 17 |  |  | 3.16 |  |  | 6.57 |  |  | 3.9291
5-DaHall 1-PDU-20 | 18 |  |  | 4.34 |  |  | 8.55 |  |  | 5.5659
5-DaHall 1-PDU-20 | 19 | 2.07 |  |  | 7.96 |  |  | 3.3922
5-DaHall 1-PDU-20 | 20 | 0.86 |  |  | 5.8 |  |  | 1.977
5-DaHall 1-PDU-20 | 21 |  | 0 |  |  | 0
5-DaHall 1-PDU-20 | 22 |  | 0.58 |  |  | 3.61 |  |  | 1.1197
5-DaHall 1-PDU-20 | 23 |  |  | 2.15 |  |  | 6.72 |  |  | 4.2274
5-DaHall 1-PDU-20 | 24 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-21 | 1 | 6.16 |  |  | 10.25 |  |  | 7.5995
5-DaHall 1-PDU-21 | 2 | 2.88 |  |  | 9.48 |  |  | 4.1999
5-DaHall 1-PDU-21 | 3 |  | 5.94 |  |  | 9.18 |  |  | 6.8495
5-DaHall 1-PDU-21 | 4 |  | 3.05 |  |  | 9.99 |  |  | 3.873
5-DaHall 1-PDU-21 | 5 |  |  | 0.58 |  |  | 4.61 |  |  | 2.1626
5-DaHall 1-PDU-21 | 6 |  |  | 2.51 |  |  | 5.59 |  |  | 4.0804
5-DaHall 1-PDU-21 | 7 | 3.11 |  |  | 12.68 |  |  | 4.5803
5-DaHall 1-PDU-21 | 8 | 5.15 |  |  | 7.83 |  |  | 5.9152
5-DaHall 1-PDU-21 | 9 |  | 3.22 |  |  | 13.38 |  |  | 7.0874
5-DaHall 1-PDU-21 | 10 |  | 4.29 |  |  | 11.14 |  |  | 6.6714
5-DaHall 1-PDU-21 | 11 |  |  | 3.12 |  |  | 12.1 |  |  | 5.0477
5-DaHall 1-PDU-21 | 12 |  |  | 1.25 |  |  | 3.14 |  |  | 1.3844
5-DaHall 1-PDU-21 | 13 | 3.21 |  |  | 10.86 |  |  | 5.5473
5-DaHall 1-PDU-21 | 14 | 1.82 |  |  | 1.97 |  |  | 1.8972
5-DaHall 1-PDU-21 | 15 |  | 3.01 |  |  | 5.28 |  |  | 3.3058
5-DaHall 1-PDU-21 | 16 |  | 3.86 |  |  | 11.65 |  |  | 7.0836
5-DaHall 1-PDU-21 | 17 |  |  | 3.15 |  |  | 6.62 |  |  | 4.3588
5-DaHall 1-PDU-21 | 18 |  |  | 4.15 |  |  | 10.04 |  |  | 5.4447
5-DaHall 1-PDU-21 | 19 | 2.24 |  |  | 6.55 |  |  | 3.8694
5-DaHall 1-PDU-21 | 20 | 5.81 |  |  | 11.45 |  |  | 8.7852
5-DaHall 1-PDU-21 | 21 |  | 0 |  |  | 0
5-DaHall 1-PDU-21 | 22 |  | 5.71 |  |  | 8.26 |  |  | 6.872
5-DaHall 1-PDU-21 | 23 |  |  | 2.34 |  |  | 6.31 |  |  | 4.0131
5-DaHall 1-PDU-21 | 24 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-22 | 1 | 6.08 |  |  | 11.16 |  |  | 7.8832
5-DaHall 1-PDU-22 | 2 | 2.85 |  |  | 9.45 |  |  | 4.1375
5-DaHall 1-PDU-22 | 3 |  | 5.67 |  |  | 9.65 |  |  | 7.0698
5-DaHall 1-PDU-22 | 4 |  | 2.9 |  |  | 10.03 |  |  | 3.794
5-DaHall 1-PDU-22 | 5 |  |  | 1.44 |  |  | 4.48 |  |  | 2.0665
5-DaHall 1-PDU-22 | 6 |  |  | 1.57 |  |  | 4.57 |  |  | 2.3277
5-DaHall 1-PDU-22 | 7 | 3.06 |  |  | 12.46 |  |  | 4.4634
5-DaHall 1-PDU-22 | 8 | 5.06 |  |  | 10.17 |  |  | 6.3435
5-DaHall 1-PDU-22 | 9 |  | 3.32 |  |  | 13.4 |  |  | 7.172
5-DaHall 1-PDU-22 | 10 |  | 4.53 |  |  | 10.77 |  |  | 6.9704
5-DaHall 1-PDU-22 | 11 |  |  | 3.46 |  |  | 12.6 |  |  | 5.3723
5-DaHall 1-PDU-22 | 12 |  |  | 1.32 |  |  | 3.14 |  |  | 1.4594
5-DaHall 1-PDU-22 | 13 | 2.82 |  |  | 10.13 |  |  | 5.0662
5-DaHall 1-PDU-22 | 14 | 1.84 |  |  | 1.98 |  |  | 1.9136
5-DaHall 1-PDU-22 | 15 |  | 3.74 |  |  | 5.81 |  |  | 4.0154
5-DaHall 1-PDU-22 | 16 |  | 4.07 |  |  | 11.89 |  |  | 7.4035
5-DaHall 1-PDU-22 | 17 |  |  | 2.92 |  |  | 6.4 |  |  | 3.6848
5-DaHall 1-PDU-22 | 18 |  |  | 4.06 |  |  | 9.65 |  |  | 5.2239
5-DaHall 1-PDU-22 | 19 | 3.41 |  |  | 6.56 |  |  | 4.1795
5-DaHall 1-PDU-22 | 20 | 0.59 |  |  | 4.6 |  |  | 1.2915
5-DaHall 1-PDU-22 | 21 |  | 0 |  |  | 0
5-DaHall 1-PDU-22 | 22 |  | 0.59 |  |  | 3.8 |  |  | 1.1181
5-DaHall 1-PDU-22 | 23 |  |  | 2.44 |  |  | 6.52 |  |  | 4.1441
5-DaHall 1-PDU-22 | 24 |  |  | 0 |  |  | 0

## 4층_부하량
장비명 | 분기번호 | MIN |  |  | MAX |  |  | AVG
|  | R | S | T | R | S | T | R | S | T
4-DaHall 1-PDU-02 | 1 | 0.58 | 0.49 | 0.72 | 0.96 | 0.73 | 1.12 | 0.76489 | 0.62691 | 0.93398
4-DaHall 1-PDU-02 | 2 | 34.83 |  |  | 35.29 |  |  | 35.0725
4-DaHall 1-PDU-02 | 3 |  | 31.82 |  |  | 32.92 |  |  | 32.4505
4-DaHall 1-PDU-02 | 4 |  |  | 35.69 |  |  | 36.12 |  |  | 35.8779
4-DaHall 1-PDU-02 | 5 | 40.41 |  |  | 41.95 |  |  | 40.9814
4-DaHall 1-PDU-02 | 6 |  | 11.85 |  |  | 12.58 |  |  | 12.237
4-DaHall 1-PDU-02 | 7 |  |  | 28.4 |  |  | 30.05 |  |  | 28.9762
4-DaHall 1-PDU-02 | 8 | 0 |  |  | 0
4-DaHall 1-PDU-02 | 9 |  | 0 |  |  | 0
4-DaHall 1-PDU-04 | 1 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-PDU-04 | 2 | 38.59 |  |  | 42.02 |  |  | 39.458
4-DaHall 1-PDU-04 | 3 |  | 27.97 |  |  | 29.53 |  |  | 28.4812
4-DaHall 1-PDU-04 | 4 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-04 | 5 | 9.55 |  |  | 10 |  |  | 9.7623
4-DaHall 1-PDU-04 | 6 |  | 13.85 |  |  | 15.11 |  |  | 14.2855
4-DaHall 1-PDU-04 | 7 |  |  | 20.29 |  |  | 22.62 |  |  | 21.233
4-DaHall 1-PDU-04 | 8 | 21.11 |  |  | 23.54 |  |  | 22.1764
4-DaHall 1-PDU-04 | 9 |  | 0 |  |  | 0
4-DaHall 1-PDU-06 | 1 | 9.9 |  |  | 11.71 |  |  | 10.5706
4-DaHall 1-PDU-06 | 2 |  | 0 |  |  | 0
4-DaHall 1-PDU-06 | 3 |  |  | 8.86 |  |  | 9.15 |  |  | 8.9381
4-DaHall 1-PDU-06 | 4 | 6.84 |  |  | 7.55 |  |  | 6.9198
4-DaHall 1-PDU-06 | 5 |  | 0 |  |  | 0
4-DaHall 1-PDU-06 | 6 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-06 | 7 | 8.1 |  |  | 9.31 |  |  | 8.5589
4-DaHall 1-PDU-06 | 8 |  | 13.6 |  |  | 14.92 |  |  | 13.8972
4-DaHall 1-PDU-06 | 9 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-06 | 10 | 37.76 |  |  | 39.49 |  |  | 38.5282
4-DaHall 1-PDU-06 | 11 |  | 0 |  |  | 0
4-DaHall 1-PDU-06 | 12 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-08 | 1 | 22.22 |  |  | 24.7 |  |  | 22.8002
4-DaHall 1-PDU-08 | 2 |  | 32.59 |  |  | 35.2 |  |  | 33.2786
4-DaHall 1-PDU-08 | 3 |  |  | 5.28 |  |  | 5.59 |  |  | 5.3758
4-DaHall 1-PDU-08 | 4 | 9.27 |  |  | 9.95 |  |  | 9.4757
4-DaHall 1-PDU-08 | 5 |  | 7.35 |  |  | 7.89 |  |  | 7.4283
4-DaHall 1-PDU-08 | 6 |  |  | 10.78 |  |  | 13.9 |  |  | 12.136
4-DaHall 1-PDU-08 | 7 | 12.97 |  |  | 13.12 |  |  | 13.0373
4-DaHall 1-PDU-08 | 8 |  | 23.6 |  |  | 33.38 |  |  | 26.6682
4-DaHall 1-PDU-08 | 9 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-08 | 10 | 0 |  |  | 0
4-DaHall 1-PDU-08 | 11 |  | 0 |  |  | 0
4-DaHall 1-PDU-08 | 12 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-10 | 1 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-PDU-10 | 2 | 29.41 | 26.75 | 28.35 | 33.72 | 31.18 | 32.47 | 30.907 | 28.3418 | 29.8349
4-DaHall 1-PDU-10 | 3 | 2.92 | 2.63 | 3.19 | 28.8 | 27.98 | 27.64 | 15.2903 | 14.9519 | 14.7226
4-DaHall 1-PDU-01 | 1 | 1.2 | 0.96 | 1.4 | 1.48 | 1.18 | 1.65 | 1.3729 | 1.0805 | 1.5629
4-DaHall 1-PDU-01 | 2 | 37.17 |  |  | 37.75 |  |  | 37.4027
4-DaHall 1-PDU-01 | 3 |  | 33.35 |  |  | 34.72 |  |  | 34.2061
4-DaHall 1-PDU-01 | 4 |  |  | 36.92 |  |  | 37.32 |  |  | 37.1317
4-DaHall 1-PDU-01 | 5 | 41.05 |  |  | 42.44 |  |  | 41.454
4-DaHall 1-PDU-01 | 6 |  | 23.03 |  |  | 24.92 |  |  | 23.6876
4-DaHall 1-PDU-01 | 7 |  |  | 12.37 |  |  | 13.07 |  |  | 12.6612
4-DaHall 1-PDU-01 | 8 | 0 |  |  | 0
4-DaHall 1-PDU-01 | 9 |  | 0 |  |  | 0
4-DaHall 1-PDU-03 | 1 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-PDU-03 | 2 | 29.71 |  |  | 33.49 |  |  | 32.2014
4-DaHall 1-PDU-03 | 3 |  | 27.78 |  |  | 28.49 |  |  | 28.08
4-DaHall 1-PDU-03 | 4 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-03 | 5 | 6.2 |  |  | 6.6 |  |  | 6.394
4-DaHall 1-PDU-03 | 6 |  | 9.8 |  |  | 10.62 |  |  | 10.2225
4-DaHall 1-PDU-03 | 7 |  |  | 27.76 |  |  | 30.88 |  |  | 28.9908
4-DaHall 1-PDU-03 | 8 | 17.47 |  |  | 20 |  |  | 18.4772
4-DaHall 1-PDU-03 | 9 |  | 0 |  |  | 0
4-DaHall 1-PDU-05 | 1 | 8.14 |  |  | 9.93 |  |  | 8.9845
4-DaHall 1-PDU-05 | 2 |  | 0 |  |  | 0
4-DaHall 1-PDU-05 | 3 |  |  | 7.67 |  |  | 7.76 |  |  | 7.7143
4-DaHall 1-PDU-05 | 4 | 7.14 |  |  | 7.51 |  |  | 7.2079
4-DaHall 1-PDU-05 | 5 |  | 0 |  |  | 0
4-DaHall 1-PDU-05 | 6 |  |  | 12.67 |  |  | 13.74 |  |  | 12.8443
4-DaHall 1-PDU-05 | 7 | 6.52 |  |  | 7.67 |  |  | 6.7918
4-DaHall 1-PDU-05 | 8 |  | 12.19 |  |  | 13.92 |  |  | 13.3068
4-DaHall 1-PDU-05 | 9 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-05 | 10 | 31.49 |  |  | 33.02 |  |  | 31.9029
4-DaHall 1-PDU-05 | 11 |  | 0 |  |  | 0
4-DaHall 1-PDU-05 | 12 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-07 | 1 | 20.1 |  |  | 21.93 |  |  | 20.5084
4-DaHall 1-PDU-07 | 2 |  | 32.83 |  |  | 35.53 |  |  | 33.5524
4-DaHall 1-PDU-07 | 3 |  |  | 5.19 |  |  | 5.52 |  |  | 5.2835
4-DaHall 1-PDU-07 | 4 | 10.11 |  |  | 10.84 |  |  | 10.3815
4-DaHall 1-PDU-07 | 5 |  | 5.95 |  |  | 6.44 |  |  | 6.0018
4-DaHall 1-PDU-07 | 6 |  |  | 14.28 |  |  | 17.48 |  |  | 15.8815
4-DaHall 1-PDU-07 | 7 | 13.74 |  |  | 13.9 |  |  | 13.8157
4-DaHall 1-PDU-07 | 8 |  | 31.44 |  |  | 37.6 |  |  | 34.5307
4-DaHall 1-PDU-07 | 9 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-07 | 10 | 0 |  |  | 0
4-DaHall 1-PDU-07 | 11 |  | 0 |  |  | 0
4-DaHall 1-PDU-07 | 12 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-09 | 1 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-PDU-09 | 2 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-PDU-09 | 3 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-PDU-11 | 1 | 0.44 | 0.34 | 0.34 | 0.44 | 0.35 | 0.35 | 0.44 | 0.34959 | 0.34999
4-DaHall 1-PDU-11 | 2 | 0 |  |  | 0
4-DaHall 1-PDU-11 | 3 |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 4 |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 5 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 6 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 7 | 0 |  |  | 0
4-DaHall 1-PDU-11 | 8 | 0 |  |  | 0
4-DaHall 1-PDU-11 | 9 |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 10 |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 11 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 12 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 13 | 0 |  |  | 0
4-DaHall 1-PDU-11 | 14 | 0 |  |  | 0
4-DaHall 1-PDU-11 | 15 |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 16 |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 17 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 18 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 19 | 0 |  |  | 0
4-DaHall 1-PDU-11 | 20 | 0 |  |  | 0
4-DaHall 1-PDU-11 | 21 |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 22 |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 23 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 24 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 25 | 0 |  |  | 0
4-DaHall 1-PDU-11 | 26 | 0 |  |  | 0
4-DaHall 1-PDU-11 | 27 |  | 0.28 |  |  | 0.28 |  |  | 0.28
4-DaHall 1-PDU-11 | 28 |  | 0.22 |  |  | 0.25 |  |  | 0.22021
4-DaHall 1-PDU-11 | 29 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 30 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 31 | 0 |  |  | 0
4-DaHall 1-PDU-11 | 32 | 0 |  |  | 0
4-DaHall 1-PDU-11 | 33 |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 34 |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 35 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 36 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 37 | 0 |  |  | 0
4-DaHall 1-PDU-11 | 38 | 0 |  |  | 0
4-DaHall 1-PDU-11 | 39 |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 40 |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 41 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 42 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 43 | 0 |  |  | 0
4-DaHall 1-PDU-11 | 44 | 0 |  |  | 0
4-DaHall 1-PDU-11 | 45 |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 46 |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 47 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 48 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-11 | 49 | 0 |  |  | 0
4-DaHall 1-PDU-11 | 50 | 0 |  |  | 0
4-DaHall 1-PDU-12 | 1 | 0.44 | 0.2 | 0 | 0.44 | 0.2 | 0 | 0.44 | 0.2
4-DaHall 1-PDU-12 | 2 | 0 |  |  | 0
4-DaHall 1-PDU-12 | 3 |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 4 |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 5 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 6 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 7 | 0 |  |  | 0
4-DaHall 1-PDU-12 | 8 | 0 |  |  | 0
4-DaHall 1-PDU-12 | 9 |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 10 |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 11 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 12 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 13 | 0 |  |  | 0
4-DaHall 1-PDU-12 | 14 | 0 |  |  | 0
4-DaHall 1-PDU-12 | 15 |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 16 |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 17 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 18 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 19 | 0 |  |  | 0
4-DaHall 1-PDU-12 | 20 | 0 |  |  | 0
4-DaHall 1-PDU-12 | 21 |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 22 |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 23 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 24 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 25 | 0 |  |  | 0
4-DaHall 1-PDU-12 | 26 | 0 |  |  | 0
4-DaHall 1-PDU-12 | 27 |  | 2.17 |  |  | 2.18 |  |  | 2.1701
4-DaHall 1-PDU-12 | 28 |  | 0.94 |  |  | 0.99 |  |  | 0.94375
4-DaHall 1-PDU-12 | 29 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 30 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 31 | 0 |  |  | 0
4-DaHall 1-PDU-12 | 32 | 0 |  |  | 0
4-DaHall 1-PDU-12 | 33 |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 34 |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 35 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 36 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 37 | 0 |  |  | 0
4-DaHall 1-PDU-12 | 38 | 0 |  |  | 0
4-DaHall 1-PDU-12 | 39 |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 40 |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 41 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 42 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 43 | 0 |  |  | 0
4-DaHall 1-PDU-12 | 44 | 0 |  |  | 0
4-DaHall 1-PDU-12 | 45 |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 46 |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 47 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 48 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-12 | 49 | 0 |  |  | 0
4-DaHall 1-PDU-12 | 50 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 1 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 2 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 3 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 4 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 5 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 6 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 7 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 8 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 9 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 10 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 11 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 12 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 13 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 14 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 15 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 16 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 17 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 18 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 19 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 20 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 21 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 22 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 23 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 24 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 25 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 26 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 27 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 28 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 29 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 30 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 31 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 32 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 33 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 34 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 35 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 36 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 37 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 38 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 39 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 40 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 41 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 42 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 43 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 44 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 45 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 46 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 47 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 48 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 49 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 50 | 0 |  |  | 0
4-DaHall 1-PDU-13 | 51 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 52 |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 53 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-13 | 54 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 1 | 0 |  |  | 0
4-DaHall 1-PDU-14 | 2 | 0 |  |  | 0
4-DaHall 1-PDU-14 | 3 |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 4 |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 5 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 6 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 7 | 0 |  |  | 0
4-DaHall 1-PDU-14 | 8 | 0 |  |  | 0
4-DaHall 1-PDU-14 | 9 |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 10 |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 11 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 12 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 13 | 0 |  |  | 0.65 |  |  | 0.00045139
4-DaHall 1-PDU-14 | 14 | 0 |  |  | 0
4-DaHall 1-PDU-14 | 15 |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 16 |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 17 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 18 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 19 | 0 |  |  | 0
4-DaHall 1-PDU-14 | 20 | 0 |  |  | 0
4-DaHall 1-PDU-14 | 21 |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 22 |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 23 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 24 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 25 | 0 |  |  | 0
4-DaHall 1-PDU-14 | 26 | 0 |  |  | 0
4-DaHall 1-PDU-14 | 27 |  | 0 |  |  | 5.85 |  |  | 0.0040625
4-DaHall 1-PDU-14 | 28 |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 29 |  |  | 0 |  |  | 5.99 |  |  | 0.0041626
4-DaHall 1-PDU-14 | 30 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 31 | 0 |  |  | 0
4-DaHall 1-PDU-14 | 32 | 0 |  |  | 0
4-DaHall 1-PDU-14 | 33 |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 34 |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 35 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 36 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 37 | 0 |  |  | 0
4-DaHall 1-PDU-14 | 38 | 0 |  |  | 5.8 |  |  | 0.0040306
4-DaHall 1-PDU-14 | 39 |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 40 |  | 0 |  |  | 1.26 |  |  | 0.00087561
4-DaHall 1-PDU-14 | 41 |  |  | 0 |  |  | 5.95 |  |  | 0.0041319
4-DaHall 1-PDU-14 | 42 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 43 | 0 |  |  | 0
4-DaHall 1-PDU-14 | 44 | 0 |  |  | 6.05 |  |  | 0.0082557
4-DaHall 1-PDU-14 | 45 |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 46 |  | 0 |  |  | 5.86 |  |  | 0.0040694
4-DaHall 1-PDU-14 | 47 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 48 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 49 | 0 |  |  | 0
4-DaHall 1-PDU-14 | 50 | 0 |  |  | 0
4-DaHall 1-PDU-14 | 51 |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 52 |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 53 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-14 | 54 |  |  | 0 |  |  | 0
4-DaHall 1-RPP-01 | 1 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-RPP-01 | 2 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-RPP-01 | 3 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-RPP-01 | 4 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-RPP-01 | 5 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-RPP-01 | 6 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-RPP-01 | 7 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-RPP-01 | 8 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-RPP-02 | 1 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-RPP-02 | 2 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-RPP-02 | 3 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-RPP-02 | 4 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-RPP-02 | 5 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-RPP-02 | 6 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-RPP-02 | 7 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-RPP-02 | 8 | 0 | 0 | 0 | 0 | 0 | 0

## 4F_current (hidden)
4F | A(전류)
4-DaHall 1-PDU-01-01 | [branch#001] [A] current
4-DaHall 1-PDU-01-02 | [branch#002] [A] current
4-DaHall 1-PDU-01-03 | [branch#003] [A] current
4-DaHall 1-PDU-01-04 | [branch#004] [A] current
4-DaHall 1-PDU-01-05 | [branch#005] [A] current
4-DaHall 1-PDU-01-06 | [branch#006] [A] current
4-DaHall 1-PDU-01-07 | [branch#007] [A] current
4-DaHall 1-PDU-01-08 | [branch#008] [A] current
4-DaHall 1-PDU-01-09 | [branch#009] [A] current
4-DaHall 1-PDU-02-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
4-DaHall 1-PDU-02-02 | [branch#002] [A] current
4-DaHall 1-PDU-02-03 | [branch#003] [A] current
4-DaHall 1-PDU-02-04 | [branch#004] [A] current
4-DaHall 1-PDU-02-05 | [branch#005] [A] current
4-DaHall 1-PDU-02-06 | [branch#006] [A] current
4-DaHall 1-PDU-02-07 | [branch#007] [A] current
4-DaHall 1-PDU-02-08 | [branch#008] [A] current
4-DaHall 1-PDU-02-09 | [branch#009] [A] current
4-DaHall 1-PDU-03-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
4-DaHall 1-PDU-03-02 | [branch#002] [A] current
4-DaHall 1-PDU-03-03 | [branch#003] [A] current
4-DaHall 1-PDU-03-04 | [branch#004] [A] current
4-DaHall 1-PDU-03-05 | [branch#005] [A] current
4-DaHall 1-PDU-03-06 | [branch#006] [A] current
4-DaHall 1-PDU-03-07 | [branch#007] [A] current
4-DaHall 1-PDU-03-08 | [branch#008] [A] current
4-DaHall 1-PDU-03-09 | [branch#009] [A] current
4-DaHall 1-PDU-04-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
4-DaHall 1-PDU-04-02 | [branch#002] [A] current
4-DaHall 1-PDU-04-03 | [branch#003] [A] current
4-DaHall 1-PDU-04-04 | [branch#004] [A] current
4-DaHall 1-PDU-04-05 | [branch#005] [A] current
4-DaHall 1-PDU-04-06 | [branch#006] [A] current
4-DaHall 1-PDU-04-07 | [branch#007] [A] current
4-DaHall 1-PDU-04-08 | [branch#008] [A] current
4-DaHall 1-PDU-04-09 | [branch#009] [A] current
4-DaHall 1-PDU-05-01 | [branch#001] [A] current
4-DaHall 1-PDU-05-02 | [branch#002] [A] current
4-DaHall 1-PDU-05-03 | [branch#003] [A] current
4-DaHall 1-PDU-05-04 | [branch#004] [A] current
4-DaHall 1-PDU-05-05 | [branch#005] [A] current
4-DaHall 1-PDU-05-06 | [branch#006] [A] current
4-DaHall 1-PDU-05-07 | [branch#007] [A] current
4-DaHall 1-PDU-05-08 | [branch#008] [A] current
4-DaHall 1-PDU-05-09 | [branch#009] [A] current
4-DaHall 1-PDU-05-10 | [branch#010] [A] current
4-DaHall 1-PDU-05-11 | [branch#011] [A] current
4-DaHall 1-PDU-05-12 | [branch#012] [A] current
4-DaHall 1-PDU-06-01 | [branch#001] [A] current
4-DaHall 1-PDU-06-02 | [branch#002] [A] current
4-DaHall 1-PDU-06-03 | [branch#003] [A] current
4-DaHall 1-PDU-06-04 | [branch#004] [A] current
4-DaHall 1-PDU-06-05 | [branch#005] [A] current
4-DaHall 1-PDU-06-06 | [branch#006] [A] current
4-DaHall 1-PDU-06-07 | [branch#007] [A] current
4-DaHall 1-PDU-06-08 | [branch#008] [A] current
4-DaHall 1-PDU-06-09 | [branch#009] [A] current
4-DaHall 1-PDU-06-10 | [branch#010] [A] current
4-DaHall 1-PDU-06-11 | [branch#011] [A] current
4-DaHall 1-PDU-06-12 | [branch#012] [A] current
4-DaHall 1-PDU-07-01 | [branch#001] [A] current
4-DaHall 1-PDU-07-02 | [branch#002] [A] current
4-DaHall 1-PDU-07-03 | [branch#003] [A] current
4-DaHall 1-PDU-07-04 | [branch#004] [A] current
4-DaHall 1-PDU-07-05 | [branch#005] [A] current
4-DaHall 1-PDU-07-06 | [branch#006] [A] current
4-DaHall 1-PDU-07-07 | [branch#007] [A] current
4-DaHall 1-PDU-07-08 | [branch#008] [A] current
4-DaHall 1-PDU-07-09 | [branch#009] [A] current
4-DaHall 1-PDU-07-10 | [branch#010] [A] current
4-DaHall 1-PDU-07-11 | [branch#011] [A] current
4-DaHall 1-PDU-07-12 | [branch#012] [A] current
4-DaHall 1-PDU-08-01 | [branch#001] [A] current
4-DaHall 1-PDU-08-02 | [branch#002] [A] current
4-DaHall 1-PDU-08-03 | [branch#003] [A] current
4-DaHall 1-PDU-08-04 | [branch#004] [A] current
4-DaHall 1-PDU-08-05 | [branch#005] [A] current
4-DaHall 1-PDU-08-06 | [branch#006] [A] current
4-DaHall 1-PDU-08-07 | [branch#007] [A] current
4-DaHall 1-PDU-08-08 | [branch#008] [A] current
4-DaHall 1-PDU-08-09 | [branch#009] [A] current
4-DaHall 1-PDU-08-10 | [branch#010] [A] current
4-DaHall 1-PDU-08-11 | [branch#011] [A] current
4-DaHall 1-PDU-08-12 | [branch#012] [A] current
4-DaHall 1-PDU-09-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
4-DaHall 1-PDU-09-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
4-DaHall 1-PDU-09-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
4-DaHall 1-PDU-10-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
4-DaHall 1-PDU-10-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
4-DaHall 1-PDU-10-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
4-EPS-CEP-06-01-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
4-EPS-CEP-06-01-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
4-EPS-CEP-06-01-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
4-EPS-CEP-06-01-04 | [branch#004] [R] I1 | [branch#004] [S] I2 | [branch#004] [T] I3
4-EPS-CEP-06-01-05 | [branch#005] [R] I1 | [branch#005] [S] I2 | [branch#005] [T] I3
4-EPS-CEP-06-01-06 | [branch#006] [R] I1 | [branch#006] [S] I2 | [branch#006] [T] I3

## 각_층_분전반_부하량 (hidden)
차단기 사용 현황
7층 | Device Name | DE 분전반 신규명칭 | 분전반 명칭 | 차단전류 (A) | 메인차단용량 (kVA) | IT허용용량 (kVA) | 사용량 (kVA) | 사용율 (%) | 2P 20A |  |  | 2P 30A |  |  | 2P 50A |  |  | 4P 225A |  |  | 3P 100A |  |  | 3P 150A |  |  | 4P 50A
[9 empty] | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF
| 7-Data Hall 1-RPP-01 | 7-1-A1 | UPS 출력 분전반 A1(From:7F 창고) | 400 | 263.2717 | 200 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | #REF! | #REF!
| 7-Data Hall 1-RPP-02 | 7-1-B1 | UPS 출력 분전반 B1(From:7F 창고) | 400 | 263.2717 | 200 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | #REF! | #REF!
| 7-Data Hall 1-PDU-01 | 7-1-A2 | U3-7A PANEL(From:TRroom-U7-5A) | 300 | 197.4538 | 150 | #REF! | #REF! |  |  |  | 2 | #REF! | #REF!
| 7-Data Hall 1-PDU-02 | 7-1-B2 | U3-7B PANEL(From:TRroom-U7-6B) | 300 | 197.4538 | 150 | #REF! | #REF! |  |  |  | 2 | #REF! | #REF!
| 7-Data Hall 1-RPP-03 | 7-1-A3 | UPS 출력 분전반 A2(From:7F 창고) | 225 | 148.0903 | 112.5 | #REF! | #REF! | [6 empty] | 2 | #REF! | #REF!
| 7-Data Hall 1-RPP-04 | 7-1-B3 | UPS 출력 분전반 B2(From:7F 창고) | 225 | 148.0903 | 112.5 | #REF! | #REF! | [6 empty] | 2 | #REF! | #REF!
| 7-Data Hall 1-PDU-03 | 7-1-A4 | UPS 출력 분전반 A(From:7F TR.Room) | 400 | 263.2717 | 200 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 7-Data Hall 1-PDU-04 | 7-1-B4 | UPS 출력 분전반 B(From:7F TR.Room) | 400 | 263.2717 | 200 | #REF! | #REF! | [12 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
|  | 총계 | 총계 | 1400 | 921.451 | 700 | #REF! | #REF! | [18 empty] | 2 | #REF! | #REF!
6층 | Device Name | DE 분전반 신규명칭 | 분전반 명칭 | 차단전류 (A) | 메인차단용량 (kVA) | IT허용용량 (kVA) | 사용량 (kVA) | 사용율 (%) | 2P 30A
[9 empty] | 총계 | ON | OFF
| 6-DaHall 1-PDU-01 | 6-1-A1 | U-A1 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-02 | 6-1-B1 | U-B1 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-03 | 6-1-A2 | U-A2 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-04 | 6-1-B2 | U-B2 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-05 | 6-1-A3 | U6-A5 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-06 | 6-1-B3 | U6-B5 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-07 | 6-1-A4 | U6-A6 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-08 | 6-1-B4 | U6-B6 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-09 | 6-1-A5 | U-A3 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-10 | 6-1-B5 | U-B3 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-11 | 6-1-A6 | U-A4 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-12 | 6-1-B6 | U-B4 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-13 | 6-1-A7 | U6-A7 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-14 | 6-1-B7 | U6-B7 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
|  | 총계 | 총계 | 3400 | 2237.8096 | 700 | #REF! | #REF!
5층 | Device Name | DE 분전반 신규명칭 | 분전반 명칭 | 차단전류 (A) | 메인차단용량 (kVA) | IT허용용량 (kVA) | 사용량 (kVA) | 사용율 (%) | 2P 30A |  |  | 2P 50A |  |  | 3P 60A |  |  | 3P 30A |  |  | 3P 20A |  |  | 3P 50A
[9 empty] | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF
| 5-DaHall 1-PDU-01 | 5-1-A1 | U5-1A | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF! |  |  |  | 2 | 1 | 1
| 5-DaHall 1-PDU-02 | 5-1-B1 | U5-1B | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF! |  |  |  | 2 | 1 | 1
| 5-DaHall 1-PDU-03 | 5-1-A2 | U5-2A | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF! |  |  |  | 2 | 1 | 1
| 5-DaHall 1-PDU-04 | 6-1-B2 | U5-2B | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF! |  |  |  | 2 | 1 | 1
| 5-DaHall 1-PDU-05 | 5-1-A3 | U5-3A | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-06 | 5-1-B3 | U5-3B | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-07 | 5-1-A4 | PDU(A)-9 | 200 | 131.6359 | 23.9316 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-08 | 5-1-B4 | PDU(B)-9 | 200 | 131.6359 | 23.9316 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-09 | 5-1-A5 | PDU(A)-10 | 200 | 131.6359 | 23.9316 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-10 | 5-1-B5 | PDU(B)-10 | 200 | 131.6359 | 23.9316 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-11 | 5-1-A6 | PDU(A)-1 | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-12 | 5-1-B6 | PDU(B)-1 | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-13 | 5-1-A7 | PDU(A)-2 | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-14 | 5-1-B7 | PDU(B)-2 | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-15 | 5-1-A8 | PDU(A)-3 | 300 | 197.4538 | 35.8974 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-16 | 5-1-B8 | PDU(B)-3 | 300 | 197.4538 | 35.8974 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 1 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-17 | 5-1-A9 | Singtel PDU-8-A | 200 | 131.6359 | 23.9316 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-18 | 5-1-B9 | Singtel PDU-8-B | 200 | 131.6359 | 23.9316 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-19 | 5-1-A10 | LG PDU(A1) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 3 | #REF! | #REF! | 5 | #REF! | #REF! |  |  |  | 2 | #REF! | #REF! | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-20 | 5-1-B10 | LG PDU(B1) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 3 | #REF! | #REF! | 5 | #REF! | #REF! |  |  |  | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-21 | 5-1-A11 | LG PDU(A2) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 3 | #REF! | #REF! | 5 | #REF! | #REF! |  |  |  | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-22 | 5-1-B11 | LG PDU(B2) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 3 | #REF! | #REF! | 5 | #REF! | #REF! |  |  |  | 2 | #REF! | #REF! | 1 | #REF! | #REF! | 2 | #REF! | #REF!
|  |  | PDU6B-1T | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
|  |  | PDU(C) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF! | 2 | 0 | 2
|  | 총계 | 총계 | 5850 | 3850.3489 | 700 | #REF! | #REF!
4층 | Device Name | DE 분전반 신규명칭 | 분전반 명칭 | 차단전류 (A) | 메인차단용량 (kVA) | 통신전력기준 (kVA) | 사용량 (kVA) | 사용율 (%) | 2P 100A |  |  | 4P 100A |  |  | 4P 200A
[9 empty] | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF
| 4-DaHall 1-PDU-01 | 4-1-A1 | KEN 8 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | 1 | 0
| 4-DaHall 1-PDU-02 | 4-1-B1 | KEN 1 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | 1 | 0
| 4-DaHall 1-PDU-03 | 4-1-A2 | KEN 9 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | 0 | 1
| 4-DaHall 1-PDU-04 | 4-1-B2 | KEN 2 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | 0 | 1
| 4-DaHall 1-PDU-05 | 4-1-A3 | KEN 10 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-06 | 4-1-B3 | KEN 3 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-07 | 4-1-A4 | KEN 13 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-08 | 4-1-B4 | KEN 6 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-09 | 4-1-A5 | KEN 14 | 300 | 197.4538 | 70 | #REF! | #REF! | [6 empty] | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-10 | 4-1-B5 | KEN 7 | 300 | 197.4538 | 70 | #REF! | #REF! | [6 empty] | 1 | #REF! | #REF!
|  | 총계 | 총계 | 3000 | 1974.5379 | 700 | #REF! | #REF!
|  |  | 각층 부하분담율 |  |  | 사용량(A) | 층 배분(%)
|  |  | 4층 | IDC | IDC | #REF! | #REF!
|  |  |  | IP | 세종 시스템 | #REF! | #REF!
|  |  |  | 공통 | 세종 시스템 | #REF! | #REF!
|  |  |  | IP | core room | #REF! | #REF!
[5 empty] | 총 합 | #REF! | #REF!
|  |  | 5층 | IDC | IDC | #REF!
|  |  | 6층 | IDC | IDC | #REF!
|  |  | 7층 | IDC | IDC상면 | #REF! | #REF!
|  |  |  | IP | 세종 인터넷 | #REF! | #REF!
|  |  |  | 전송 | 전송 | #REF! | #REF!
|  |  |  | 전송 | 정류기 | #REF! | #REF!
|  |  |  | 전송/인터넷 | 세종 7층 NOC(미확인 포함) | #REF! | #REF!
[5 empty] | 총 합 | #REF! | #REF!

## 세분화 (hidden)
차단기 사용 현황
7층 | Device Name | DE 분전반 신규명칭 | 분전반 명칭 | 차단전류 (A) | 메인차단용량 (kVA) | IT허용용량 (kVA) | 사용량 (kVA) | 사용율 (%) | 2P 20A |  |  | 2P 30A |  |  | 2P 50A |  |  | 4P 225A |  |  | 3P 100A |  |  | 3P 150A |  |  | 4P 50A
[9 empty] | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF
| 7-DaHall 1-RPP-01 | 7-1-A1 | UPS 출력 분전반 A1(From:7F 창고) | 400 | 263.2717 | 200 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | #REF! | #REF!
| 7-DaHall 1-PDU-01 | 7-1-A2 | U3-7A PANEL(From:TRroom-U7-5A) | 300 | 197.4538 | 150 | #REF! | #REF! |  |  |  | 2 | #REF! | #REF!
| 7-DaHall 1-RPP-03 | 7-1-A3 | UPS 출력 분전반 A2(From:7F 창고) | 225 | 148.0903 | 112.5 | #REF! | #REF! | [6 empty] | 2 | #REF! | #REF!
| 7-DaHall 1-PDU-03 | 7-1-A4 | UPS 출력 분전반 A(From:7F TR.Room) | 400 | 263.2717 | 200 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 7-DaHall 1-RPP-02 | 7-1-B1 | UPS 출력 분전반 B1(From:7F 창고) | 400 | 263.2717 | 200 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | #REF! | #REF!
| 7-DaHall 1-PDU-02 | 7-1-B2 | U3-7B PANEL(From:TRroom-U7-6B) | 300 | 197.4538 | 150 | #REF! | #REF! |  |  |  | 2 | #REF! | #REF!
| 7-DaHall 1-RPP-04 | 7-1-B3 | UPS 출력 분전반 B2(From:7F 창고) | 225 | 148.0903 | 112.5 | #REF! | #REF! | [6 empty] | 2 | #REF! | #REF!
| 7-DaHall 1-PDU-04 | 7-1-B4 | UPS 출력 분전반 B(From:7F TR.Room) | 400 | 263.2717 | 200 | #REF! | #REF! | [12 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
|  | 총계 | 총계 | 1400 | 921.451 | 700 | #REF! | #REF! | [18 empty] | 2 | #REF! | #REF!
6층 | Device Name | DE 분전반 신규명칭 | 분전반 명칭 | 차단전류 (A) | 메인차단용량 (kVA) | IT허용용량 (kVA) | 사용량 (kVA) | 사용율 (%) | 2P 30A
[9 empty] | 총계 | ON | OFF
| 6-DaHall 1-PDU-01 | 6-1-A1 | U-A1 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-03 | 6-1-A2 | U-A2 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-05 | 6-1-A3 | U6-A5 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-07 | 6-1-A4 | U6-A6 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-09 | 6-1-A5 | U-A3 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-11 | 6-1-A6 | U-A4 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-13 | 6-1-A7 | U6-A7 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-02 | 6-1-B1 | U-B1 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-04 | 6-1-B2 | U-B2 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-06 | 6-1-B3 | U6-B5 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-08 | 6-1-B4 | U6-B6 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-10 | 6-1-B5 | U-B3 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-12 | 6-1-B6 | U-B4 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-14 | 6-1-B7 | U6-B7 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
|  | 총계 | 총계 | 3400 | 2237.8096 | 700 | #REF! | #REF!
5층 | Device Name | DE 분전반 신규명칭 | 분전반 명칭 | 차단전류 (A) | 메인차단용량 (kVA) | IT허용용량 (kVA) | 사용량 (kVA) | 사용율 (%) | 2P 30A |  |  | 2P 50A |  |  | 3P 60A |  |  | 3P 30A |  |  | 3P 20A |  |  | 3P 50A
[9 empty] | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF
| 5-DaHall 1-PDU-01 | 5-1-A1 | U5-1A | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF! |  |  |  | 2 | 1 | 1
| 5-DaHall 1-PDU-03 | 5-1-A2 | U5-2A | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF! |  |  |  | 2 | 1 | 1
| 5-DaHall 1-PDU-05 | 5-1-A3 | U5-3A | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-07 | 5-1-A4 | PDU(A)-9 | 200 | 131.6359 | 23.9316 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-09 | 5-1-A5 | PDU(A)-10 | 200 | 131.6359 | 23.9316 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-11 | 5-1-A6 | PDU(A)-1 | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-13 | 5-1-A7 | PDU(A)-2 | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-15 | 5-1-A8 | PDU(A)-3 | 300 | 197.4538 | 35.8974 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-17 | 5-1-A9 | Singtel PDU-8-A | 200 | 131.6359 | 23.9316 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-19 | 5-1-A10 | LG PDU(A1) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 3 | #REF! | #REF! | 5 | #REF! | #REF!
| 5-DaHall 1-PDU-21 | 5-1-A11 | LG PDU(A2) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 3 | #REF! | #REF! | 5 | #REF! | #REF!
| 5-DaHall 1-PDU-02 | 5-1-B1 | U5-1B | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF! |  |  |  | 2 | 1 | 1
| 5-DaHall 1-PDU-04 | 6-1-B2 | U5-2B | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF! |  |  |  | 2 | 1 | 1
| 5-DaHall 1-PDU-06 | 5-1-B3 | U5-3B | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-08 | 5-1-B4 | PDU(B)-9 | 200 | 131.6359 | 23.9316 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-10 | 5-1-B5 | PDU(B)-10 | 200 | 131.6359 | 23.9316 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-12 | 5-1-B6 | PDU(B)-1 | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-14 | 5-1-B7 | PDU(B)-2 | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-16 | 5-1-B8 | PDU(B)-3 | 300 | 197.4538 | 35.8974 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 1 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-18 | 5-1-B9 | Singtel PDU-8-B | 200 | 131.6359 | 23.9316 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-20 | 5-1-B10 | LG PDU(B1) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 3 | #REF! | #REF! | 5 | #REF! | #REF!
| 5-DaHall 1-PDU-22 | 5-1-B11 | LG PDU(B2) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 3 | #REF! | #REF! | 5 | #REF! | #REF!
|  |  | PDU6B-1T | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
|  |  | PDU(C) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF! | 2 | 0 | 2
|  | 총계 | 총계 | 5850 | 3850.3489 | 700 | #REF! | #REF!
4층 | Device Name | DE 분전반 신규명칭 | 분전반 명칭 | 차단전류 (A) | 메인차단용량 (kVA) | IT허용용량 (kVA) | 사용량 (kVA) | 사용율 (%) | 2P 100A |  |  | 4P 100A |  |  | 4P 200A
[9 empty] | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF
| 4-DaHall 1-PDU-01 | 4-1-A1 | KEN 8 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | 1 | 0
| 4-DaHall 1-PDU-03 | 4-1-A2 | KEN 9 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | 0 | 1
| 4-DaHall 1-PDU-05 | 4-1-A3 | KEN 10 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-07 | 4-1-A4 | KEN 13 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-09 | 4-1-A5 | KEN 14 | 300 | 197.4538 | 70 | #REF! | #REF! | [6 empty] | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-02 | 4-1-B1 | KEN 1 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | 1 | 0
| 4-DaHall 1-PDU-04 | 4-1-B2 | KEN 2 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | 0 | 1
| 4-DaHall 1-PDU-06 | 4-1-B3 | KEN 3 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-08 | 4-1-B4 | KEN 6 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-10 | 4-1-B5 | KEN 7 | 300 | 197.4538 | 70 | #REF! | #REF! | [6 empty] | 1 | #REF! | #REF!
|  | 총계 | 총계 | 3000 | 1974.5379 | 700 | #REF! | #REF!
|  |  | 각층 부하분담율 |  |  | 사용량(A) | 층 배분(%)
|  |  | 4층 | IDC | DEKR IDC | #REF! | #REF!
|  |  |  | IP | 세종 시스템 | #REF! | #REF!
|  |  |  | 공통 | 세종 시스템 | #REF! | #REF!
|  |  |  | IP | 세종 core room | #REF! | #REF!
[5 empty] | 총 합 | #REF! | #REF!
|  |  | 5층 | IDC | DEKR IDC | #REF!
|  |  | 6층 | IDC | DEKR IDC | #REF!
|  |  | 7층 | IDC | DEKR IDC | #REF! | #REF!
|  |  |  | IP | 세종 인터넷 | #REF! | #REF! | [5 empty] | 구 분 |  |  |  | 8월 |  |  | 9월 |  |  | 사용량 |  |  |  |  | 전류 |  | 점유율
|  |  |  | 전송 | 세종 전송설비 | #REF! | #REF! | [5 empty] | 8F 전체 전력지침 |  |  |  | 1701.4 |  |  | 3194 |  |  | 1492.6 |  |  |  |  | 9.119
|  |  |  | 전송 | 세종 정류기 | #REF! | #REF! | [5 empty] | DEK 사용량 | [9 empty] | 1163.9 |  |  |  |  | 7.1108 |  | 77.98%
|  |  |  | 전송/인터넷 | 세종 7층 NOC(미확인 포함) | #REF! | #REF! | [5 empty] | SJT 모니터 |  |  |  | 0.1 |  |  | 0.1 |  |  | 0 |  |  | 328.7 |  | 2.0082 |  | 22.02%
|  |  |  | 8F Office | SJT | #REF! | #REF! | [5 empty] | SJT Office |  |  |  | 193.2 |  |  | 320.4 |  |  | 127.2
[5 empty] | DEKR IDC | #REF! | #REF! | [5 empty] | SJT Server |  |  |  | 364.1 |  |  | 565.6 |  |  | 201.5
[5 empty] | 총 합 | #REF! | #REF!
#REF!
#REF!
#REF!

## SJT설비_7층_IPD (hidden)
IPD 운용현황(' 22 년 월 일)
|  | 201 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/A-1
| 번호 | BAY_부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | BAY_부하명 | 번호
| 1 | 203A | O | X |  |  |  |  | O | X | NTT RACK 1 | 41
| 2 | DTX-360(A) | O | X |  |  |  |  | O | X | NTT RACK 2 | 42
| 3 |  | X | X |  |  |  | 35A | O | O | IPD / A-1_P43 406BAY PDP_A /405bay표기 | 43
| 4 | Clarent 1 | O | X |  |  |  | 35A | O | O | IPD / A-1_P44 407BAY PDP_A /406bay표기 | 44
| 5 | LG 교환기 | O | X |  |  |  |  | O | X | C-A | 45
| 6 | DTX240 #1 (503BAY / A) | O | X |  |  |  |  | O | X | 언리미텔 | 46 | 2021.01.19 탈거
| 7 | IPD / A-1_P07 306BAY PDP-A | O | O | 100A |  |  |  | O | X | EXL 1-B | 47
| 8 |  | X | X |  |  |  |  | O | X | EXL 2-B | 48
| 9 |  | X | X |  |  |  |  | O | X | EXL 3-A | 49
| 10 | 502BAY A, DTX-6000 | O | X |  |  |  | 35A | O | O | IPD / A-1_P50 G-7 랙 PDP_A / NTT-4A표기 | 50 | 미사용, 전원OFF 상태
| 11 | IPD / A-1_P11 506BAY PDP-A | O | O | 35A |  |  | 35A | O | O | IPD / A-1_P51 F-1 랙 PDP_A | 51
| 12 | 204A 교환기 | O | X |  |  |  |  | O | X | F-2랙 (201A-NTT#9-PDU상) | 52 | 2021.01.19 탈거
| 13 |  | X | X |  |  |  |  | X | X |  | 53
| 14 |  | X | X |  |  |  |  | X | X |  | 54
| 15 | IPD / A-1_P15 506BAY PDP_A(2) /509B 3PDA표기 | O | O | 35A |  |  |  | X | X |  | 55
| 16 | IPD / A-1_P16 504BAY PDP_B | O | O | 35A |  |  | 50A | O | O | IPD / A-1_P56 502BAY PDP_A | 56
| 17 | IPD / A-1_P17 503BAY PDP_A | O | O | 50A |  |  | 50A | O | O | IPD / A-1_P57 305BAY PDP_A | 57
| 18 | IPD / A-1_P18 303BAY PDP_A | O | O | 100A |  |  |  | X | X |  | 58
| 19 | IPD / A-1_P19 501BAY PDP_A | O | O | 100A |  |  |  | X | X |  | 59
| 20 | IPD / A-1_P20 507BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 60
| 21 | IPD / A-1_P21 304BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 61
| 22 |  | X | X |  |  |  |  | X | X |  | 62
| 23 | 302Bay, SKB-A ('21.09.13) | O | O | 100A |  |  |  | X | X |  | 63
| 24 | 307BAY_LGU+PDP.A 201BAY_PDR_P24 | O | O | 100A |  |  |  | X | X |  | 64
| 25 |  | X | X |  |  |  |  | X | X |  | 65
| 26 |  | X | X |  |  |  |  | X | X |  | 66
| 27 |  | X | X |  |  |  |  | X | X |  | 67
| 28 |  | X | X |  |  |  |  | X | X |  | 68
| 29 |  | X | X |  |  |  |  | X | X |  | 69
| 30 |  | X | X |  |  |  |  | X | X |  | 70
| 31 |  | X | X |  |  |  |  | X | X |  | 71
| 32 |  | X | X |  |  |  |  | X | X |  | 72
| 33 |  | X | X |  |  |  |  | X | X |  | 73
| 34 |  | X | X |  |  |  |  | X | X |  | 74
| 35 |  | X | X |  |  |  |  | X | X |  | 75
| 36 |  | X | X |  |  |  |  | X | X |  | 76
| 37 |  | X | X |  |  |  |  | X | X |  | 77
| 38 |  | X | X |  |  |  |  | X | X |  | 78
| 39 |  | X | X |  |  |  |  | X | X |  | 79
| 40 |  | X | X |  |  |  |  | X | X |  | 80
[7 empty] | 합계: | 0
|  | 401 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/B-1
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
| 1 |  | X | X |  |  |  | 100A | O | O | IPD / B-1_P41 C-1 랙 장비_B | 41
| 2 | DTX-360(B) | O | X |  |  |  |  | X | X |  | 42
| 3 |  | X | X |  |  |  |  | O | X | C-B | 43
| 4 | Crlarent 1 | O | X |  |  |  |  | O | X | EXL 1-A | 44
| 5 | IPD / B-1_P05 406BAY PDP_B /403bay dcn-1b표기 | O | O | 35A |  |  |  | O | X | EXL 2-A | 45
| 6 | IPD / B-1_P06 407BAY PDP_B / 406bay dcn-2b표기 | O | O | 35A |  |  |  | O | X | EXL 3-B | 46
| 7 | IPD / B-1_P07 306BAY PDP_B | O | O | 100A |  |  | 50A | O | O | IPD / B-1_P47 G-7 랙 PDP_B | 47 | 미사용, 전원OFF
| 8 | 503 BAY/B DTX-240#2 | O | X |  |  |  |  | X | X |  | 48
| 9 | N-DCS#1 | O | X |  |  |  |  | X | X |  | 49
| 10 | N-DCS#2 | O | X |  |  |  |  | X | X |  | 50
| 11 | N-DCS#3 | O | X |  |  |  | 35A | O | O | IPD / B-1_P51 F-1 랙 PDP_B | 51
| 12 | 502BAY B DTX-6000 | O | X |  |  |  |  | X | X | F-2랙 (401B-NTT#9-PDU하) | 52 | 2021.01.19 탈거
랙 철거 예정 | 13 | IPD / B-1_P13 505BAY PDP_A(단일) | O | X |  |  |  |  | X | X | 401B-NTT#1-PDU하 | 53
| 14 | IPD / B-1_P14 506BAY PDP_B | O | O | 35A |  |  |  | X | X | 401B-NTT#1-PDU상 | 54
| 15 | IPD / B-1_P15 506BAY PDP_B(2) /509b 3pdp b표기 | O | O | 35A |  |  |  | X | X | NTT-2B(20.6.16철거) | 55
| 16 | IPD / B-1_P16 504BAY PDP_A | O | O | 35A |  |  | 50A | O | O | IPD / B-1_P56 502BAY PDP_B | 56
| 17 | IPD / B-1_P17 503BAY PDP_B | O | O | 50A |  |  | 50A | O | O | IPD / B-1_P57 305BAY PDP_B | 57
| 18 | IPD / B-1_P18 303BAY PDP_B | O | O | 100A |  |  |  | X | X |  | 58
| 19 | IPD / B-1_P19 501BAY PDP_B | O | O | 100A |  |  |  | X | X |  | 59
| 20 | IPD / B-1_P20 507BAY PDP_B | O | O | 50A |  |  |  | X | X |  | 60
| 21 | IPD / B-1_P21 304BAY PDP_B | O | O | 50A |  |  |  | X | X |  | 61
| 22 |  | X | X | X |  |  |  | X | X |  | 62
| 23 | 302Bay, SKB-B ('21.09.13) | O | O | 100A |  |  |  | X | X |  | 63
| 24 | 307BAY_LGU+PDP.B 401BAY_PDR_P24 | O | O | 100A |  |  |  | X | X |  | 64
| 25 |  | X | X |  |  |  |  | X | X |  | 65
| 26 |  | X | X |  |  |  |  | X | X |  | 66
| 27 |  | X | X |  |  |  |  | X | X |  | 67
| 28 |  | X | X |  |  |  |  | X | X |  | 68
| 29 |  | X | X |  |  |  |  | X | X |  | 69
| 30 |  | X | X |  |  |  |  | X | X |  | 70
| 31 |  | X | X |  |  |  |  | X | X |  | 71
| 32 |  | X | X |  |  |  |  | X | X |  | 72
| 33 |  | X | X |  |  |  |  | X | X |  | 73
| 34 |  | X | X |  |  |  |  | X | X |  | 74
| 35 |  | X | X |  |  |  |  | X | X |  | 75
| 36 |  | X | X |  |  |  |  | X | X |  | 76
| 37 |  | X | X |  |  |  |  | X | X |  | 77
| 38 |  | X | X |  |  |  |  | X | X |  | 78
| 39 |  | X | X |  |  |  |  | X | X |  | 79
| 40 |  | X | X |  |  |  |  | X | X |  | 80
[7 empty] | 합계: | 0
|  | 211 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/A-2
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
| 1 |  | X | X |  |  |  |  | X | X |  | 41
20210204 FUSE 제거 | 2 | 311BAY FLC-P_A | X | X |  |  |  |  | X | X |  | 42 | 20210120 Fuse 제거
| 3 | 413BAY PDP_1A | X | X |  |  |  |  | X | X |  | 43
| 4 | 413BAY PDP_2A | X | X |  |  |  | 16A | O | O | IPD / A-2_P44 518BAY PDP_A | 44
| 5 | 511BAY(KT SMOT4_A) | X | X |  |  |  |  | X | X |  | 45
20210204 FUSE 제거 | 6 | 312BAY FLC-P_A | X | X |  |  |  |  | X | X |  | 46
| 7 | IPD / A-2_P07 513BAY PDP_A | O | O | 50A |  |  | 35A | O | O | IPD / A-2_P47 519BAY PDP_A | 47
20210204 FUSE 제거 | 8 |  | X | X |  |  |  | 50A | O | O | IPD / A-2_P48 520BAY 장비_A | 48
20210204 FUSE 제거 | 9 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P49 418BAY PDP_A | 49
| 10 | IPD / A-2_P10 414BAY PDP_A | O | O | 35A |  |  |  | X | X |  | 50
20210204 FUSE 제거 | 11 |  | X | X |  |  |  |  | X | X |  | 51 | 20201028 랙 철거
| 12 | IPD / A-2_P12 212BAY PDP_A | O | O | 50A |  |  | 35A | O | O | IPD / A-2_P52 419BAY PDP_A | 52
| 13 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P53 519BAY PDP_A(2) / CWDM-A표기 | 53
20210204 FUSE 제거 | 14 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P54 112BAY PDP_A | 54
20210224 FUSE 제거 | 15 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P55 113BAY PDP_A | 55
| 16 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P56 114BAY PDP_A | 56
| 17 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P57 111BAY PDP_A | 57
| 18 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P58 517BAY PDP_A | 58
20210204 FUSE 제거 | 19 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P59 115BAY PDP_A | 59
20210204 FUSE 제거 | 20 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P60 117BAY PDP_A | 60
20210224 FUSE 제거 | 21 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P61 116BAY PDP_A | 61
| 22 | IPD / A-2_P22 219BAY PDP_A | O | O | 50A |  |  | 35A | O | O | IPD / A-2_P62 511BAY PDP_A | 62
| 23 | IPD / A-2_P23 514BAY PDP_ A | O | O | 50A |  |  | 35A | O | O | IPD / A-2_P63 511BAY 장비_A | 63
| 24 |  | X | X |  |  |  | 50A | O | O | IPD / A-2_P64 118BAY PDP_A | 64
| 25 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P65 119BAY PDP_A | 65
| 26 |  | X | X |  |  |  | 50A | O | O | IPD / A-2_P66 121BAY PDP_A | 66
| 27 |  | X | X |  |  |  | 50A | O | O | IPD / A-2_P67 120BAY PDP_A | 67
| 28 |  | X | X |  |  |  |  | X | X |  | 68
| 29 |  | X | X |  |  |  |  | X | X |  | 69
| 30 |  | X | X |  |  |  |  | X | X |  | 70
| 31 |  | X | X |  |  |  |  | X | X |  | 71
| 32 |  | X | X |  |  |  |  | X | X |  | 72
| 33 |  | X | X |  |  |  |  | X | X |  | 73
| 34 |  | X | X |  |  |  |  | X | X |  | 74
| 35 |  | X | X |  |  |  |  | X | X |  | 75
| 36 |  | X | X |  |  |  |  | X | X |  | 76
| 37 |  | X | X |  |  |  |  | X | X |  | 77
| 38 |  | X | X |  |  |  |  | X | X |  | 78
| 39 |  | X | X |  |  |  |  | X | X |  | 79
| 40 |  | X | X |  |  |  |  | X | X |  | 80
[7 empty] | 합계: | 0
|  | 411 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/B-2
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
20210204 FUSE 제거 | 1 |  | X | X |  |  |  |  | X | X |  | 41
| 2 |  | X | X |  |  |  |  | X | X |  | 42 | 20210120 FUSE 제거
| 3 |  | X | X |  |  |  |  | X | X |  | 43
| 4 |  | X | X |  |  |  |  | X | X |  | 44
20210204 FUSE 제거 | 5 |  | X | X |  |  |  |  | X | X |  | 45
| 6 |  | X | X |  |  |  | 16A | O | O | IPD / B-2_P46 518BAY PDP_B | 46
| 7 | IPD / B-2_P07 513BAY PDP_B | O | O | 50A |  |  | 35A | O | O | IPD / B-2_P47 519BAY PDP_B | 47
20210204 FUSE 제거 | 8 |  | X | X |  |  |  | 50A | O | O | IPD / B-2_P48 520BAY 장비_B | 48
20210204 FUSE 제거 | 9 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P49 418BAY PDP_B | 49
| 10 | IPD / B-2_P10 414BAY PDP_B | O | O | 35A |  |  |  | X | X |  | 50
20210204 FUSE 제거 | 11 |  | X | X |  |  |  |  | X | X |  | 51 | 랙철거 20201028
| 12 | IPD / B-2_P12 212BAY PDP_B | O | O | 50A |  |  | 35A | O | O | IPD / B-2_P52 419BAY PDP_B | 52
| 13 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P53 519BAY PDP_B(2) / CWDM-B표기 | 53
20210204 FUSE 제거 | 14 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P54 112BAY PDP_B | 54
20210224 FUSE 제거 | 15 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P55 113BAY PDP_B | 55
| 16 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P56 114BAY PDP_B | 56
| 17 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P57 111BAY PDP_B | 57
| 18 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P58 517BAY PDP_B | 58
20210204 FUSE 제거 | 19 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P59 115BAY PDP_B | 59
20210204 FUSE 제거 | 20 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P60 117BAY PDP_B | 60
20210224 FUSE 제거 | 21 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P61 116BAY PDP_B | 61
| 22 | IPD / B-2_P22 219BAY PDP_B | O | O | 50A |  |  | 35A | O | O | IPD / B-2_P62 511BAY PDP_B | 62
| 23 | IPD / B-2_P23 514BAY PDP_B | O | O | 50A |  |  | 35A | O | O | IPD / B-2_P63 511BAY 장비_B | 63
| 24 |  | X | X |  |  |  | 50A | O | O | IPD / B-2_P64 118BAY PDP_B | 64
| 25 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P65 119BAY PDP_B | 65
| 26 |  | X | X |  |  |  | 50A | O | O | IPD / B-2_P66 121BAY PDP_B | 66
| 27 |  | X | X |  |  |  | 50A | O | O | IPD / B-2_P67 120BAY PDP_B | 67
| 28 |  | X | X |  |  |  |  | X | X |  | 68
| 29 |  | X | X |  |  |  |  | X | X |  | 69
| 30 |  | X | X |  |  |  |  | X | X |  | 70
| 31 |  | X | X |  |  |  |  | X | X |  | 71
| 32 |  | X | X |  |  |  |  | X | X |  | 72
| 33 |  | X | X |  |  |  |  | X | X |  | 73
| 34 |  | X | X |  |  |  |  | X | X |  | 74
| 35 |  | X | X |  |  |  |  | X | X |  | 75
| 36 |  | X | X |  |  |  |  | X | X |  | 76
| 37 |  | X | X |  |  |  |  | X | X |  | 77
| 38 |  | X | X |  |  |  |  | X | X |  | 78
| 39 |  | X | X |  |  |  |  | X | X |  | 79
| 40 |  | X | X |  |  |  |  | X | X |  | 80
[7 empty] | 합계: | 0
|  | 222 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/A-3
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
| 1 | IPD / A-3_P01 426BAY PDP_A-1 | O | O | 100A |  |  | 50A | O | O | IPD / A-3_P41 527BAY PDP_A | 41
| 2 | IPD / A-3_P02 426BAY PDP_A-2 | O | O | 100A |  |  | 50A | O | O | IPD / A-3_P42 425BAY PDP_A-1 | 42
| 3 | IPD / A-3_P03 426BAY PDP_A-3 | O | O | 50A |  |  | 50A | O | O | IPD / A-3_P43 425BAY PDP_A-2 | 43
| 4 | 427BAY-A | O | X |  |  |  | 50A | O | O | IPD / A-3_P44 530BAY PDP_A | 44
| 5 | IPD / A-3_P05 523BAY PDP_A | O | O | 50A |  |  |  | O | X | LT 2.5G 531BAY A | 45
| 6 | IPD / A-3_P06 524BAY PDP_A | O | O | 50A |  |  | 50A | O | O | IPD / A-3_P46 531BAY PDP_A | 46
| 7 | IPD / A-3_P07 525BAY PDP_A | O | O | 50A |  |  | 50A | O | O | IPD / A-3_P47 532BAY PDP_A | 47
| 8 | 428BAY-A | O | X |  |  |  |  | O | X | LT 2.5G 534BAY A | 48
| 9 | 429BAY-A | O | X |  |  |  | 50A | O | O | IPD / A-3_P49 228BAY PDP_A | 49
| 10 | IPD / A-3_P10 526BAY PDP_A | O | O | 50A |  |  | 35A | O | O | IPD / A-3_P50 229BAY PDP_A | 50
| 11 | 430BAY-A | O | X |  |  |  | 35A | O | O | IPD / A-3_P51 230BAY PDP_A | 51
| 12 | 431BAY-A | O | X |  |  |  | 35A | O | O | IPD / A-3_P52 225BAY PDP_A | 52
| 13 | 331BAY-A | O | X |  |  |  | 35A | O | O | IPD / A-3_P53 420BAY PDP_A | 53
| 14 | 330BAY-A | O | X |  |  |  |  | X | X |  | 54
| 15 | IPD / A-3_P15 329BAY PDP_A | O | O | 50A |  |  | 35A | O | O | IPD / A-3_P55 225BAY PDP_A(2) | 55
| 16 | IPD / A-3_P16 328BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 56
| 17 | IPD / A-3_P17 327BAY PDP_A | O | O | 50A |  |  | 50A | O | O | IPD / A-3_P57 427BAY PDP_A-1 | 57
| 18 | IPD / A-3_P18 223BAY PDP_A | O | O | 35A |  |  | 50A | O | O | IPD / A-3_P58 427BAY PDP_A-2 | 58
| 19 | IPD / A-3_P19 224BAY PDP_A | O | O | 35A |  |  | 100A | O | O | IPD / A-3_P59 305BAY PDP_A | 59
| 20 | IPD / A-3_P20 226BAY PDP_A | O | O | 35A |  |  | 100A | O | O | 331BAY_코위버ROADM(A) 222BAY_P60 | 60
| 21 | IPD / A-3_P21 227BAY PDP_A | O | O | 50A |  |  | 100A | O | O | 323B ODO -48VA 코위버 갬으 DURTKA#2 | 61
| 22 | IPD / A-3_P22 231BAY PDP_A | O | O | 35A |  |  |  | X | X |  | 62
| 23 | IPD / A-3_P23 326BAY PDP_A | O | O | 35A |  |  |  | X | X |  | 63
| 24 |  | X | X |  |  |  |  | X | X |  | 64
| 25 | IPD / A-3_P25 319BAY PDP_A | O | O | 35A |  |  |  | X | X |  | 65
| 26 | IPD / A-3_P26 423BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 66
| 27 | IPD / A-3_P27 424BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 67
| 28 | 330BAY_코위버ROADM(A) 222BAY_P28 | O | O | 100A |  |  |  | X | X |  | 68
| 29 |  | X | X |  |  |  |  | X | X |  | 69
| 30 |  | X | X |  |  |  |  | X | X |  | 70
| 31 |  | X | X |  |  |  |  | X | X |  | 71
| 32 |  | X | X |  |  |  |  | X | X |  | 72
| 33 |  | X | X |  |  |  |  | X | X |  | 73
| 34 |  | X | X |  |  |  |  | X | X |  | 74
| 35 |  | X | X |  |  |  |  | X | X |  | 75
| 36 |  | X | X |  |  |  |  | X | X |  | 76
| 37 |  | X | X |  |  |  |  | X | X |  | 77
| 38 |  | X | X |  |  |  |  | X | X |  | 78
| 39 |  | X | X |  |  |  |  | X | X |  | 79
| 40 |  | X | X |  |  |  |  | X | X |  | 80
[7 empty] | 합계: | 0
|  | 422 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/B-3
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
| 1 | IPD / B-3_P01 426BAY PDP_B-1 | O | O | 100A |  |  | 50A | O | O | IPD / B-3_P41 527BAY PDP_B | 41
| 2 | IPD / B-3_P02 426BAY PDP_B-2 | O | O | 100A |  |  | 50A | O | O | IPD / B-3_P42 425BAY PDP_B-1 | 42
| 3 | IPD / B-3_P03 426BAY PDP_B-3 | O | O | 50A |  |  | 50A | O | O | IPD / B-3_P43 425BAY PDP_B-2 | 43
| 4 | 427 BAY-B NT2.5G 3B 3BAY | O | X |  |  |  | 50A | O | O | IPD / B-3_P44 530BAY PDP_B | 44
| 5 | IPD / B-3_P05 523BAY PDP_B | O | O | 50A |  |  |  | O | X | LT 2.5G 531BAY B | 45
| 6 | IPD / B-3_P06 524BAY PDP_B | O | O | 50A |  |  | 50A | O | O | IPD / B-3_P46 531BAY PDP_B | 46
| 7 | IPD / B-3_P07 525BAY PDP_B | O | O | 50A |  |  | 50A | O | O | IPD / B-3_P47 532BAY PDP_B | 47
| 8 | 428BAY-B NT2.5 4 BAY B | O | X |  |  |  |  | O | X | LT 2.5G 534BAY B | 48
| 9 | 429BAY-B NT2.5 5 BAY B | O | X |  |  |  | 35A | O | O | IPD / B-3_P49 228BAY PDP_B | 49
| 10 | IPD / B-3_P10 526BAY PDP_B | O | O | 50A |  |  | 35A | O | O | IPD / B-3_P50 229BAY PDP_B | 50
| 11 | 430BAY-B 525BAY B | O | X |  |  |  | 35A | O | O | IPD / B-3_P51 230BAY PDP_B | 51
| 12 | 431BAY-B NT2.5G B 430 BAY | O | X |  |  |  | 35A | O | O | IPD / B-3_P52 420BAY PDP_B | 52
| 13 | 331 BAY-B NT2.5G 330BAY B | O | X |  |  |  |  | X | X |  | 53
| 14 | 330 BAY NT2.5G 329BAY B | O | X |  |  |  | 35A | O | O | IPD / B-3_P54 225BAY PDP_B(2) | 54
| 15 | IPD / B-3_P15 329BAY PDP_B | O | O | 50A |  |  |  | X | X |  | 55
| 16 | IPD / B-3_P16 328BAYPDP_B | O | O | 50A |  |  |  | X | X |  | 56
| 17 | IPD / B-3_P17 327BAY PDP_B | O | O | 50A |  |  | 50A | O | O | IPD / B-3_P57 427BAY PDP_B-1 | 57
| 18 | IPD / B-3_P18 223BAY PDP_B | O | O | 50A |  |  | 50A | O | O | IPD / B-3_P58 427BAY PDP_B-2 | 58
| 19 | IPD / B-3_P19 224BAY PDP_B | O | O | 50A |  |  | 100A | O | O | IPD / B-3_P59 305BAY PDP_B | 59
| 20 | IPD / B-3_P20 226BAY PDP_B | O | O | 50A |  |  | 100A | O | O | 331BAY_코위버ROADM(B) 422BAY_P60 | 60
| 21 | IPD / B-3_P21 227BAY PDP_B | O | O | 50A |  |  | 100A | O | O | 323B ODO -48VB 코위버 갬으 DURTKA#2 | 61
| 22 | IPD / B-3_P22 231BAY PDP_B | O | O | 35A |  |  |  | X | X |  | 62
| 23 | IPD / B-3_P23 225BAY PDP_B | O | O | 35A |  |  |  | X | X |  | 63
| 24 | IPD / B-3_P24 326BAY PDP_B | O | O | 35A |  |  |  | X | X |  | 64
| 25 | IPD / B-3_P25 319BAY PDP_B | O | O | 35A |  |  |  | X | X |  | 65
| 26 | IPD / B-3_P26 423BAY PDP_B | O | O | 50A |  |  |  | X | X |  | 66
| 27 | IPD / B-3_P27 424BAY PDP_B | O | O | 50A |  |  |  | X | X |  | 67
| 28 | 330BAY_코위버ROADM(B) 422BAY_P28 | O | O | 100A |  |  |  | X | X |  | 68
| 29 |  | X | X |  |  |  |  | X | X |  | 69
| 30 |  | X | X |  |  |  |  | X | X |  | 70
| 31 |  | X | X |  |  |  |  | X | X |  | 71
| 32 |  | X | X |  |  |  |  | X | X |  | 72
| 33 |  | X | X |  |  |  |  | X | X |  | 73
| 34 |  | X | X |  |  |  |  | X | X |  | 74
| 35 |  | X | X |  |  |  |  | X | X |  | 75
| 36 |  | X | X |  |  |  |  | X | X |  | 76
| 37 |  | X | X |  |  |  |  | X | X |  | 77
| 38 |  | X | X |  |  |  |  | X | X |  | 78
| 39 |  | X | X |  |  |  |  | X | X |  | 79
| 40 |  | X | X |  |  |  |  | X | X |  | 80
[7 empty] | 합계: | 0
|  | 235 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/A-4
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
| 1 |  | X | X |  |  |  | 50 | O | O | IPD / A-4_P41 343BAY PDP_A / 에르고DWDM-1A | 41 | 미사용
| 2 |  | X | X |  |  |  | 35 | O | O | IPD / A-4_P42 339BAY PDP_B | 42
| 3 | IPD / A-4_P03 436BAY PDP_A | O | O | 100A |  |  | 35 | O | O | IPD / A-4_P43 338BAY PDP_A | 43
| 4 |  | X | X |  |  |  | 35 | O | O | IPD / A-4_P44 337AY PDP_A | 44
| 5 |  | X | X |  |  |  | 50 | O | O | IPD / A-4_P45 238AY PDP_A | 45
| 6 |  | X | X |  |  |  | 50 | O | O | IPD / A-4_P46 335AY PDP_A | 46
| 7 |  | X | X |  |  |  |  | X | X |  | 47
| 8 |  | X | X |  |  |  |  | X | X |  | 48
| 9 |  | X | X |  |  |  |  | X | X |  | 49
| 10 | IPD / A-4_P10 239BAY PDP_A-1 | O | O | 50A |  |  | 35 | O | O | IPD / A-4_P50 336AY PDP_A | 50
| 11 | IPD / A-4_P11 239BAY PDP_A-2 | O | O | 50A |  |  |  | X | X |  | 51
| 12 |  | X | X |  |  |  | 35 | O | O | IPD / A-4_P52 237AY PDP_A | 52
| 13 |  | X | X |  |  |  | 35 | O | O | IPD / A-4_P53 236AY PDP_A | 53
| 14 |  | X | X |  |  |  | 35 | O | O | IPD / A-4_P54 334AY PDP_A | 54
| 15 |  | X | X |  |  |  |  | X | X |  | 55
| 16 |  | X | X |  |  |  | 100 | O | O | IPD / A-4_P56 537BAY PDP_A | 56
| 17 |  | X | X |  |  |  |  | X | X |  | 57
| 18 | IPD / A-4_P18 239BAY PDP_A-3 | O | O | 50A |  |  | 100 | O | O | IPD / A-4_P58 538BAY PDP_A | 58
| 19 |  | X | X |  |  |  | 50 | O | O | IPD / A-4_P59 536BAY PDP_A | 59
| 20 |  | X | X |  |  |  |  | X | X |  | 60
| 21 |  | X | X |  |  |  |  | X | X |  | 61
| 22 |  | X | X |  |  |  |  | X | X |  | 62
| 23 |  | X | X |  |  |  |  | X | X |  | 63
| 24 |  | X | X |  |  |  |  | X | X |  | 64
| 25 | IPD / A-4_P25 235Bay-노키아1830_PSS8-A전원 | O | O | 50A |  |  |  | X | X |  | 65
| 26 | IPD / A-4_P26 244BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 66
| 27 | IPD / A-4_P27 240BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 67
| 28 | IPD / A-4_P28 243BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 68
| 29 | IPD / A-4_P29 437BAY PDP_A | O | O | 100A |  |  |  | X | X |  | 69
| 30 | IPD / A-4_P30 439BAY PDP_B | O | O | 100A |  |  |  | X | X |  | 70
| 31 | IPD / A-4_P31 440BAY PDP_B | O | O | 100A |  |  |  | X | X |  | 71
FUSE 제거(21.02.03) | 32 | IPD / A-4_P32 TEST BED PDP_A | O | O | 35A |  |  |  | X | X |  | 72
| 33 | IPD / A-4_P33 240BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 73
| 34 | IPD/A-4_P34 437BAY(下) PDP_A-2 | O | O | 35A |  |  |  | X | X |  | 74
| 35 |  | X | X |  |  |  |  | X | X |  | 75
| 36 |  | X | X |  |  |  |  | X | X |  | 76
| 37 |  | X | X |  |  |  |  | X | X |  | 77
| 38 |  | X | X |  |  |  |  | X | X |  | 78
| 39 |  | X | X |  |  |  |  | X | X |  | 79
| 40 |  | X | X |  |  |  |  | X | X |  | 80
[7 empty] | 합계: | 0
|  | 435 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/B-4
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
| 1 |  | X | X |  |  |  | 50A | O | O | IPD / B-4_P41 343BAY PDP_B / 에르고 DWDM 1B표기 | 41 | 미사용
| 2 |  | X | X |  |  |  |  | X | X |  | 42
| 3 | IPD / B-4_P03 436BAY PDP_B | O | O | 100A |  |  | 50A | O | O | IPD / B-4_P43 239BAY PDP_B-1 | 43
| 4 |  | X | X |  |  |  | 50A | O | O | IPD / B-4_P44 239BAY PDP_B-2 | 44
| 5 |  | X | X |  |  |  | 50A | O | O | IPD / B-4_P45 239BAY PDP_B-3 | 45
| 6 |  | X | X |  |  |  | 35A | O | O | IPD / B-4_P46 339BAY PDP_A | 46
| 7 |  | X | X |  |  |  | 50A | O | O | IPD / B-4_P47 338BAY PDP_B | 47
| 8 |  | X | X |  |  |  | 35A | O | O | IPD / B-4_P48 337AY PDP_B | 48
| 9 |  | X | X |  |  |  | 50A | O | O | IPD / B-4_P49 335AY PDP_B | 49
| 10 |  | X | X |  |  |  | 35A | O | O | IPD / B-4_P50 336AY PDP_B | 50
| 11 |  | X | X |  |  |  | 50A | O | O | IPD / B-4_P51 238BAY PDP_B | 51
| 12 |  | X | X |  |  |  | 35A | O | O | IPD / B-4_P52 237AY PDP_B | 52
| 13 |  | X | X |  |  |  | 35A | O | O | IPD / B-4_P53 236AY PDP_B | 53
| 14 |  | X | X |  |  |  | 35A | O | O | IPD / B-4_P54 334AY PDP_B | 54
| 15 |  | X | X |  |  |  |  | X | X |  | 55
| 16 |  | X | X |  |  |  | 35A | O | O | IPD / B-4_P56 537BAY PDP_B | 56
| 17 |  | X | X |  |  |  | 50A | O | O | IPD / B-4_P57 240BAY PDP_B | 57
| 18 |  | X | X |  |  |  | 100A | O | O | IPD / B-4_P58 538BAY PDP_B | 58
| 19 |  | X | X |  |  |  | 50A | O | O | IPD / B-4_P59 536BAY PDP_B | 59
| 20 |  | X | X |  |  |  |  | X | X |  | 60
| 21 |  | X | X |  |  |  |  | X | X |  | 61
| 22 |  | X | X |  |  |  |  | X | X |  | 62
| 23 |  | X | X |  |  |  |  | X | X |  | 63
| 24 |  | X | X |  |  |  |  | X | X |  | 64
| 25 | 235Bay, 노키아1830_PSS8-B전원('21.09.14 투입) | O | O | 50A |  |  |  | X | X |  | 65
| 26 | IPD / B-4_P26 244BAY PDP_B | O | O | 50A |  |  |  | X | X |  | 66
| 27 |  | X | X |  |  |  |  | X | X |  | 67
| 28 | IPD / B-4_P28 243BAY PDP_B | O | O | 50A |  |  |  | X | X |  | 68
| 29 | IPD / B-4_P29 437BAY PDP_B | O | O | 100A |  |  |  | X | X |  | 69
| 30 | IPD / B-4_P30 439BAY PDP_A | O | O | 100A |  |  |  | X | X |  | 70
| 31 | IPD / B-4_P31 440BAY PDP_A | O | O | 100A |  |  |  | X | X |  | 71
FUSE 제거(21.02.03) | 32 | IPD / B-4_P32 TEST BED PDP_B | O | O | 35A |  |  |  | X | X |  | 72
| 33 | IPD / B-4_P33 240BAY PDP_B | O | O | 50A |  |  |  | X | X |  | 73
| 34 | IPD/B-4_P34 437BAY(下) PDP_B-2 | ○ | ○ | 35A |  |  |  | X | X |  | 74
| 35 |  | X | X |  |  |  |  | X | X |  | 75
| 36 |  | X | X |  |  |  |  | X | X |  | 76
| 37 |  | X | X |  |  |  |  | X | X |  | 77
| 38 |  | X | X |  |  |  |  | X | X |  | 78
| 39 |  | X | X |  |  |  |  | X | X |  | 79
| 40 |  | X | X |  |  |  |  | X | X |  | 80
[7 empty] | 합계: | 0
|  | A-A1 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/A-5 (구 IPD-B)
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
| F1 |  | X | X | X |  |  | 35A | X | X |  | F61
| F2 |  | X | X | X |  |  | 35A | X | X |  | F62
| F3 |  | X | X | X |  |  | 35A | X | X |  | F63
| F4 |  | X | X | X |  |  | 35A | X | X |  | F64
| F5 |  | X | X | X |  |  | 35A | X | X |  | F65
| F6 |  | X | X | X |  |  | 35A | X | X |  | F66
| F7 |  | X | X | X |  |  | 35A | X | X |  | F67
| F8 |  | X | X | X |  |  | 35A | X | X |  | F68
| F9 |  | X | X | X |  |  | 35A | X | X |  | F69
| F10 |  | X | X | X |  |  | 35A | X | X |  | F70
| F11 |  | X | X | X |  |  | 35A | X | X |  | F71
| F12 |  | X | X | X |  |  | 35A | X | X |  | F72
| F13 |  | X | X | X |  |  | 35A | X | X |  | F73
| F14 |  | X | X | X |  |  | 35A | X | X |  | F74
| F15 |  | X | X | X |  |  | 35A | X | X |  | F75
| F16 |  | X | X | X |  |  | 35A | X | X |  | F76
| F17 |  | X | X | X |  |  | 35A | X | X |  | F77
| F18 |  | X | X | X |  |  | 35A | X | X |  | F78
| F19 |  | X | X | X |  |  | 35A | X | X |  | F79
| F20 |  | X | X | X |  |  | 35A | X | X |  | F80
| F21 |  | X | X | X |  |  | X | X | X |  | F81
| F22 |  | X | X | X |  |  | X | X | X |  | F82
| F23 |  | X | X | X |  |  | X | X | X |  | F83
| F24 |  | X | X | X |  |  | X | X | X |  | F84
| F25 |  | X | X | X |  |  | X | X | X |  | F85
| F26 |  | X | X | X |  |  | X | X | X |  | F86
| F27 |  | X | X | X |  |  | X | X | X |  | F87
| F28 |  | X | X | X |  |  | 35A | X | X |  | F88
| F29 |  | X | X | X |  |  | 35A | X | X |  | F89
| F30 |  | X | X | X |  |  | 35A | X | X |  | F90
| F31 |  | X | X | X |  |  | 35A | X | X |  | F91
| F32 |  | X | X | X |  |  | 35A | X | X |  | F92
| F33 |  | X | X | X |  |  | 35A | X | X |  | F93
| F34 |  | X | X | X |  |  | 35A | X | X |  | F94
| F35 |  | X | X | X |  |  | 35A | X | X |  | F95
| F36 |  | X | X | X |  |  | 35A | X | X |  | F96
| F37 |  | X | X | X |  |  | 35A | X | X |  | F97
| F38 |  | X | X | X |  |  | 35A | X | X |  | F98
| F39 |  | X | X | X |  |  | 35A | X | X |  | F99
| F40 |  | X | X | X |  |  | 35A | X | X |  | F100
| F41 | IPD / A-5_P41 F-8 랙 PDP_B off 상태 | O | O | 35A |  |  | 35A | X | X |  | F101
| F42 | IPD / A-5_P42 A-5 랙 장비_B(1) | O | O | 35A |  |  | 35A | X | X |  | F102
| F43 | IPD / A-5_P43 A-5 랙 장비_B(2) | O | O | 35A |  |  | 35A | X | X |  | F103
| F44 | D3-B | O | X | X |  |  | 35A | X | X |  | F104
| F45 | C-8-B | O | X | X |  |  | 35A | X | X |  | F105
| F46 | C-7-B | O | X | X |  |  | 35A | X | X |  | F106
| F47 |  | X | X | X |  |  | 35A | X | X |  | F107
| F48 |  | X | X | X |  |  | 35A | X | X |  | F108
| F49 |  | X | X | X |  |  | 35A | X | X |  | F109
| F50 |  | X | X | X |  |  | 35A | X | X |  | F110
| F51 |  | X | X | 35A |  |  | 35A | X | X |  | F111
| F52 |  | X | X | 35A |  |  | 35A | X | X |  | F112
| F53 |  | X | X | 35A |  |  | 35A | X | X |  | F113
| F54 |  | X | X | 35A |  |  | 35A | X | X |  | F114
| F55 |  | X | X | 35A |  |  | X | X | X |  | F115
| F56 |  | X | X | 35A |  |  | X | X | X |  | F116
| F57 |  | X | X | 35A |  |  | X | X | X |  | F117
| F58 |  | X | X | 35A |  |  | X | X | X |  | F118
| F59 |  | X | X | 35A |  |  | X | X | X |  | F119
| F60 |  | X | X | 35A |  |  | X | X | X |  | F120
[7 empty] | 합계: | 0
|  | B-B1 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/B-5 (구 IPD-A)
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
| F1 |  | X |  | 400A |  |  | 400A | X |  |  | F2
| F3 |  | X | X | X |  |  | 400A | X |  |  | F4
| F5 |  | X | X | X |  |  | 35A | O | O | IPD / B-5_P03 F-8 랙 PDP_A off상태 | F40 | 미사용
| F6 |  | X | X | X |  |  | X | X |  |  | F41
| F7 |  | X | X | X |  |  | 35A | O | O | IPD / B-5_P42 A-5 랙 장비_A(1) | F42 | 장비직결
| F8 |  | X | X | X |  |  | 35A | O | O | IPD / B-5_P43 A-5 랙 장비_A(2) | F43 | 장비직결
| F9 |  | X | X | X |  |  | X | O | X | C-8-A | F44
| F10 |  | X | X | X |  |  | X | O | X | C-7-A | F45
| F11 |  | X | X | X |  |  | X | X | X |  | F46
| F12 |  | X | X | X |  |  | X | O | X | D3-A | F47
| F13 |  | X | X | X |  |  | 100A | O | O | IPD / B-5_P48 C-1 랙 장비__A | F48 | 장비직결
| F14 |  | X | X | X |  |  | X | X | X |  | F49
| F15 |  | X | X | X |  |  | X | X | X |  | F50
| F16 |  | X | X | X |  |  | 35A | X | X |  | F51
| F17 |  | X | X | X |  |  | 35A | X | X |  | F52
| F18 |  | X | X | X |  |  | 35A | X | X |  | F53
| F19 |  | X | X | X |  |  | 35A | X | X |  | F54
| F20 |  | X | X | X |  |  | 35A | X | X |  | F55
| F21 |  | X | X | X |  |  | 35A | X | X |  | F56
| F22 |  | X | X | 50A |  |  | 35A | X | X |  | F57
| F23 |  | X | X | 50A |  |  | 35A | X | X |  | F58
| F24 |  | X | X | 50A |  |  | 35A | X | X |  | F59
| F25 |  | X | X | 50A |  |  | 35A | X | X |  | F60
| F26 |  | X | X | 50A |  |  | 35A | X | X |  | F61
| F27 |  | X | X | 50A |  |  | 35A | X | X |  | F62
| F28 |  | X | X | 50A |  |  | 35A | X | X |  | F63
| F29 |  | X | X | 50A |  |  | 35A | X | X |  | F64
| F30 |  | X | X | 50A |  |  | 35A | X | X |  | F65
| F31 |  | X | X | 50A |  |  | 35A | X | X |  | F66
| F32 |  | X | X | 50A |  |  | 35A | X | X |  | F67
| F33 |  | X | X | 50A |  |  | 35A | X | X |  | F68
| F34 |  | X | X | 50A |  |  | 35A | X | X |  | F69
| F35 |  | X | X | 50A |  |  | 35A | X | X |  | F70
| F36 |  | X | X | 50A |  |  | 35A | X | X |  | F71
| F37 |  | X | X | 50A |  |  | 35A | X | X |  | F72
| F38 |  | X | X | 50A |  |  | X | O | X | E-7랙 | F73
| F39 |  | X | X | 50A |  |  | 35A | X | X |  | F74
[7 empty] | 합계: | 0
[6 empty] | 0 | 0 | 0
Note on C300: 이현상: 2021.09.14 전원 투입