Monthly
Report

February 2023

| DC Site Name: NARRA 1 Customer: Customer ID: Report ID: DE-RPT-CUST-2023-xx | info@digitaledgedc.com digitaledgedc.com |
| --- | --- |

Digital Edge Monthly Report

Contents

1.	Executive Summary	3

1.1.	Service Level Availability Achievement________________________________________________	3

2.	Temperature and Relative Humidity	3

3.	Incident Report Summary	4

4.	Site Access Report	5

5.	Shipment Report	5

6.	Remote Hands Report	6

7.	Maintenance Schedule	7

8.	Power Usage	8

8.1.	Summary of Power Usage for the Month_____________________________________________	8

| Prepared By | Data Center Operations Manager |
| --- | --- |
| Prepared For | Customer |
| Important Note | Digital Edge DC Proprietary Information: The information contained in this document is confidential and proprietary to Digital Edge. The use, disclosure, reproduction, or distribution of this information to any third party without the written permission of Digital Edge is prohibited. |

Executive Summary

During the month, the Service Availability for all facility services for the Data Center is at 100%. There are no incidents reported for the month.

Service Level Availability Achievement

All SLAs were met for the month of xx 2023.

Table 1 - Service Level Availability

| Service Level Agreement | Target Availability | Availability Achieved (%) |
| --- | --- | --- |
| Power | 99.99% (Non Redundant) 100% (Redundant) | 100% |
| Temperature (18°C – 27°C) | 99.99% | 100% |
| Relative Humidity (30% - 70%) | 99.99% | 100% |

Temperature and Relative Humidity

The following table shows the average temperature, relative humidity, and the trend for Data Hall xxx…

- The recorded result for temperature is within the SLA: 18°C - 27°C

- The recorded result for relative humidity (RH) is within the SLA: 30% - 70%

Table 2 - Monthly Records for Temperature and Relative Humidity

| Data Center - location |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Month in 2023 | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| Ave. Temp (°C) | 21.83 | 22.90 |  |  |  |  |  |  |  |  |  |  |
| Ave. Hum (%) | 54.56 | 53.37 |  |  |  |  |  |  |  |  |  |  |

Figure 1 - Trend Log for Temperature and Relative Humidity

Incident Report Summary

The Incident Report summary will comprise details of incidents occurred within the reporting month that affects the performance of the Power, Temperature, Relative Humidity and Security Access to the customer leased area.

Below is a summary of the incident report for the month.

Table 3 - Incident Report Summary

| S/N | Incident Ticket No. | Descriptions | Start Date Time | End Date Time | Comments Attached IR |
| --- | --- | --- | --- | --- | --- |
| 1 | MNL01_20230511_01 | Breaker trip for Power Source B to Rack 11-05 | 16 Jun 23 1159hr | 16 Jun 23 1230hr | Breaker trip was caused by faulty PS on Server (XXYY) in rack. |

Site Access Report

The following is a summary of the site access tickets. Please refer to the attachment for details.

Table 4 - Site Access Tickets

| Created Date Time | Ticket No. | Ticket Type | Site Visit Date Time | Visitor Names |
| --- | --- | --- | --- | --- |
| 2023-06-13 16:27:24 | 6193 | Work Visits | 2023-06-13 16:27:00 | 박민영 |
| 2023-06-13 08:53:02 | 6161 | Work Visits | 2023-06-20 13:00:00 | 김민균 |
| 2023-06-12 13:26:55 | 6134 | Work Visits | 2023-06-16 08:00:00 | 조이국 |
| Attachments |  |  |  |  |

Shipment Report

The following is a summary of the shipping tickets. Please refer to the attachment for details.

Table 5 - Shipment Tickets Requests

| Created Date Time | Ticket No. | Requester | Ticket Type | Status |
| --- | --- | --- | --- | --- |
| 2023-06-13 15:41:39 | 6190 | 정진환 부장 | Inbound | Pending Approval |
| 2023-06-09 08:57:44 | 6041 | 문민주 | Inbound | Completed |
| 2023-06-07 14:39:28 | 5955 | DEK PUS1 | Inbound | Pending Approval |
| 2023-06-07 14:01:47 | 5952 | DEK PUS1 | Inbound | Pending Approval |
| Attachments |  |  |  |  |

Remote Hands Report

The following is a summary of the shipping tickets. Please refer to the attachment for details

Table 6 - Remote Hand Service Requests

| Created Date Time | Subject | Ticket Sub-Type | Requester | Service ID | Total Hours Spent |
| --- | --- | --- | --- | --- | --- |
| 2023-06-13 05:44:19 | [Sysone] 서버 재부팅 요청 | Power On/Off Equipment | XXX | SSOKR-IB-00035532: 19" Cabinet | 0.50 |
| 2023-06-09 11:39:43 | [한국JS데이터시스템즈] 서버 리부팅 요청 | Power On/Off Equipment | XXX | JSDKR-IB-00035395: 19" Cabinet | 0.25 |
| Attachments |  |  |  |  |  |

Maintenance Schedule

- The following maintenance activities were performed for the month and planned for the next 2 months.

Table 7 - Schedule Maintenance

| S/N | Systems | Maint. Frequency | May 2023 |  | Jun 2023 |  | Jul 2023 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Plan | Actual | Plan | Actual | Plan | Actual |
| 1 | Water Leak Detection | Monthly | 18 | 18 | 20 | - | 20 | - |
| 2 | BMS | Quarterly | - | - | 8 | - | - | - |
| 3 | Cooling Towers | Quarterly | - | - | 28 | - | - | - |
| 4 | CHWP & CWP | Quarterly | - | - | 28 | - | - | - |
| 5 | CRAC Units | Monthly | 5 | 5 | 7 | - | 5 | - |
| 6 | Thermal Graphic Scanning | Annual | 17 | 17 | - | - | - | - |
| 7 | Shutdown Maintenance for DRUPS | 5 years | - | - | - | - | - | - |
| 8 | Fan & Cap Replacement for DRUPS | Bi-monthly | 8, 22 | 8, 22 | 5, 19 | - | 10,24 | - |
| 9 | Fire Drills (Building / DC evacuation) | Annual | - | - | - | - | - | - |
| 10 | Fire Protection (pre-action & building system) | Bi-yearly | - | - | - | - | - | - |
| 11 | Fire Extinguisher | Annual | 16 | 16 | - | - | 19 | - |
| 12 | Fire Extinguisher In-house Inspection | Monthly | 16 | 16 | 19 | - | 19 | - |
| 13 | Generator Run-Test (in-house no load test) | Monthly | 5 | 5 | 7 | - | 5 | - |
| Attachments |  |  |  |  |  |  |  |  |

Power Usage

Summary of Power Usage for the Month

The following is a summary of the power usage for the subscribed racks.

Table 8 - Rack in KVA & Total Power in KWh –Dedicated RPP/PDUs

|  | Description | Power |
| --- | --- | --- |
| Total Power Usage for Customer XXYY | Power Usage Total | 70.32 kW |
|  | Subscribed Power | 81.00 KVA |
|  | Remaining Power | 10.68 kW |
| Attachments |  |  |