## 7층_랙별_계통_및_부하량
7층 전송 및 고객 랙별 부하 사용내역
|  |  |  | =E5:E278 | [33 empty] | =AM5:AM278 |  | 2023년 기준
구분 | DEKR NO. | BAY NAME | RACK NAME | 계약용량 | 전원구성 |  | DEK차단기명칭 |  | DEK차단기명칭 (NEW) |  | 차단기 정보(수정) | [7 empty] | Fuse/차단기 정보 |  | IPD/2차분전반 사용정보 |  | 2차 분전반/정류기 정보 |  | 1차 분전반 사용정보 |  | 1차 분전반 정보 |  | 배전반 정보 |  | TR 정보 |  | 계측값 |  |  | 월 유효전력량 |  | 월간 사용전력량[kWh] | RACK별 장비명 | 비고
구분 |  |  |  | kW | AC | DC | A | B | A | B | A |  |  |  | B |  |  |  | A | B | A | B | A | B | A | B | A | B | A | B | A | B | A전원 | B전원 | 합계 | A전원 | B전원
SJT | 정류기실 |  | SJT 정류기1 | 50 | ○ |  | 7-1-A4-225-6 |  | 7-DaHall 1-PDU-03-225-6 |  | 380 | 225 | PDU-03 | 6 |  |  |  |  | A: 7-1-A4-06 / 4P 225A; A: 7-1-A4 (4P 400A); A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 131.1306; 합계: 131.1306; A전원: 22829.8 | 22829.8
|  |  | SJT 정류기2 | 50 | ○ |  |  | 7-1-B4-150-1 |  | 7-DaHall 1-PDU-04-150-1 |  |  |  |  | 380 | 150 | PDU-04 | 1 | B: 7-1-B4-01 / 3P 150A; B: 7-1-B4 (4P 400A); B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 142.2093; 합계: 142.2093; B전원: 20193.4 | 20193.4
회의실 |  |  | TEST_BED |  |  | ○ | 7-1-A-4-35-32 | 7-1-B-4-35-32 | 7-DaHall 1-A-4-35-32 | 7-DaHall 1-B-4-35-32 | 48 | 35 | A-4 | 32 | 48 | 35 | B-4 | 32 | IPD A-4-32 / 35A | IPD B-4-32 / 35A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | TEST_BED 장비
| A111 |  |  | 2.2 | ○ |  | 7-1-A2-30-37 | 7-1-B2-30-37 | 7-DaHall 1-PDU-01-30-37 | 7-DaHall 1-PDU-02-30-37 | 220 | 30 | PDU-01 | 37 | 220 | 30 | PDU-02 | 37 | A: U3-7A-37 / 2P 30A; B: U3-7B-37 / 2P 30A; A: U3-7A(U7-5A) 4P 300A; B: U3-7B(U7-6B) 4P 300A; A: LV-7A #05 / 3P 320A (U7-5A); B: LV-7B #06 / 3P 320A (U7-6B); A전원: 1.7538; B전원: 1.2372; 합계: 2.991; A전원: 0; B전원: 0 | 0 | TEST_BED 계측기/노트북 전원
| A207 | 538 BAY | 538B_NOKIA1830 |  |  | ○ | 7-1-A-4-100-58 | 7-1-B-4-100-58 | 7-DaHall 1-A-4-100-58 | 7-DaHall 1-B-4-100-58 | 48 | 100 | A-4 | 58 | 48 | 100 | B-4 | 58 | IPD A-4-58 / 100A | IPD B-4-58 / 100A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| A208 | 537 BAY | 537B_NOKIA1830 |  |  | ○ | 7-1-A-4-100-56 | 7-1-B-4-35-56 | 7-DaHall 1-A-4-100-56 | 7-DaHall 1-B-4-35-56 | 48 | 100 | A-4 | 56 | 48 | 35 | B-4 | 56 | IPD A-4-56 / 100A | IPD B-4-56 / 35A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| A209 | 536 BAY | 536B_NOKIA1830 |  |  | ○ | 7-1-A-4-50-59 | 7-1-B-4-50-59 | 7-DaHall 1-A-4-50-59 | 7-DaHall 1-B-4-50-59 | 48 | 50 | A-4 | 59 | 48 | 50 | B-4 | 59 | IPD A-4-59 / 50A | IPD B-4-59 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| A210 | 535 BAY | 536B_NOKIA1830, PSS-8 |  |  | ○ | 7-1-A-4-50-25 | 7-1-B-4-50-25 | 7-DaHall 1-A-4-50-25 | 7-DaHall 1-B-4-50-25 | 48 | 50 | A-4 | 25 | 48 | 50 | B-4 | 25 | IPD A-4-25 / 50A | IPD B-4-25 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | 노키아1830_PSS 8 ('21.09.14 전기투입)
|  | 443 BAY | [35 empty] | 0
|  | 442 BAY | [35 empty] | 0
|  | 441 BAY | [35 empty] | 0
| A307 | 440 BAY | 440B_CN6500 |  |  | ○ | 7-1-B-4-100-31 | 7-1-A-4-100-31 | 7-DaHall 1-B-4-100-31 | 7-DaHall 1-A-4-100-31 | 48 | 100 | B-4 | 31 | 48 | 100 | A-4 | 31 | IPD B-4-31 / 100A | IPD A-4-31 / 100A | IPD B-4 | IPD A-4 | 정류기 B -48V 1400A | 정류기 A -48V 1400A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | [5 empty] | 0
| A308 | 439 BAY | 439B_CN6500 |  |  | ○ | 7-1-B-4-100-30 | 7-1-A-4-100-30 | 7-DaHall 1-B-4-100-30 | 7-DaHall 1-A-4-100-30 | 48 | 100 | B-4 | 30 | 48 | 100 | A-4 | 30 | IPD B-4-30 / 100A | IPD A-4-30 / 100A | IPD B-4 | IPD A-4 | 정류기 B -48V 1400A | 정류기 A -48V 1400A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | [5 empty] | 0
| A309 | 437 BAY | 437B(上)_코위버P7200 |  |  | ○ | 7-1-A-4-100-29 | 7-1-B-4-100-29 | 7-DaHall 1-A-4-100-29 | 7-DaHall 1-B-4-100-29 | 48 | 100 | A-4 | 29 | 48 | 100 | B-4 | 29 | IPD A-4-29 / 100A | IPD B-4-29 / 100A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | 코위버P7200
|  |  | 437B(下)_텔레필드_FM700 |  |  | ○ | 7-1-A-4-35-34 | 7-1-B-4-35-34 | 7-DaHall 1-A-4-35-34 | 7-DaHall 1-B-4-35-34 | 48 | 35 | A-4 | 34 | 48 | 35 | B-4 | 34 | IPD A-4-34 / 35A | IPD B-4-34 / 35A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | 텔레필드_FM700 | 2021/06/10 전원신규 구성 및 투입
| A310 | 436 BAY | 436B_코위버P7200 |  |  | ○ | 7-1-A-4-100-3 | 7-1-B-4-100-3 | 7-DaHall 1-A-4-100-3 | 7-DaHall 1-B-4-100-3 | 48 | 100 | A-4 | 3 | 48 | 100 | B-4 | 3 | IPD A-4-03 / 100A | IPD B-4-03 / 100A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| A402 | 343 BAY | Sejong Telecom Inc. |  |  | ○ | 7-1-A-4-50-41 | 7-1-B-4-50-41 | 7-DaHall 1-A-4-50-41 | 7-DaHall 1-B-4-50-41 | 48 | 50 | A-4 | 41 | 48 | 50 | B-4 | 41 | IPD A-4-41 / 50A | IPD B-4-41 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 |  | DC 전원 미사용
[5 empty] | ○ | [13 empty] | A: U3-7A-05 / 2P 30A (342Bay 인출) | 0 |  | 342Bay에서 1개 전원 인출사용 중
| A403 | 342 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-B2-30-3 | 7-1-A2-30-5 | 7-DaHall 1-PDU-01-30-5 | 7-DaHall 1-PDU-02-30-3 | 220 | 30 | PDU-02 | 3 | 220 | 30 | PDU-01 | 5 | U3-7B-03 / 2P 30A | U3-7A-05 / 2P 30A | [6 empty] | U3-7B(U7-6B) 4P 300A | U3-7A(U7-5A) 4P 300A | LV-7B #06 / 3P 320A (U7-6B) | LV-7A #05 / 3P 320A (U7-5A) | TR-7B 1000kVA | TR-7A 1000kVA | 5.2297 | 5.5322 | 10.7619 | 744.6 | 731.8 | 1476.4 | 인터넷팀 장비
| A404 | 341 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A1-30-40 | 7-1-B1-30-38 | 7-DaHall 1-RPP-01-30-40 | 7-DaHall 1-RPP-02-30-38 | 220 | 30 | RPP-01 | 40 | 220 | 30 | RPP-02 | 38 | UPS A1-40 / 2P 30A | UPS B1-38 / 2P 30A | UPS 출력분전반 A1 #40 | UPS 출력분전반 B1 #38 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 4.8317 | 5.3995 | 10.2313 | 736.8 | 745.2 | 1482 | 인터넷팀 장비(MAN POP)
| A405 | 340 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A1-20-25 | 7-1-A1-30-20 | 7-DaHall 1-RPP-01-20-25 | 7-DaHall 1-RPP-01-30-20 | 220 | 20 | RPP-01 | 25 | 220 | 30 | RPP-01 | 20 | UPS A1-25 / 2P 20A | UPS A1-20 / 2P 30A | UPS 출력분전반 A1 #25 | UPS 출력분전반 A1 #20 | UPS 출력 분전반A1, 4P 400A |  | UPS 출력 분전반A, #01 4P 225A |  | UPS 출력 배전반A, 4P 400A |  | LV-7A #06 / 3P 320A (U7-6A) |  | TR-7A 1000kVA |  | 1.5435 | 1.4647 | 3.0082 | 233.4 | 223.8 | 457.2 | 인터넷팀 장비 | 인터넷운영팀 MAN Rack #2, A & B전원
| A406 | 339 BAY | 339B_CN4200 |  |  | ○ | 7-1-B-4-35-46 | 7-1-A-4-35-42 | 7-DaHall 1-B-4-35-46 | 7-DaHall 1-A-4-35-42 | 48 | 35 | B-4 | 46 | 48 | 35 | A-4 | 42 | IPD B-4-46 / 35A | IPD A-4-42 / 35A | IPD B-4 | IPD A-4 | 정류기 B -48V 1400A | 정류기 A -48V 1400A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | [5 empty] | 0
| A407 | 338 BAY | Sejong Telecom Inc. |  |  | ○ | 7-1-A-4-35-43 | 7-1-B-4-50-47 | 7-DaHall 1-A-4-35-43 | 7-DaHall 1-B-4-50-47 | 48 | 35 | A-4 | 43 | 48 | 50 | B-4 | 47 | IPD A-4-43 / 35A | IPD B-4-47 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
|  |  |  | 1.6 | ○ | [13 empty] | A: UPS A1-25 / 2P 20A (340Bay에서 인출) | 0 |  | 340Bay에서 1개 전원 인출사용 중
| A408 | 337 BAY | Sejong Telecom Inc. |  |  | ○ | 7-1-A-4-35-44 | 7-1-B-4-35-48 | 7-DaHall 1-A-4-35-44 | 7-DaHall 1-B-4-35-48 | 48 | 35 | A-4 | 44 | 48 | 35 | B-4 | 48 | IPD A-4-44 / 35A | IPD B-4-48 / 35A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
|  |  |  | 1.6 | ○ |  |  | 7-1-B2-30-8 |  | 7-DaHall 1-PDU-02-30-8 |  |  |  |  | 220 | 30 | PDU-02 | 8 | B: U3-7B-08 / 2P 30A; B: U3-7B(U7-6B) 4P 300A; B: LV-7B #06 / 3P 320A (U7-6B); B: TR-7B 1000kVA; B전원: 1.011; 합계: 1.011; B전원: 3 | 3
| A409 | 336 BAY | 336B_CN4200 |  |  | ○ | 7-1-A-4-35-50 | 7-1-B-4-35-50 | 7-DaHall 1-A-4-35-50 | 7-DaHall 1-B-4-35-50 | 48 | 35 | A-4 | 50 | 48 | 35 | B-4 | 50 | IPD A-4-50 / 35A | IPD B-4-50 / 35A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| A410 | 335 BAY | 335B_CN4200 |  |  | ○ | 7-1-A-4-50-46 | 7-1-B-4-50-49 | 7-DaHall 1-A-4-50-46 | 7-DaHall 1-B-4-50-49 | 48 | 50 | A-4 | 46 | 48 | 50 | B-4 | 49 | IPD A-4-46 / 50A | IPD B-4-49 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| A411 | 334 BAY | 334B_CN4200 |  |  | ○ | 7-1-A-4-35-54 | 7-1-B-4-35-54 | 7-DaHall 1-A-4-35-54 | 7-DaHall 1-B-4-35-54 | 48 | 35 | A-4 | 54 | 48 | 35 | B-4 | 54 | IPD A-4-54 / 35A | IPD B-4-54 / 35A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| A502 | 244 BAY | 244B_코위버CWDM |  |  | ○ | 7-1-A-4-50-26 | 7-1-B-4-50-26 | 7-DaHall 1-A-4-50-26 | 7-DaHall 1-B-4-50-26 | 48 | 50 | A-4 | 26 | 48 | 50 | B-4 | 26 | IPD A-4-26 / 50A | IPD B-4-26 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| A503 | 243 BAY | 243B_코위버CWDM |  |  | ○ | 7-1-A-4-50-28 | 7-1-B-4-50-28 | 7-DaHall 1-A-4-50-28 | 7-DaHall 1-B-4-50-28 | 48 | 50 | A-4 | 28 | 48 | 50 | B-4 | 28 | IPD A-4-28 / 50A | IPD B-4-28 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| A504 | 242 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-9 | 7-1-B2-30-9 | 7-DaHall 1-PDU-01-30-9 | 7-DaHall 1-PDU-02-30-9 | 220 | 30 | PDU-01 | 9 | 220 | 30 | PDU-02 | 9 | U3-7A-09 / 2P 30A | U3-7B-09 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 5.6284 | 5.1452 | 10.7736 | 957.7 | 870.9 | 1828.6 | 인터넷팀 장비
| A505 | 241 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-7 | 7-1-B2-30-7 | 7-DaHall 1-PDU-01-30-7 | 7-DaHall 1-PDU-02-30-7 | 220 | 30 | PDU-01 | 7 | 220 | 30 | PDU-02 | 7 | U3-7A-07 / 2P 30A | U3-7B-07 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 6.0984 | 5.6451 | 11.7434 | 920.5 | 880.2 | 1800.7 | 인터넷팀 장비
| A506 | 240 BAY | 240B_코위버CWDM |  |  | ○ | 7-1-A-4-50-27 | 7-1-B-4-50-57 | 7-DaHall 1-A-4-50-27 | 7-DaHall 1-B-4-50-57 | 48 | 50 | A-4 | 27 | 48 | 50 | B-4 | 57 | IPD A-4-27 / 50A | IPD B-4-57 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 |  | PDP 2개
[6 empty] | ○ | 7-1-A-4-50-33 | 7-1-B-4-50-33 | 7-DaHall 1-A-4-50-33 | 7-DaHall 1-B-4-50-33 | 48 | 50 | A-4 | 33 | 48 | 50 | B-4 | 33 | IPD A-4-33 / 50A | IPD B-4-33 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| A507 | 239 BAY | 239B_OSN7500 |  |  | ○ | 7-1-A-4-50-10 | 7-1-B-4-50-43 | 7-DaHall 1-A-4-50-10 | 7-DaHall 1-B-4-50-43 | 48 | 50 | A-4 | 10 | 48 | 50 | B-4 | 43 | IPD A-4-10 / 50A | IPD B-4-43 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 |  | IPD 3개
[6 empty] | ○ | 7-1-A-4-50-11 | 7-1-B-4-50-44 | 7-DaHall 1-A-4-50-11 | 7-DaHall 1-B-4-50-44 | 48 | 50 | A-4 | 11 | 48 | 50 | B-4 | 44 | IPD A-4-11 / 50A | IPD B-4-44 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
[6 empty] | ○ | 7-1-A-4-50-18 | 7-1-B-4-50-45 | 7-DaHall 1-A-4-50-18 | 7-DaHall 1-B-4-50-45 | 48 | 50 | A-4 | 18 | 48 | 50 | B-4 | 45 | IPD A-4-18 / 50A | IPD B-4-45 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| A508 | 238 BAY | 238B_동원DWDM |  |  | ○ | 7-1-A-4-50-45 | 7-1-B-4-50-51 | 7-DaHall 1-A-4-50-45 | 7-DaHall 1-B-4-50-51 | 48 | 50 | A-4 | 45 | 48 | 50 | B-4 | 51 | IPD A-4-45 / 50A | IPD B-4-51 / 50A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| A509 | 237 BAY | 237B_CN4200 |  |  | ○ | 7-1-A-4-35-52 | 7-1-B-4-35-52 | 7-DaHall 1-A-4-35-52 | 7-DaHall 1-B-4-35-52 | 48 | 35 | A-4 | 52 | 48 | 35 | B-4 | 52 | IPD A-4-52 / 35A | IPD B-4-52 / 35A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| A510 | 236 BAY | 236B_CN4200 |  |  | ○ | 7-1-A-4-35-53 | 7-1-B-4-35-53 | 7-DaHall 1-A-4-35-53 | 7-DaHall 1-B-4-35-53 | 48 | 35 | A-4 | 53 | 48 | 35 | B-4 | 53 | IPD A-4-53 / 35A | IPD B-4-53 / 35A | IPD A-4 | IPD B-4 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B202 | 532 BAY | 532B_코위버1664 |  |  | ○ | 7-1-A-3-50-47 | 7-1-B-3-50-47 | 7-DaHall 1-A-3-50-47 | 7-DaHall 1-B-3-50-47 | 48 | 50 | A-3 | 47 | 48 | 50 | B-3 | 47 | IPD A-3-47 / 50A | IPD B-3-47 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B203 | 531 BAY | 531B_코위버1664 |  |  | ○ | 7-1-A-3-50-46 | 7-1-B-3-50-46 | 7-DaHall 1-A-3-50-46 | 7-DaHall 1-B-3-50-46 | 48 | 50 | A-3 | 46 | 48 | 50 | B-3 | 46 | IPD A-3-46 / 50A | IPD B-3-46 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B204 | 530 BAY | 530B_코위버1664 |  |  | ○ | 7-1-A-3-50-44 | 7-1-B-3-50-44 | 7-DaHall 1-A-3-50-44 | 7-DaHall 1-B-3-50-44 | 48 | 50 | A-3 | 44 | 48 | 50 | B-3 | 44 | IPD A-3-44 / 50A | IPD B-3-44 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B206 |  | Sejong Telecom Inc.('23.10.12 투입) | 1.6 | ○ |  | 7-1-A2-30-48 | 7-1-B2-30-48 | 7-DaHall 1-PDU-01-30-48 | 7-DaHall 1-PDU-02-30-48 | 220 | 30 | PDU-01 | 48 | 220 | 30 | PDU-02 | 48 | U3-7A-48 / 2P 30A | U3-7B-48 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.0633 | 2.4513 | 4.5146 | 267.2 | 293.5 | 560.7 | SJT | '23.10.12 투입
| B207 | 527 BAY | 527B_코위버1664 |  |  | ○ | 7-1-A-3-50-41 | 7-1-B-3-50-41 | 7-DaHall 1-A-3-50-41 | 7-DaHall 1-B-3-50-41 | 48 | 50 | A-3 | 41 | 48 | 50 | B-3 | 41 | IPD A-3-41 / 50A | IPD B-3-41 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B208 | 526 BAY | 526B_코위버1664 |  |  | ○ | 7-1-A-3-50-10 | 7-1-B-3-50-10 | 7-DaHall 1-A-3-50-10 | 7-DaHall 1-B-3-50-10 | 48 | 50 | A-3 | 10 | 48 | 50 | B-3 | 10 | IPD A-3-10 / 50A | IPD B-3-10 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B209 | 525 BAY | 525B_코위버1664 |  |  | ○ | 7-1-A-3-50-7 | 7-1-B-3-50-7 | 7-DaHall 1-A-3-50-7 | 7-DaHall 1-B-3-50-7 | 48 | 50 | A-3 | 7 | 48 | 50 | B-3 | 7 | IPD A-3-07 / 50A | IPD B-3-07 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B210 | 524 BAY | 524B_코위버1664 |  |  | ○ | 7-1-A-3-50-6 | 7-1-B-3-50-6 | 7-DaHall 1-A-3-50-6 | 7-DaHall 1-B-3-50-6 | 48 | 50 | A-3 | 6 | 48 | 50 | B-3 | 6 | IPD A-3-06 / 50A | IPD B-3-06 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B211 | 523 BAY | 523B_코위버3264 |  |  | ○ | 7-1-A-3-50-5 | 7-1-B-3-50-5 | 7-DaHall 1-A-3-50-5 | 7-DaHall 1-B-3-50-5 | 48 | 50 | A-3 | 5 | 48 | 50 | B-3 | 5 | IPD A-3-05 / 50A | IPD B-3-05 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B216 |  |  |  |  | ○ | 7-1-A-2-50-48 | 7-1-B-2-50-48 | 7-DaHall 1-A-2-50-48 | 7-DaHall 1-B-2-50-48 | 48 | 50 | A-2 | 48 | 48 | 50 | B-2 | 48 | IPD A-2-48 / 50A | IPD B-2-48 / 50A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | 드림라인 장비
| B217 |  | Sejong Telecom Inc. |  |  | ○ | 7-1-A-2-35-47 | 7-1-B-2-35-47 | 7-DaHall 1-A-2-35-47 | 7-DaHall 1-B-2-35-47 | 48 | 35 | A-2 | 47 | 48 | 35 | B-2 | 47 | IPD A-2-47 / 35A | IPD B-2-47 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | SKT/SKB장비 | PDP 2개 ??
[5 empty] | ○ | [13 empty] | A: UPS A1-07 / 2P 20A (518Bay에서 인출) | 0
[6 empty] | ○ | 7-1-A-2-35-53 | 7-1-B-2-35-53 | 7-DaHall 1-A-2-35-53 | 7-DaHall 1-B-2-35-53 | 48 | 35 | A-2 | 53 | 48 | 35 | B-2 | 53 | IPD A-2-53 / 35A | IPD B-2-53 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B218 |  | Sejong Telecom Inc. |  |  | ○ | 7-1-A-2-16-44 | 7-1-B-2-16-46 | 7-DaHall 1-A-2-16-44 | 7-DaHall 1-B-2-16-46 | 48 | 16 | A-2 | 44 | 48 | 16 | B-2 | 46 | IPD A-2-44 / 16A | IPD B-2-46 / 16A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | 드림라인 장비
[5 empty] | ○ | [13 empty] | A: UPS A1-07 / 2P 20A (517Bay에서 인출) | 0
| B219 |  | Sejong Telecom Inc. |  |  | ○ | 7-1-A-2-35-58 | 7-1-B-2-35-58 | 7-DaHall 1-A-2-35-58 | 7-DaHall 1-B-2-35-58 | 48 | 35 | A-2 | 58 | 48 | 35 | B-2 | 58 | IPD A-2-58 / 35A | IPD B-2-58 | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | SKB장비
|  |  |  | 2.2 | ○ |  | 7-1-A1-20-7 |  | 7-DaHall 1-RPP-01-20-7 |  | 220 | 20 | RPP-01 | 7 |  |  |  |  | A: UPS A1-07 / 2P 20A; A: UPS 출력분전반 A1 #07; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 0 | 0
| B222 | 514 BAY | 514B_LGU+장비 |  |  | ○ | 7-1-A-2-50-23 | 7-1-B-2-50-23 | 7-DaHall 1-A-2-50-23 | 7-DaHall 1-B-2-50-23 | 48 | 50 | A-2 | 23 | 48 | 50 | B-2 | 23 | IPD A-2-23 / 50A | IPD B-2-23 | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | LGU+장비
| B223 | 513 BAY | 513B_SKB장비 |  |  | ○ | 7-1-A-2-50-7 | 7-1-B-2-50-7 | 7-DaHall 1-A-2-50-7 | 7-DaHall 1-B-2-50-7 | 48 | 50 | A-2 | 7 | 48 | 50 | B-2 | 7 | IPD A-2-07 / 50A | IPD B-2-07 | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | SKB장비
| B224 | 512 BAY | Digital Edge | 2.2 | ○ | [13 empty] | B: 회로 조사 실패, B1 PNL 의심 / 413Bay 상부에서 숨어버림; 합계: 0 | 0 | 7F-5F UTP PATCH
| B225 | 511 BAY | 511B_LGU+장비 |  |  | ○ | 7-1-A-2-35-62 | 7-1-B-2-35-62 | 7-DaHall 1-A-2-35-62 | 7-DaHall 1-B-2-35-62 | 48 | 35 | A-2 | 62 | 48 | 35 | B-2 | 62 | IPD A-2-62 / 35A | IPD B-2-62 | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | LGU+장비 | PDP 1개, 장비직결 1개
[6 empty] | ○ | 7-1-A-2-35-63 | 7-1-B-2-35-63 | 7-DaHall 1-A-2-35-63 | 7-DaHall 1-B-2-35-63 | 48 | 35 | A-2 | 63 | 48 | 35 | B-2 | 63 | IPD A-2-63 / 35A | IPD B-2-63 | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B306 | 427 BAY | 427B_ZTE POTN |  |  | ○ | 7-1-A-3-50-57 | 7-1-B-3-50-57 | 7-DaHall 1-A-3-50-57 | 7-DaHall 1-B-3-50-57 | 48 | 50 | A-3 | 57 | 48 | 50 | B-3 | 57 | IPD A-3-57 / 50A | IPD B-3-57 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 |  | IPD 2개
[6 empty] | ○ | 7-1-A-3-50-58 | 7-1-B-3-50-58 | 7-DaHall 1-A-3-50-58 | 7-DaHall 1-B-3-50-58 | 48 | 50 | A-3 | 58 | 48 | 50 | B-3 | 58 | IPD A-3-58 / 50A | IPD B-3-58 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B307 | 426 BAY | 426B_ZTE POTN |  |  | ○ | 7-1-A-3-100-1 | 7-1-B-3-100-1 | 7-DaHall 1-A-3-100-1 | 7-DaHall 1-B-3-100-1 | 48 | 100 | A-3 | 1 | 48 | 100 | B-3 | 1 | IPD A-3-01 / 100A | IPD B-3-01 / 100A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 |  | IPD 3개
[6 empty] | ○ | 7-1-A-3-100-2 | 7-1-B-3-100-2 | 7-DaHall 1-A-3-100-2 | 7-DaHall 1-B-3-100-2 | 48 | 100 | A-3 | 2 | 48 | 100 | B-3 | 2 | IPD A-3-02 / 100A | IPD B-3-02 / 100A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
[6 empty] | ○ | 7-1-A-3-50-3 | 7-1-B-3-50-3 | 7-DaHall 1-A-3-50-3 | 7-DaHall 1-B-3-50-3 | 48 | 50 | A-3 | 3 | 48 | 50 | B-3 | 3 | IPD A-3-03 / 50A | IPD B-3-03 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B308 | 425 BAY | 425B_ZTE POTN |  |  | ○ | 7-1-A-3-50-42 | 7-1-B-3-50-42 | 7-DaHall 1-A-3-50-42 | 7-DaHall 1-B-3-50-42 | 48 | 50 | A-3 | 42 | 48 | 50 | B-3 | 42 | IPD A-3-42 / 50A | IPD B-3-42 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 |  | IPD 2개
[6 empty] | ○ | 7-1-A-3-50-43 | 7-1-B-3-50-43 | 7-DaHall 1-A-3-50-43 | 7-DaHall 1-B-3-50-43 | 48 | 50 | A-3 | 43 | 48 | 50 | B-3 | 43 | IPD A-3-43 / 50A | IPD B-3-43 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B309 | 424 BAY | 424B_ZTE385 |  |  | ○ | 7-1-A-3-50-27 | 7-1-B-3-50-27 | 7-DaHall 1-A-3-50-27 | 7-DaHall 1-B-3-50-27 | 48 | 50 | A-3 | 27 | 48 | 50 | B-3 | 27 | IPD A-3-27 / 50A | IPD B-3-27 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B310 | 423 BAY | 423B_코위버1664 |  |  | ○ | 7-1-A-3-50-26 | 7-1-B-3-50-26 | 7-DaHall 1-A-3-50-26 | 7-DaHall 1-B-3-50-26 | 48 | 50 | A-3 | 26 | 48 | 50 | B-3 | 26 | IPD A-3-26 / 50A | IPD B-3-26 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B315 | 420 BAY | 420B_DOTS |  |  | ○ | 7-1-A-3-35-53 | 7-1-B-3-35-52 | 7-DaHall 1-A-3-35-53 | 7-DaHall 1-B-3-35-52 | 48 | 35 | A-3 | 53 | 48 | 35 | B-3 | 52 | IPD A-3-53 / 35A | IPD B-3-52 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B316 | 419 BAY | Sejong Telecom Inc. |  |  | ○ | 7-1-A-2-35-52 | 7-1-B-2-35-52 | 7-DaHall 1-A-2-35-52 | 7-DaHall 1-B-2-35-52 | 48 | 35 | A-2 | 52 | 48 | 35 | B-2 | 52 | IPD A-2-52 / 35A | IPD B-2-52 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | SKB장비
[5 empty] | ○ | [13 empty] | A: 1회로 사용(차단기 정보 조사 실패; 합계: 0 | 0 |  | 1회로. 차단기 정보 파악 불가
| B317 | 418 BAY | 418B_SKB장비 |  |  | ○ | 7-1-A-2-35-49 | 7-1-B-2-35-49 | 7-DaHall 1-A-2-35-49 | 7-DaHall 1-B-2-35-49 | 48 | 35 | A-2 | 49 | 48 | 35 | B-2 | 49 | IPD A-2-49 / 35A | IPD B-2-49 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | SKB장비
| B319 | 416 BAY | 416B_Patch |  | X | X | [31 empty] | 0 | 7F-5F OJC PATCH
| B320 | 415 BAY | 415B_Patch |  | X | X | [31 empty] | 0 | 7F-5F OJC PATCH
| B322 | 414 BAY | 414B_드림라인 |  |  | ○ | 7-1-A-2-35-10 | 7-1-B-2-35-10 | 7-DaHall 1-A-2-35-10 | 7-DaHall 1-B-2-35-10 | 48 | 35 | A-2 | 10 | 48 | 35 | B-2 | 10 | IPD A-2-10 / 35A | IPD B-2-10 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | 드림라인 장비
| B323 | 413 BAY | Sejong Telecom Inc. |  | ○ | [13 empty] | A: U3-7A-08 / 2P 30A (405Bay 인출) | 0 | 7F-5F UTP PATCH | 405Bay에서 1회로 연결 사용 중
| B402 | 331 BAY | 코위버 ROADM |  |  | ○ | 7-1-A-3-100-60 | 7-1-B-3-100-60 | 7-DaHall 1-A-3-100-60 | 7-DaHall 1-B-3-100-60 | 48 | 100 | A-3 | 60 | 48 | 100 | B-3 | 60 | IPD A-3-60 / 100A | IPD B-3-60 / 100A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 |  | 2022.02.10 전기구성
| B403 | 330 BAY | 코위버 ROADM |  |  | ○ | 7-1-A-3-100-28 | 7-1-B-3-100-28 | 7-DaHall 1-A-3-100-28 | 7-DaHall 1-B-3-100-28 | 48 | 100 | A-3 | 28 | 48 | 100 | B-3 | 28 | IPD A-3-28 / 100A | IPD B-3-28 / 100A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 |  | 2022.02.10 전기구성
| B404 | 329 BAY | 329B_ZTE385 |  |  | ○ | 7-1-A-3-50-15 | 7-1-B-3-50-15 | 7-DaHall 1-A-3-50-15 | 7-DaHall 1-B-3-50-15 | 48 | 50 | A-3 | 15 | 48 | 50 | B-3 | 15 | IPD A-3-15 / 50A | IPD B-3-15 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B405 | 328 BAY | 328B_ZTE385 |  |  | ○ | 7-1-A-3-50-16 | 7-1-B-3-50-16 | 7-DaHall 1-A-3-50-16 | 7-DaHall 1-B-3-50-16 | 48 | 50 | A-3 | 16 | 48 | 50 | B-3 | 16 | IPD A-3-16 / 50A | IPD B-3-16 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B406 | 327 BAY | 327B_ZTE385 |  |  | ○ | 7-1-A-3-50-17 | 7-1-B-3-50-17 | 7-DaHall 1-A-3-50-17 | 7-DaHall 1-B-3-50-17 | 48 | 50 | A-3 | 17 | 48 | 50 | B-3 | 17 | IPD A-3-17 / 50A | IPD B-3-17 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B407 | 326 BAY | 326B_코위버1664 |  |  | ○ | 7-1-A-3-35-23 | 7-1-B-3-35-24 | 7-DaHall 1-A-3-35-23 | 7-DaHall 1-B-3-35-24 | 48 | 35 | A-3 | 23 | 48 | 35 | B-3 | 24 | IPD A-3-23 / 35A | IPD B-3-24 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B408 | 325 BAY | 325B_코위버CWDM |  |  | ○ | 7-1-A-3-100-59 | 7-1-B-3-100-59 | 7-DaHall 1-A-3-100-59 | 7-DaHall 1-B-3-100-59 | 48 | 100 | A-3 | 59 | 48 | 100 | B-3 | 59 | IPD A-3-59 / 100A | IPD B-3-59 / 100A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 |  | 2012.02.09 설치
| B409 | 324 BAY | [16 empty] | A: TR-7A 1000kVA | 0
| B410 | 323 BAY |  |  |  | ○ | [12 empty] | A: TR-7A 1000kVA | 0
| B411 | 322 BAY | Sejong Telecom Inc. |  | ○ |  | 7-1-A2-30-29 |  | 7-DaHall 1-PDU-01-30-29 |  | 220 | 30 | PDU-01 | 29 |  |  |  |  | A: U3-7A-29 / 2P 30A; A: U3-7A (U7-5A) 4P 300A; A: LV-7A #05 / 3P 320A (U7-5A); A: TR-7A 1000kVA; A전원: 0.12754; 합계: 0.12754; A전원: 3.5 | 3.5 | PTN 7200 UTP PATCH 예정
| B415 | [36 empty] | 0 | bar: A to B; A전원 to B전원
| B416 | 318 BAY | Digital Edge | 2.2 | ○ |  | 7-1-A2-30-18 | 7-1-B2-30-18 | 7-DaHall 1-PDU-01-30-18 | 7-DaHall 1-PDU-02-30-18 | 220 | 30 | PDU-01 | 18 | 220 | 30 | PDU-02 | 18 | U3-7A-18 / 2P 30A | U3-7B-18 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.7001 | 2.6467 | 5.3468 | 265 | 263 | 528 | 전기투입 : '22.02.24 | DEKR Networks Cabinet('22.02.09)
| B417 | 317 BAY | Digital Edge | 2.2 | ○ |  | 7-1-A2-30-20 | 7-1-B2-30-20 | 7-DaHall 1-PDU-01-30-20 | 7-DaHall 1-PDU-02-30-20 | 220 | 30 | PDU-01 | 20 | 220 | 30 | PDU-02 | 20 | U3-7A-20 / 2P 30A | U3-7B-20 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.7184 | 1.9609 | 3.6794 | 280.7 | 301.1 | 581.8 | 전기투입 : '22.02.24 | DEKR Networks Cabinet('22.02.09)
| B418 | 316 BAY | Digital Edge | 2.2 | ○ |  | 7-1-A2-30-22 | 7-1-B2-30-22 | 7-DaHall 1-PDU-01-30-22 | 7-DaHall 1-PDU-02-30-22 | 220 | 30 | PDU-01 | 22 | 220 | 30 | PDU-02 | 22 | U3-7A-22 / 2P 30A | U3-7B-22 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.6897 | 1.9178 | 3.6075 | 258.6 | 296.8 | 555.4 | 전기투입 : '22.02.24 | DEKR Networks Cabinet('22.02.09)
| B419 | 315 BAY | Digital Edge | 2.2 | ○ |  | 7-1-A2-30-24 | 7-1-B2-30-24 | 7-DaHall 1-PDU-01-30-24 | 7-DaHall 1-PDU-02-30-24 | 220 | 30 | PDU-01 | 24 | 220 | 30 | PDU-02 | 24 | U3-7A-24 / 2P 30A | U3-7B-24 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.65 | 2.2107 | 4.8607 | 408 | 329.4 | 737.4 | 전기투입 : '22.02.24 | DEKR Networks Cabinet('22.02.09)
| B420 | 314 BAY | Digital Edge | 2.2 | ○ |  | 7-1-A2-30-26 | 7-1-B2-30-26 | 7-DaHall 1-PDU-01-30-26 | 7-DaHall 1-PDU-02-30-26 | 220 | 30 | PDU-01 | 26 | 220 | 30 | PDU-02 | 26 | U3-7A-26 / 2P 30A | U3-7B-26 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 3.3292 | 3.0434 | 6.3726 | 502.1 | 537 | 1039.1 | 전기투입 : '22.02.24 | DEKR Networks Cabinet('22.02.09)
| B421 | 313 BAY | Digital Edge | 2.2 | ○ |  | 7-1-A2-30-28 | 7-1-B2-30-28 | 7-DaHall 1-PDU-01-30-28 | 7-DaHall 1-PDU-02-30-28 | 220 | 30 | PDU-01 | 28 | 220 | 30 | PDU-02 | 28 | U3-7A-28 / 2P 30A | U3-7B-28 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 5.4264 | 5.6621 | 11.0885 | 811.8 | 855.5 | 1667.3 | 전기투입 : '22.02.24 | DEKR Networks Cabinet('22.02.09)
| B422 | 312 BAY | Digital Edge | 2.2 | ○ |  | 7-1-A2-30-40 | 7-1-B2-30-40 | 7-DaHall 1-PDU-01- 30AT-40 | 7-DaHall 1-PDU-02- 30AT-40 | 220V | 30AT | PDU-01 | 40 | 220V | 30AT | PDU-02 | 40 | A: U3-7A(U7-5A) 4P 300A; B: U3-7B(U7-6B) 4P 300A; A: LV-7A #05 / 3P 320A (U7-5A); B: LV-7B #06 / 3P 320A (U7-6B); A: TR-7A 1000kVA; B: TR-7B 1000kVA; A전원: 3.3337; B전원: 3.0971; 합계: 6.4308; A전원: 455.6; B전원: 422 | 877.6
| B423 | 311 BAY | Digital Edge | 2.2 | ○ |  | 7-1-A2-30-38 | 7-1-B2-30-38 | 7-DaHall 1-PDU-01- 30AT-38 | 7-DaHall 1-PDU-02- 30AT-38 | 220V | 30AT | PDU-01 | 38 | 220V | 30AT | PDU-02 | 38 | A: U3-7A(U7-5A) 4P 300A; B: U3-7B(U7-6B) 4P 300A; A: LV-7A #05 / 3P 320A (U7-5A); B: LV-7B #06 / 3P 320A (U7-6B); A: TR-7A 1000kVA; B: TR-7B 1000kVA; A전원: 2.6066; B전원: 3.5214; 합계: 6.128; A전원: 380.7; B전원: 529.7 | 910.4
| B424 |  |  | 2.2 | ○ |  | 7-1-A2-30-36 | 7-1-B2-30-36 | 7-DaHall 1-PDU-01- 30AT-36 | 7-DaHall 1-PDU-02- 30AT-36 | 220V | 30AT | PDU-01 | 36 | 220V | 30AT | PDU-02 | 36 | A: U3-7A(U7-5A) 4P 300A; B: U3-7B(U7-6B) 4P 300A; A: LV-7A #05 / 3P 320A (U7-5A); B: LV-7B #06 / 3P 320A (U7-6B); A: TR-7A 1000kVA; B: TR-7B 1000kVA; A전원: 1.6549; B전원: 1.6451; 합계: 3.3; A전원: 0; B전원: 0 | 0
| B502 | 231 BAY | 231B_ZTE385 |  |  | ○ | 7-1-A-3-35-22 | 7-1-B-3-35-22 | 7-DaHall 1-A-3-35-22 | 7-DaHall 1-B-3-35-22 | 48 | 35 | A-3 | 22 | 48 | 35 | B-3 | 22 | IPD A-3-22 / 35A | IPD B-3-22 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B503 | 230 BAY | 230B_ZTE385 |  |  | ○ | 7-1-A-3-35-51 | 7-1-B-3-35-51 | 7-DaHall 1-A-3-35-51 | 7-DaHall 1-B-3-35-51 | 48 | 35 | A-3 | 51 | 48 | 35 | B-3 | 51 | IPD A-3-51 / 35A | IPD B-3-51 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B504 | 229 BAY | 229B_ZTE385 |  |  | ○ | 7-1-A-3-35-50 | 7-1-B-3-35-50 | 7-DaHall 1-A-3-35-50 | 7-DaHall 1-B-3-35-50 | 48 | 35 | A-3 | 50 | 48 | 35 | B-3 | 50 | IPD A-3-50 / 35A | IPD B-3-50 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B505 | 228 BAY | 228B_ZTE385 |  |  | ○ | 7-1-A-3-50-49 | 7-1-B-3-35-49 | 7-DaHall 1-A-3-50-49 | 7-DaHall 1-B-3-35-49 | 48 | 50 | A-3 | 49 | 48 | 35 | B-3 | 49 | IPD A-3-49 / 50A | IPD B-3-49 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B506 | 227 BAY | 227B_ZTE385 |  |  | ○ | 7-1-A-3-50-21 | 7-1-B-3-50-21 | 7-DaHall 1-A-3-50-21 | 7-DaHall 1-B-3-50-21 | 48 | 50 | A-3 | 21 | 48 | 50 | B-3 | 21 | IPD A-3-21 / 50A | IPD B-3-21 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B507 | 226 BAY | 226B_코위버155M |  |  | ○ | 7-1-A-3-35-20 | 7-1-B-3-50-20 | 7-DaHall 1-A-3-35-20 | 7-DaHall 1-B-3-50-20 | 48 | 35 | A-3 | 20 | 48 | 50 | B-3 | 20 | IPD A-3-20 / 35A | IPD B-3-20 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B508 | 225 BAY | 225B_코위버622M |  |  | ○ | 7-1-A-3-35-52 | 7-1-B-3-35-23 | 7-DaHall 1-A-3-35-52 | 7-DaHall 1-B-3-35-23 | 48 | 35 | A-3 | 52 | 48 | 35 | B-3 | 23 | IPD A-3-52 / 35A | IPD B-3-23 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 |  | PDP 2개
[6 empty] | ○ | 7-1-A-3-35-55 | 7-1-B-3-35-54 | 7-DaHall 1-A-3-35-55 | 7-DaHall 1-B-3-35-54 | 48 | 35 | A-3 | 55 | 48 | 35 | B-3 | 54 | IPD A-3-55 / 35A | IPD B-3-54 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B509 | 224 BAY | 224B_우리넷 |  |  | ○ | 7-1-A-3-35-19 | 7-1-B-3-50-19 | 7-DaHall 1-A-3-35-19 | 7-DaHall 1-B-3-50-19 | 48 | 35 | A-3 | 19 | 48 | 50 | B-3 | 19 | IPD A-3-19 / 35A | IPD B-3-19 / 50A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B510 | 223 BAY | 223B_코위버155M |  |  | ○ | 7-1-A-3-35-18 | 7-1-B-3-35-18 | 7-DaHall 1-A-3-35-18 | 7-DaHall 1-B-3-35-18 | 48 | 35 | A-3 | 18 | 48 | 35 | B-3 | 18 | IPD A-3-18 / 35A | IPD B-3-18 / 35A | IPD A-3 | IPD B-3 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B515 | 219 BAY | 219B_코위버PTN |  |  | ○ | 7-1-A-2-50-22 | 7-1-B-2-50-22 | 7-DaHall 1-A-2-50-22 | 7-DaHall 1-B-2-50-22 | 48 | 50 | A-2 | 22 | 48 | 50 | B-2 | 22 | IPD A-2-22 / 50A | IPD B-2-22 / 50A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B516 | 218 BAY | DEKR, Network Rack#2 | 2.2 | ○ |  | 7-1-A2-30-14 | 7-1-B2-30-14 | 7-DaHall 1-PDU-01-30-14 | 7-DaHall 1-PDU-02-30-14 | 220 | 30 | PDU-01 | 14 | 220 | 30 | PDU-02 | 14 | U3-7A-14 / 2P 30A | U3-7B-14 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 4.0892 | 3.2196 | 7.3088 | 644.4 | 351.1 | 995.5 |  | 2022.01.12 전기투입
| B517 | 217 BAY | DEKR, Network Rack#1 | 2.2 | ○ |  | 7-1-A2-30-16 | 7-1-B2-30-16 | 7-DaHall 1-PDU-01-30-16 | 7-DaHall 1-PDU-02-30-16 | 220 | 30 | PDU-01 | 16 | 220 | 30 | PDU-02 | 16 | U3-7A-16 / 2P 30A | U3-7B-16 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.7079 | 3.0965 | 5.8044 | 320.2 | 392.5 | 712.7 |  | 2022.01.12 전기투입
|  | 216 BAY | [16 empty] | A: TR-7A 1000kVA; B: TR-7B 1000kVA | 0
|  | 215 BAY | [16 empty] | A: TR-7A 1000kVA; B: TR-7B 1000kVA | 0
|  | 214 BAY | [16 empty] | A: TR-7A 1000kVA; B: TR-7B 1000kVA | 0
|  | 213 BAY | [16 empty] | A: TR-7A 1000kVA; B: TR-7B 1000kVA | 0
| B524 | 212 BAY | 212B_코위버155M |  |  | ○ | 7-1-A-2-50-12 | 7-1-B-2-50-12 | 7-DaHall 1-A-2-50-12 | 7-DaHall 1-B-2-50-12 | 48 | 50 | A-2 | 12 | 48 | 50 | B-2 | 12 | IPD A-2-12 / 50A | IPD B-2-12 / 50A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
1열 | B615 | 121 BAY | 121B_ZTE325 |  |  | ○ | 7-1-A-2-50-66 | 7-1-B-2-50-66 | 7-DaHall 1-A-2-50-66 | 7-DaHall 1-B-2-50-66 | 48 | 50 | A-2 | 66 | 48 | 50 | B-2 | 66 | IPD A-2-66 / 50A | IPD B-2-66 / 50A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B616 | 120 BAY | 120B_ZTE325 |  |  | ○ | 7-1-A-2-50-67 | 7-1-B-2-50-67 | 7-DaHall 1-A-2-50-67 | 7-DaHall 1-B-2-50-67 | 48 | 50 | A-2 | 67 | 48 | 50 | B-2 | 67 | IPD A-2-67 / 50A | IPD B-2-67 / 50A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B617 | 119 BAY | 119B_우리넷 |  |  | ○ | 7-1-A-2-35-65 | 7-1-B-2-35-65 | 7-DaHall 1-A-2-35-65 | 7-DaHall 1-B-2-35-65 | 48 | 35 | A-2 | 65 | 48 | 35 | B-2 | 65 | IPD A-2-65 / 35A | IPD B-2-65 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B618 | 118 BAY | 118B_ZTE385 |  |  | ○ | 7-1-A-2-50-64 | 7-1-B-2-50-64 | 7-DaHall 1-A-2-50-64 | 7-DaHall 1-B-2-50-64 | 48 | 50 | A-2 | 64 | 48 | 50 | B-2 | 64 | IPD A-2-64 / 50A | IPD B-2-64 / 50A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B619 | 117 BAY | 117B_ZTE385 |  |  | ○ | 7-1-A-2-35-60 | 7-1-B-2-35-60 | 7-DaHall 1-A-2-35-60 | 7-DaHall 1-B-2-35-60 | 48 | 35 | A-2 | 60 | 48 | 35 | B-2 | 60 | IPD A-2-60 / 35A | IPD B-2-60 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B620 | 116 BAY | 116B_ZTE385 |  |  | ○ | 7-1-A-2-35-61 | 7-1-B-2-35-61 | 7-DaHall 1-A-2-35-61 | 7-DaHall 1-B-2-35-61 | 48 | 35 | A-2 | 61 | 48 | 35 | B-2 | 61 | IPD A-2-61 / 35A | IPD B-2-61 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B621 | 115 BAY | 115B_ZTE325 |  |  | ○ | 7-1-A-2-35-59 | 7-1-B-2-35-59 | 7-DaHall 1-A-2-35-59 | 7-DaHall 1-B-2-35-59 | 48 | 35 | A-2 | 59 | 48 | 35 | B-2 | 59 | IPD A-2-59 / 35A | IPD B-2-59 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B622 | 114 BAY | 114B_ZTE325 |  |  | ○ | 7-1-A-2-35-56 | 7-1-B-2-35-56 | 7-DaHall 1-A-2-35-56 | 7-DaHall 1-B-2-35-56 | 48 | 35 | A-2 | 56 | 48 | 35 | B-2 | 56 | IPD A-2-56 / 35A | IPD B-2-56 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B623 | 113 BAY | 113B_ZTE325 |  |  | ○ | 7-1-A-2-35-55 | 7-1-B-2-35-55 | 7-DaHall 1-A-2-35-55 | 7-DaHall 1-B-2-35-55 | 48 | 35 | A-2 | 55 | 48 | 35 | B-2 | 55 | IPD A-2-55 / 35A | IPD B-2-55 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B624 | 112 BAY | 112B_ZTE325 |  |  | ○ | 7-1-A-2-35-54 | 7-1-B-2-35-54 | 7-DaHall 1-A-2-35-54 | 7-DaHall 1-B-2-35-54 | 48 | 35 | A-2 | 54 | 48 | 35 | B-2 | 54 | IPD A-2-54 / 35A | IPD B-2-54 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| B625 | 111 BAY | 111B_ZTE325 |  |  | ○ | 7-1-A-2-35-57 | 7-1-B-2-35-57 | 7-DaHall 1-A-2-35-57 | 7-DaHall 1-B-2-35-57 | 48 | 35 | A-2 | 57 | 48 | 35 | B-2 | 57 | IPD A-2-57 / 35A | IPD B-2-57 / 35A | IPD A-2 | IPD B-2 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
|  | 508 BAY | [35 empty] | 0
| C104 | 507 BAY | Sejong Telecom Inc. |  |  | ○ | 7-1-A-1-50-20 | 7-1-B-1-50-20 | 7-DaHall 1-A-1-50-20 | 7-DaHall 1-B-1-50-20 | 48 | 50 | A-1 | 20 | 48 | 50 | B-1 | 20 | IPD A-1-20 / 50A | IPD B-1-20 / 50A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | SKB장비
|  |  |  | 2.2 | ○ | [13 empty] | A: 미상(A-E1 ??); B: 미상(UPS분전반(B) / E-20 ??); 합계: 0 | 0 |  | 랙 상부 위치 / 미사용 전원
| C105 | 506 BAY | 506B_KT장비 |  |  | ○ | 7-1-A-1-35-11(1) | 7-1-B-1-35-14(1) | 7-DaHall 1-A-1-35-11(1) | 7-DaHall 1-B-1-35-14(1) | 48 | 35 | A-1 | 11(1) | 48 | 35 | B-1 | 14(1) | IPD A-1-11(1) / 35A | IPD B-1-14(1) / 35A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | KT장비 | PDP 2개
[6 empty] | ○ | 7-1-A-1-35-15(2) | 7-1-B-1-35-15(2) | 7-DaHall 1-A-1-35-15(2) | 7-DaHall 1-B-1-35-15(2) | 48 | 35 | A-1 | 15(2) | 48 | 35 | B-1 | 15(2) | IPD A-1-15(2) / 35A | IPD B-1-15(2) / 35A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
|  | 505 BAY | [35 empty] | 0
| C107 | 504 BAY | 504B_KT장비 |  |  | ○ | 7-1-B-1-35-16 | 7-1-A-1-35-16 | 7-DaHall 1-B-1-35-16 | 7-DaHall 1-A-1-35-16 | 48 | 35 | B-1 | 16 | 48 | 35 | A-1 | 16 | IPD B-1-16 / 35A | IPD A-1-16 / 35A | IPD B-1 | IPD A-1 | 정류기 B -48V 1400A | 정류기 A -48V 1400A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | [5 empty] | 0 | KT장비
| C108 | 503 BAY | 503B_KT장비 |  |  | ○ | 7-1-A-1-50-17 | 7-1-B-1-50-17 | 7-DaHall 1-A-1-50-17 | 7-DaHall 1-B-1-50-17 | 48 | 50 | A-1 | 17 | 48 | 50 | B-1 | 17 | IPD A-1-17 / 50A | IPD B-1-17 / 50A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | KT장비
| C109 | 502 BAY | 502B_KT장비 |  |  | ○ | 7-1-A-1-50-56 | 7-1-B-1-50-56 | 7-DaHall 1-A-1-50-56 | 7-DaHall 1-B-1-50-56 | 48 | 50 | A-1 | 56 | 48 | 50 | B-1 | 56 | IPD A-1-56 / 50A | IPD B-1-56 / 50A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | KT장비
5열 | C110 | 501 BAY | 501B_LGU+장비 |  |  | ○ | 7-1-A-1-100-19 | 7-1-B-1-100-19 | 7-DaHall 1-A-1-100-19 | 7-DaHall 1-B-1-100-19 | 48 | 100 | A-1 | 19 | 48 | 100 | B-1 | 19 | IPD A-1-19 / 100A | IPD B-1-19 / 100A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | LGU+장비
| C201 | 410 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A1-30-32 | 7-1-B1-30-26 | 7-DaHall 1-RPP-01-30-32 | 7-DaHall 1-RPP-02-30-26 | 220 | 30 | RPP-01 | 32 | 220 | 30 | RPP-02 | 26 | UPS A1-32 / 2P 30A | UPS B1-26 / 2P 30A | UPS 출력분전반 A1 #32 | UPS 출력분전반 B1 #26 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 0 | 1.2034 | 1.2034 | 0 | 27.4 | 27.4 | PBX 교환기
| C202 | 409 BAY | Sejong Telecom Inc. | 1.6 | ○ | [13 empty] | A: UPS A1-12 / 2P 30A (408Bay 인출); B: UPS B1-17 / 2P 20A (408Bay 인출) | 0 |  | 408Bay에서 멀티탭 2개 연결 사용 중
| C203 | 408 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A1-30-12 | 7-1-B1-20-17 | 7-DaHall 1-RPP-01-30-12 | 7-DaHall 1-RPP-02-20-17 | 220 | 30 | RPP-01 | 12 | 220 | 20 | RPP-02 | 17 | UPS A1-12 / 2P 30A | UPS B1-17 / 2P 20A | UPS 출력분전반 A1 #12 | UPS 출력분전반 B1 #17 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 3.5739 | 3.1283 | 6.7022 | 571.8 | 430.7 | 1002.5
| C204 | 407 BAY | Sejong Telecom Inc. |  |  | ○ | 7-1-A-1-35-44 | 7-1-B-1-35-6 | 7-DaHall 1-A-1-35-44 | 7-DaHall 1-B-1-35-6 | 48 | 35 | A-1 | 44 | 48 | 35 | B-1 | 6 | IPD A-1-44 / 35A | IPD B-1-06 / 35A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
|  |  |  | 1.6 | ○ |  | 7-1-A1-30-10 | 7-1-B1-20-15 | 7-DaHall 1-RPP-01-30-10 | 7-DaHall 1-RPP-02-20-15 | 220 | 30 | RPP-01 | 10 | 220 | 20 | RPP-02 | 15 | UPS A1-10 / 2P 30A | UPS B1-15 / 2P 20A | UPS 출력분전반 A1 #10 | UPS 출력분전반 B1 #15 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.5543 | 1.7234 | 3.2777 | 232.1 | 261.9 | 494
| C205 | 406 BAY | Sejong Telecom Inc. |  |  | ○ | 7-1-A-1-35-43 | 7-1-B-1-35-5 | 7-DaHall 1-A-1-35-43 | 7-DaHall 1-B-1-35-5 | 48 | 35 | A-1 | 43 | 48 | 35 | B-1 | 5 | IPD A-1-43 / 35A | IPD B-1-05 / 35A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
|  |  |  | 1.6 | ○ |  | 7-1-A1-30-8 | 7-1-B1-20-13 | 7-DaHall 1-RPP-01-30-8 | 7-DaHall 1-RPP-02-20-13 | 220 | 30 | RPP-01 | 8 | 220 | 20 | RPP-02 | 13 | UPS A1-08 / 2P 30A | UPS B1-13 / 2P 20A | UPS 출력분전반 A1 #08 | UPS 출력분전반 B1 #13 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.295 | 2.7752 | 5.0701 | 319.5 | 379.8 | 699.3
| C206 | 405 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-B1-20-9 | 7-1-A2-30-8 | 7-DaHall 1-PDU-01-30-8 | 7-DaHall 1-RPP-02-20-9 | 220 | 20 | RPP-02 | 9 | 220 | 30 | PDU-01 | 8 | UPS B1-09 / 2P 20A | U3-7A-08 / 2P 30A | UPS 출력분전반 B1 #09 |  | UPS 출력 분전반B1, 4P 400A |  | UPS 출력 분전반B, #02 3P 150A |  | UPS 출력 배전반B, 4P 400A | U3-7A(U7-5A) 4P 300A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #05 / 3P 320A (U7-5A) | TR-7B 1000kVA | TR-7A 1000kVA | 1.6519 | 1.4678 | 3.1197 | 261.8 | 173.6 | 435.4
| C207 | 404 BAY | Sejong Telecom Inc. | 1.6 | ○ | [13 empty] | B: 라벨 없음(B1 PNL에서 인출 추정); 합계: 0 | 0 | 인터넷팀 장비
4열 | C208 | 403 BAY | Sejong Telecom Inc. | 1.6 | ○ | [13 empty] | B: 라벨 없음(B1 PNL에서 인출 추정); 합계: 0 | 0 | 인터넷팀 장비
| C304 | 307 BAY | LGU+PDP |  |  | ○ | 7-1-A-1-100-24 | 7-1-B-1-100-24 | 7-DaHall 1-A-1-100-24 | 7-DaHall 1-B-1-100-24 | 48 | 100 | A-1 | 24 | 48 | 100 | B-1 | 24 | IPD A-1-24 / 100A | IPD B-1-24 / 100A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | LGU+ POP 장비
| C305 | 306 BAY | 306B_SKB장비 |  |  | ○ | 7-1-A-1-100-7 | 7-1-B-1-100-7 | 7-DaHall 1-A-1-100-7 | 7-DaHall 1-B-1-100-7 | 48 | 100 | A-1 | 7 | 48 | 100 | B-1 | 7 | IPD A-1-07 / 100A | IPD B-1-07 / 100A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | SKB장비
| C306 | 305 BAY | 305B_LGU+장비 |  |  | ○ | 7-1-A-1-50-57 | 7-1-B-1-50-57 | 7-DaHall 1-A-1-50-57 | 7-DaHall 1-B-1-50-57 | 48 | 50 | A-1 | 57 | 48 | 50 | B-1 | 57 | IPD A-1-57 / 50A | IPD B-1-57 / 50A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | LGU+장비
| C307 | 304 BAY | 304B_KT장비 |  |  | ○ | 7-1-A-1-50-21 | 7-1-B-1-50-21 | 7-DaHall 1-A-1-50-21 | 7-DaHall 1-B-1-50-21 | 48 | 50 | A-1 | 21 | 48 | 50 | B-1 | 21 | IPD A-1-21 / 50A | IPD B-1-21 / 50A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | KT장비
| C308 | 303 BAY | 303B_NDCS |  |  | ○ | 7-1-A-1-100-18 | 7-1-B-1-100-18 | 7-DaHall 1-A-1-100-18 | 7-DaHall 1-B-1-100-18 | 48 | 100 | A-1 | 18 | 48 | 100 | B-1 | 18 | IPD A-1-18 / 100A | IPD B-1-18 / 100A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
| C309 | 302 BAY | 302B_SKB |  |  | ○ | 7-1-A-1-100-23 | 7-1-B-1-100-23 | 7-DaHall 1-A-1-100-23 | 7-DaHall 1-B-1-100-23 | 48 | 100 | A-1 | 23 | 48 | 100 | B-1 | 23 | IPD A-1-23 / 100A | IPD B-1-23 / 100A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0
3열 | C310 | 301 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-30 | 7-1-B2-30-30 | 7-DaHall 1-PDU-01-30-30 | 7-DaHall 1-PDU-02-30-30 | 220 | 30 | PDU-01 | 30 | 220 | 30 | PDU-02 | 30 | U3-7A-30 / 2P 30A | U3-7B-30 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 0.34146 | 0.5586 | 0.90006 | 40.3 | 55.3 | 95.6
| C401 | 210 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-13 | 7-1-B2-30-13 | 7-DaHall 1-PDU-01-30-13 | 7-DaHall 1-PDU-02-30-13 | 220 | 30 | PDU-01 | 13 | 220 | 30 | PDU-02 | 13 | U3-7A-13 / 2P 30A | U3-7B-13 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 5.7529 | 4.6923 | 10.4452 | 1006.3 | 785.8 | 1792.1 | 인터넷팀 장비 | AC 콘센트 라벨 : 410Bay-A & 410Bay-B
| C402 | 209 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-11 | 7-1-B2-30-11 | 7-DaHall 1-PDU-01-30-11 | 7-DaHall 1-PDU-02-30-11 | 220 | 30 | PDU-01 | 11 | 220 | 30 | PDU-02 | 11 | U3-7A-11 / 2P 30A | U3-7B-11 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 6.3336 | 5.4275 | 11.7611 | 963.8 | 776.4 | 1740.2 | 인터넷팀 장비 | AC 콘센트 라벨 : 409Bay-A & 409Bay-B
| C403 | 208 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-17 | 7-1-B2-30-17 | 7-DaHall 1-PDU-01-30-17 | 7-DaHall 1-PDU-02-30-17 | 220 | 30 | PDU-01 | 17 | 220 | 30 | PDU-02 | 17 | U3-7A-17 / 2P 30A | U3-7B-17 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 3.9791 | 4.2887 | 14.5867 | 426.6 | 528.3 | 954.9 | 인터넷팀 장비
[5 empty] | ○ |  | 7-1-A2-30-27 | 7-1-B2-30-27 | 7-DaHall 1-PDU-01-30-27 | 7-DaHall 1-PDU-02-30-27 | 220 | 30 | PDU-01 | 27 | 220 | 30 | PDU-02 | 27 | U3-7A-27 / 2P 30A | U3-7B-27 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 3.2123 | 3.1066 |  | 514.6 | 573.2 | 1087.8
| C404 | 207 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-19 | 7-1-B2-30-19 | 7-DaHall 1-PDU-01-30-19 | 7-DaHall 1-PDU-02-30-19 | 220 | 30 | PDU-01 | 19 | 220 | 30 | PDU-02 | 19 | U3-7A-19 / 2P 30A | U3-7B-19 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 3.8195 | 8.6048 | 12.4243 | 580.6 | 1311.5 | 1892.1 | 인터넷팀 장비
| C405 | 206 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-21 | 7-1-B2-30-21 | 7-DaHall 1-PDU-01-30-21 | 7-DaHall 1-PDU-02-30-21 | 220 | 30 | PDU-01 | 21 | 220 | 30 | PDU-02 | 21 | U3-7A-21 / 2P 30A | U3-7B-21 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 3.462 | 4.0313 | 7.4932 | 601 | 621.5 | 1222.5 | 인터넷팀 장비
| C406 | 205 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-23 | 7-1-B2-30-23 | 7-DaHall 1-PDU-01-30-23 | 7-DaHall 1-PDU-02-30-23 | 220 | 30 | PDU-01 | 23 | 220 | 30 | PDU-02 | 23 | U3-7A-23 / 2P 30A | U3-7B-23 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.8628 | 2.6238 | 4.4866 | 282.5 | 395.8 | 678.3 | 인터넷팀 장비
| C407 | 204 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-25 | 7-1-B2-30-25 | 7-DaHall 1-PDU-01-30-25 | 7-DaHall 1-PDU-02-30-25 | 220 | 30 | PDU-01 | 25 | 220 | 30 | PDU-02 | 25 | U3-7A-25 / 2P 30A | U3-7B-25 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.9762 | 2.064 | 4.0402 | 304.5 | 334.6 | 639.1 | 인터넷팀 장비
| C408 | 203 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-32 | 7-1-B2-30-32 | 7-DaHall 1-PDU-01-30-32 | 7-DaHall 1-PDU-02-30-32 | 220 | 30 | PDU-01 | 32 | 220 | 30 | PDU-02 | 32 | U3-7A-32 / 2P 30A | U3-7B-32 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.205 | 2.1671 | 4.3721 | 283.7 | 236.8 | 520.5 | 세종 긴급청약 | 22.07.14 구성 및 전기투입
2열 | C409 | 202 BAY | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-41 | 7-1-B2-30-41 | 7-DaHall 1-PDU-01-30-41 | 7-DaHall 1-PDU-02-30-41 | 220 | 30 | PDU-01 | 41 | 220 | 30 | PDU-02 | 41 | U3-7A-32 / 2P 30A | U3-7B-32 / 2P 30A | [6 empty] | U3-7A (U7-5A) 4P 300A | U3-7B (U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.9029 | 5.4582 | 7.3611 | 123.8 | 0 | 123.8 |  | '23.07. 31 전기투입/세종요청 1랙 증설
G열 | C501 | G10 | Shinhan financial Investment | 1.1 | ○ |  | 7-1-A1-20-19 | 7-1-B1-30-10 | 7-DaHall 1-RPP-01-20-19 | 7-DaHall 1-RPP-02-30-10 | 220 | 20 | RPP-01 | 19 | 220 | 30 | RPP-02 | 10 | UPS A1-19 (A1-L-10) / 2P 20A | UPS B1-10 (B1-R-5) / 2P 30A | UPS 출력분전반 A1 #19 | UPS 출력분전반 B1 #10 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.7132 | 0.65395 | 2.3671 | 108.3 | 73.3 | 181.6 | IDC 고객 (신한금융투자)
| C502 | G09 | Quad Miner | 4 | ○ |  | 7-1-A2-30-44 | 7-1-B2-30-44 | 7-DaHall 1-PDU-01-30-44 | 7-DaHall 1-PDU-02-30-44 | 220 | 30 | PDU-01 | 44 | 220 | 30 | PDU-02 | 44 | U3-7A-44 / 2P 30A | U3-7B-44 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 5.6326 | 1.8154 | 7.448 | 866.9 | 223.6 | 1090.5 | 쿼드마이너('23.04.10 예정)
| C503 | G08 |  |  | ○ |  | 7-1-A2-30-2 | 7-1-B2-30-2 | 7-DaHall 1-PDU-01-30-2 | 7-DaHall 1-PDU-02-30-2 | 220 | 30 | PDU-01 | 2 | 220 | 30 | PDU-02 | 2 | U3-7A-02 / 2P 30A | U3-7B-02 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.2574 | 5.4828 | 7.7402 | 0 | 0 | 0 | 쿼드마이너(미정)
| C504 | G07 | 7F-G07 랙 |  |  | ○ | 7-1-A-1-35-50 | 7-1-B-1-50-47 | 7-DaHall 1-A-1-35-50 | 7-DaHall 1-B-1-50-47 | 48 | 35 | A-1 | 50 | 48 | 50 | B-1 | 47 | IPD A-1-50 / 35A | IPD B-1-47 / 50A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 |  | DC FUSE 제거/미사용
[5 empty] | ○ |  | 7-1-A2-30-46 | 7-1-B2-30-46 | 7-DaHall 1-PDU-01-30-46 | 7-DaHall 1-PDU-02-30-46 | 220 | 30 | PDU-01 | 46 | 220 | 30 | PDU-02 | 46 | U3-7A-46 / 2P 30A | U3-7B-46 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.6241 | 3.6165 | 6.2406 | 0 | 0 | 0 | 쿼드마이너(미정)
| C505 | G06 |  |  | ○ |  | 7-1-B1-30-18 | 7-1-A1-30-24 | 7-DaHall 1-RPP-01-30-24 | 7-DaHall 1-RPP-02-30-18 | 220 | 30 | RPP-02 | 18 | 220 | 30 | RPP-01 | 24 | UPS B1-18 / 2P 30A | UPS A1-24 / 2P 30A | UPS 출력분전반 B1 #18 | UPS 출력분전반 A1 #24 | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | 2.1344 | 2.4131 | 4.5475 | 0 | 0 | 0 | IDC 고객 (NTT #5)
| C506 | G05 |  |  | ○ |  | 7-1-B1-20-29 | 7-1-A1-20-33 | 7-DaHall 1-RPP-01-20-33 | 7-DaHall 1-RPP-02-20-29 | 220 | 20 | RPP-02 | 29 | 220 | 20 | RPP-01 | 33 | UPS B1-29 / 2P 20A | UPS A1-33 / 2P 20A | UPS 출력분전반 B1 #29 | UPS 출력분전반 A1 #33 | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | IDC 고객 (NTT #6)
| C507 | G04 |  |  | ○ |  | 7-1-B1-30-16 | 7-1-A1-30-22 | 7-DaHall 1-RPP-01-30-22 | 7-DaHall 1-RPP-02-30-16 | 220 | 30 | RPP-02 | 16 | 220 | 30 | RPP-01 | 22 | UPS B1-16 / 2P 30A | UPS A1-22 / 2P 30A | UPS 출력분전반 B1 #16 | UPS 출력분전반 A1 #22 | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | IDC 고객 (NTT #7)
| C508 | G03 |  |  | ○ |  | 7-1-A2-30-1 | 7-1-B2-30-1 | 7-DaHall 1-PDU-01-30-1 | 7-DaHall 1-PDU-02-30-1 | 220 | 30 | PDU-01 | 1 | 220 | 30 | PDU-02 | 1 | U3-7A-01 / 2P 30A | U3-7B-01 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | IDC 고객 (NTT #8)
[5 empty] | ○ |  | 7-1-A2-30-12 | 7-1-B2-30-12 | 7-DaHall 1-PDU-01-30-12 | 7-DaHall 1-PDU-02-30-12 | 220 | 30 | PDU-01 | 12 | 220 | 30 | PDU-02 | 12 | U3-7A-12 / 2P 30A | U3-7B-12 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA |  | 2.0299 | 2.6773 | 4.7072 | 0 | 0 | 0
| C509 | G02 | 7F-G02 랙 | [15 empty] | 합계: 0 | 0 | 미사용 랙 (빈 랙)
[19 empty] | B: TR-7B 1000kVA | 0 |  | AC 전원 철거
| C510 | G01 | 7F-G01 랙 | [15 empty] | 합계: 0 | 0 | LG HELLOVISION (빈 랙)
F열 | C601 | [36 empty] | 0
| C602 | F09 |  |  | ○ |  | 7-1-A1-20-39 | 7-1-B1-30-40 | 7-DaHall 1-RPP-01-20-39 | 7-DaHall 1-RPP-02-30-40 | 220 | 20 | RPP-01 | 39 | 220 | 30 | RPP-02 | 40 | UPS A1-39 / 2P 20A | UPS B1-40 / 2P 30A | UPS 출력분전반 A1 #39 | UPS 출력분전반 B1 #40 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.0833 | 0 | 2.0833 | 0 | 0 | 0 | 미사용 랙 (빈 랙) | C509, A회로 이설(12/7)
| C603 | F08 |  |  |  | ○ | 7-1-B-5-35-40 | 7-1-A-5-35-41 | 7-DaHall 1-B-5-35-40 | 7-DaHall 1-A-5-35-41 | 48 | 35 | B-5 | 40 | 48 | 35 | A-5 | 41 | IPD B-5-F40 (구 IPD A) / 35A | IPD A-5-F41 (구 IPD B) / 35A | IPD B-5 (구 IPD A) | IPD A-5 (구 IPD B) | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | 미사용 랙 (빈 랙) | DC FUSE 삽입상태 /DC PDP 미사용 중
[5 empty] | ○ |  | 7-1-A1-20-35 | 7-1-B1-30-34 | 7-DaHall 1-RPP-01-20-35 | 7-DaHall 1-RPP-02-30-34 | 220 | 20 | RPP-01 | 35 | 220 | 30 | RPP-02 | 34 | UPS A1-35 / 2P 20A | UPS B1-34 / 2P 30A | UPS 출력분전반 A1 #35 | UPS 출력분전반 B1 #34 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 |  | C510, A회로 이설(12/7)
| C604 | F07 | CARANG | 2.2 | ○ |  | 7-1-A1-30-18 | 7-1-B2-30-29 | 7-DaHall 1-RPP-01-30-18 | 7-DaHall 1-PDU-02-30-29 | 220 | 30 | RPP-01 | 18 | 220 | 30 | PDU-02 | 29 | UPS A1-18 / 2P 30A | U3-7B-29 / 2P 30A | UPS 출력분전반 A1 #18 |  | UPS 출력 분전반A1, 4P 400A |  | UPS 출력 분전반A, #01 4P 225A |  | UPS 출력 배전반A, 4P 400A | U3-7B(U7-6B) 4P 300A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.4665 | 1.8172 | 3.2838 | 198.3 | 0 | 198.3 | 미사용 랙 (빈 랙)
| C605 | F06 | Delphicom Co., Ltd. | 2.2 | ○ |  |  | 7-1-B1-30-36 |  | 7-DaHall 1-RPP-02-30-36 |  |  |  |  | 220 | 30 | RPP-02 | 36 | B: UPS B1-36 / 2P 30A; B: UPS 출력분전반 B1 #36; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 6.6171; 합계: 6.6171; B전원: 1054.4 | 1054.4 | IDC 고객 (델피콤)
| C606 | F05 | Delphicom Co., Ltd. | 1.1 | ○ |  | 7-1-A2-30-3 | 7-1-A1-30-16 | 7-DaHall 1-PDU-01-30-3 | 7-DaHall 1-RPP-01-30-16 | 220 | 30 | PDU-01 | 3 | 220 | 30 | RPP-01 | 16 | U3-7A-03 / 2P 30A | UPS A1-16 / 2P 30A |  | UPS 출력분전반 A1 #16 |  | UPS 출력 분전반A1, 4P 400A |  | UPS 출력 분전반A, #01 4P 225A | U3-7A(U7-5A) 4P 300A | UPS 출력 배전반A, 4P 400A | LV-7A #05 / 3P 320A (U7-5A) | LV-7A #06 / 3P 320A (U7-6A) | TR-7A 1000kVA |  | 2.954 | 3.2014 | 6.1553 | 329.6 | 223.2 | 552.8 | IDC 고객 (델피콤)
| C607 | F04 | Feather-IT | 2.2 | ○ |  | 7-1-A1-30-26 | 7-1-B1-30-20 | 7-DaHall 1-RPP-01-30-26 | 7-DaHall 1-RPP-02-30-20 | 220 | 30 | RPP-01 | 26 | 220 | 30 | RPP-02 | 20 | UPS A1-26 / 2P 30A | UPS B1-26 / 2P 30A | UPS 출력분전반 A1 #26 | UPS 출력분전반 B1 #20 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.137 | 2.7515 | 4.8885 | 198.3 | 323.7 | 522 | 2023.11.06 설치 (패더IT)
| C608 | F03 | 7F-F03 랙 | [34 empty] | 0 | bar: A; A to B전원
| C609 | F02 | 7F-F02 랙 |  |  | ○ | [12 empty] | IPD A-1-52 | IPD B-1-52 | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | IDC 고객 (NTT) | DC FUSE 제거/미사용(2021.01.19)
| C610 | F01 | 7F-F01 랙 |  |  | ○ | 7-1-A-1-35-51 | 7-1-B-1-35-51 | 7-DaHall 1-A-1-35-51 | 7-DaHall 1-B-1-35-51 | 48 | 35 | A-1 | 51 | 48 | 35 | B-1 | 51 | IPD A-1-51 / 35A | IPD B-1-51 / 35A | IPD A-1 | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | IDC 고객 (NTT)
E열 | C701 | [36 empty] | 0
| C702 | E09 | eBID | 2.2 | ○ |  | 7-1-B1-30-30 | 7-1-A1--36 | 7-DaHall 1-RPP-01--36 | 7-DaHall 1-RPP-02-30-30 | 220 | 30 | RPP-02 | 30 |  |  | RPP-01 | 36 | UPS B1-30 / 2P 30A | UPS A1-36 / 2P 30A | UPS 출력분전반 B1 #30 | UPS 출력분전반 A1 #36 | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | 3.4252 | 1.8933 | 5.3185 | 518.2 | 273.2 | 791.4 | IDC 고객 (르네트)
| C703 | E08 | Exanet | 0.55 | ○ |  | 7-1-B1-20-27 | 7-1-A1-30-14 | 7-DaHall 1-RPP-01-30-14 | 7-DaHall 1-RPP-02-20-27 | 220 | 20 | RPP-02 | 27 | 220 | 30 | RPP-01 | 14 | UPS B1-27 / 2P 20A | UPS A1-14 / 2P 30A | UPS 출력분전반 B1 #27 | UPS 출력분전반 A1 #14 | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | 5.8455 | 7.3389 | 13.1844 | 955.4 | 861.1 | 1816.5 | IDC 고객 (엑사넷)
| C704 | E07 |  |  | ○ |  |  | 7-1-B1-20-25 |  | 7-DaHall 1-RPP-02-20-25 |  |  |  |  | 220 | 20 | RPP-02 | 25 | B: UPS B1-25 / 2P 20A; B: UPS 출력분전반 B1 #25; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 0.62625; 합계: 0.62625; B전원: 0 | 0 | 미사용 랙 (빈 랙)
| C705 | E06 |  |  | ○ |  |  | 7-1-B1-20-23 |  | 7-DaHall 1-RPP-02-20-23 |  |  |  |  | 220 | 20 | RPP-02 | 23 | B: UPS B1-23 / 2P 20A; B: UPS 출력분전반 B1 #23; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 0; 합계: 0; B전원: 0 | 0 | 미사용 랙 (빈 랙)
| C706 | E05 |  |  | ○ |  |  | 7-1-B1-20-21 |  | 7-DaHall 1-RPP-02-20-21 |  |  |  |  | 220 | 20 | RPP-02 | 21 | B: UPS B1-21 / 2P 20A; B: UPS 출력분전반 B1 #21; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 1.5628; 합계: 1.5628; B전원: 0 | 0 | IDC 고객 (니즈텔레콤)
| C707 | E04 | Net People Co., Ltd. | 2.2 | ○ |  | 7-1-A1-30-4 |  | 7-DaHall 1-RPP-01-30-4 |  | 220 | 30 | RPP-01 | 4 |  |  |  |  | A: UPS A1-04 / 2P 30A; A: UPS 출력분전반 A1 #04; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 0 | 0 | IDC 고객 (넷피플)
| C708 | E03 |  |  | ○ |  | 7-1-A1-30-6 |  | 7-DaHall 1-RPP-01-30-6 |  | 220 | 30 | RPP-01 | 6 |  |  |  |  | A: UPS A1-06 / 2P 30A; A: UPS 출력분전반 A1 #06; A전원: 0; 합계: 0; A전원: 0 | 0 | IDC 고객 (넷피플)
| C709 | E02 |  |  | ○ |  |  | 7-1-B1-20-19 |  | 7-DaHall 1-RPP-02-20-19 |  |  |  |  | 220 | 20 | RPP-02 | 19 | B: UPS B1-19 / 2P 20A; B: UPS 출력분전반 B1 #19; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 5.5701; 합계: 5.5701; B전원: 0 | 0 | 미사용 랙 (빈 랙)
| C710 | E01 | 7F-E01 랙 |  | X | X | [31 empty] | 0 | IDC / 압류장비
D열 | C801 | [36 empty] | 0
| C802 | D07 | Needs Telecom |  | ○ |  |  | 7-1-A1-20-11 | 7-DaHall 1-RPP-01-20-11 | [5 empty] | 220 | 20 | RPP-01 | 11 | B: UPS A1-11 / 2P 20A; B: UPS 출력분전반 A1 #11; B: UPS 출력 분전반A1, 4P 400A; B: UPS 출력 분전반A, #01 4P 225A; B: UPS 출력 배전반A, 4P 400A; B: LV-7A #06 / 3P 320A (U7-6A); B: TR-7A 1000kVA; A전원: 0; 합계: 3.2696; A전원: 0 | 0 | IDC 고객 (니즈텔레콤) | 미사용 회로로 판단됨. 12월 계측시 0A면 삭제 예정
|  |  |  | 2.2 | ○ |  | 7-1-B1-30-32 | 7-1-A1-30-38 | 7-DaHall 1-RPP-01-30-38 | 7-DaHall 1-RPP-02-30-32 | 220 | 30 | RPP-02 | 32 | 220 | 30 | RPP-01 | 38 | UPS B1-32 / 2P 30A | UPS A1-38 / 2P 30A | UPS 출력분전반 B1 #32 | UPS 출력분전반 A1 #38 | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 분전반A, #01 4P 225A | UPS 출력분전반B 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | 2.4542 | 3.2696 |  | 310.2 | 530.1 | 840.3
| C803 | D06 |  |  | ○ |  | 7-1-B1-30-28 | 7-1-A1-30-34 | 7-DaHall 1-RPP-01-30-34 | 7-DaHall 1-RPP-02-30-28 | 220 | 30 | RPP-02 | 28 | 220 | 30 | RPP-01 | 34 | UPS B1-28 / 2P 30A | UPS A1-34 / 2P 30A | UPS 출력분전반 B1 #28 | UPS 출력분전반 A1 #14 | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B, #02 3P 150A | UPS 출력 분전반A, #01 4P 225A | UPS 출력분전반B 4P 400A | UPS 출력 배전반A, 4P 400A | LV-7B #07 / 3P 320A (U7-7B) | LV-7A #06 / 3P 320A (U7-6A) | TR-7B 1000kVA | TR-7A 1000kVA | 1.4248 | 0 | 1.4248 | 0 | 0 | 0 | IDC 고객 (??)
| C804 | D05 | NTT KOREA Co., Ltd. | 1.1 | ○ |  | 7-1-A2-30-6 | 7-1-B2-30-6 | 7-DaHall 1-PDU-01-30-6 | 7-DaHall 1-PDU-02-30-6 | 220 | 30 | PDU-01 | 6 | 220 | 30 | PDU-02 | 6 | U3-7A-06 / 2P 30A | U3-7B-06 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 6.3779 | 5.3234 | 12.2662 | 0 | 0 | 0 | IDC 고객 (NTT) | 미사용 회로. 랙 상부 방치 중(12/6 확인)
[7 empty] | 7-1-A2-30-54 | 7-1-B2-30-53 | 7-DaHall 1-PDU-01-30-54 | 7-DaHall 1-PDU-02-30-53 | 220 | 30 | PDU-01 | 54 | 220 | 30 | PDU-02 | 53 | A: U3-7A-54 / 2P 30A; B: U3-7B-53 / 2P 30A; A: U3-7A(U7-5A) 4P 300A; B: U3-7B(U7-6B) 4P 300A; A: LV-7A #05 / 3P 320A (U7-5A); B: LV-7B #06 / 3P 320A (U7-6B); A: TR-7A 1000kVA; B: TR-7B 1000kVA; A전원: 0.34024; B전원: 0.22466 | 0
| C805 | D04 | NTT KOREA Co., Ltd. | 1.1 | ○ |  | 7-1-A3-50-2 | 7-1-B3-50-2 | 7-DaHall 1-RPP-03-50-2 | 7-DaHall 1-RPP-04-50-2 | 220 | 50 | RPP-03 | 2 | 220 | 50 | RPP-04 | 2 | UPS A2-02 / 2P 50A | UPS B2-02 / 2P 50A | UPS 출력분전반 A2 #02 | UPS 출력분전반 B2 #01 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.3236 | 2.0054 | 3.329 | 137.8 | 242.6 | 380.4 | IDC 고객 (NTT_스미세이)
| C806 | D03 | UNSYS Co., Ltd. | 2.2 | ○ |  |  | 7-1-B1-30-14 |  | 7-DaHall 1-RPP-02-30-14 |  |  |  |  | 220 | 30 | RPP-02 | 14 | B: UPS B1-14 / 2P 30A; B: UPS 출력분전반 B1 #14; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 12.9108; 합계: 12.9108; B전원: 2175.5 | 2175.5 | IDC 고객 (유엔시스)
| C807 | D02 |  |  | ○ | [13 empty] | A: 1회로 구성(미사용), 차단기 파악 실패. A1 또는 B1 PNL 의심; 합계: 0 | 0 | IDC / 압류장비 | 1회로 구성(미사용)
| C808 | D01 |  |  | ○ |  | 7-1-A2-30-4 | 7-1-B2-30-4 | 7-DaHall 1-PDU-01-30-4 | 7-DaHall 1-PDU-02-30-4 | 220 | 30 | PDU-01 | 4 | 220 | 30 | PDU-02 | 4 | U3-7A-04 / 2P 30A | U3-7B-04 / 2P 30A | [6 empty] | U3-7A 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 5.6083 | 5.3789 | 10.9872 | 0 | 0 | 0 | 미사용 랙 (빈 랙)
|  | QDF | [35 empty] | 0
|  | QDF | [35 empty] | 0
C열 | C901 | [36 empty] | 0
| C902 | C08 | IT Train | 2.2 | ○ |  | 7-1-A1-20-23 | 7-1-B1-30-12 | 7-DaHall 1-RPP-01-20-23 | 7-DaHall 1-RPP-02-30-12 | 220 | 20 | RPP-01 | 23 | 220 | 30 | RPP-02 | 12 | UPS A1-23 / 2P 20A | UPS B1-12 / 2P 30A | UPS 출력분전반 A1 #23 | UPS 출력분전반 B1 #12 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력배전반A, 4P 400A | UPS 출력분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.4198 | 4.3444 | 5.7642 | 184.2 | 619.2 | 803.4 | IDC 고객(IT Train - 사조2차)
| C903 | C07 | IT Train | 2.2 | ○ |  | 7-1-A1-20-37 | 7-1-B1-30-8 | 7-DaHall 1-RPP-01-20-37 | 7-DaHall 1-RPP-02-30-8 | 220 | 20 | RPP-01 | 37 | 220 | 30 | RPP-02 | 8 | UPS A1-37 / 2P 20A | UPS B1-08 / 2P 30A | UPS 출력분전반 A1 #37 | UPS 출력분전반 B1 #08 | UPS 출력 분전반A1, 4P 400A | UPS 출력 분전반B1, 4P 400A | UPS 출력 분전반A, #01 4P 225A | UPS 출력 분전반B, #02 3P 150A | UPS 출력배전반A, 4P 400A | UPS 출력분전반B 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 4.639 | 3.7722 | 8.4112 | 678.9 | 592 | 1270.9 | IDC 고객(IT Train - 사조2차)
| C904 | C06 | IT Train | 2.2 | ○ |  | 7-1-A2-30-10 | 7-1-B2-30-10 | 7-DaHall 1-PDU-01-30-10 | 7-DaHall 1-PDU-02-30-10 | 220 | 30 | PDU-01 | 10 | 220 | 30 | PDU-02 | 10 | U3-7A-10 / 2P 30A | U3-7B-10 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U3-7A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.8402 | 4.3618 | 7.202 | 359.3 | 476.4 | 835.7 | IDC 고객(IT Train - 사조2차) |  | 10
| C905 |  | IT Train | 2.2 | ○ |  | 7-1-A2-30-42 | 7-1-B2-30-42 | 7-DaHall 1-PDU-01-30-42 | 7-DaHall 1-PDU-02-30-42 | 220 | 30 | PDU-01 | 42 | 220 | 30 | PDU-02 | 42 | U3-7A-42 / 2P 30A | U3-7B-42 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U3-7A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.8907 | 3.9346 | 6.8252 | 492.9 | 669.7 | 1162.6 | IDC 고객(IT Train - 사조2차)
| C907 | C04 | 7F-C04 랙 | [34 empty] | 0 | 미설치 (랙 없음)
| C908 | C03 | 7F-C03 랙 | [34 empty] | 0 | 미설치 (랙 없음)
| C909 | C02 | Sejong Telecom Inc. | 2.2 | ○ |  | 7-1-A2-30-34 | 7-1-B2-30-34 | 7-DaHall 1-PDU-01-30-34 | 7-DaHall 1-PDU-02-30-34 | 220 | 30 | PDU-01 | 34 | 220 | 30 | PDU-02 | 34 | U3-7A-34 / 2P 30A | U3-7B-34 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 4.0287 | 2.8911 | 6.9198 | 0 | 0 | 0 | IDC 고객(타타커뮤니케이션즈)
| C910 | C01 | Sejong Telecom Inc. |  |  | ○ | 7-1-B-5-100-48 | 7-1-B-1-100-41 | 7-DaHall 1-B-5-100-48 | 7-DaHall 1-B-1-100-41 | 48 | 100 | B-5 | 48 | 48 | 100 | B-1 | 41 | IPD B-5-F48 (구 IPD A) / 100A | IPD B-1-41 / 100A | IPD B-5 (구 IPD A) | IPD B-1 | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | IDC 고객(타타커뮤니케이션즈) | DC전원 장비직결
|  |  |  | 2.2 | ○ |  | 7-1-A2-30-15 | 7-1-B2-30-15 | 7-DaHall 1-PDU-01-30-15 | 7-DaHall 1-PDU-02-30-15 | 220 | 30 | PDU-01 | 15 | 220 | 30 | PDU-02 | 15 | U3-7A-15 / 2P 30A | U3-7B-15 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 0.7122 | 1.1919 | 1.9041 | 68.3 | 92.9 | 161.2
B열 | C1001 | [36 empty] | 0
| C1002 | B08 | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-35 | 7-1-B2-30-35 | 7-DaHall 1-PDU-01-30-35 | 7-DaHall 1-PDU-02-30-35 | 220 | 30 | PDU-01 | 35 | 220 | 30 | PDU-02 | 35 | U3-7A-35 / 2P 30A | U3-7B-35 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 5.9127 | 5.8439 | 11.7566 | 1040.6 | 1007.9 | 2048.5 | 세종 인터넷(클라우드이음) | 신규 구성중
| C1003 | B07 | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-33 | 7-1-B2-30-33 | 7-DaHall 1-PDU-01-30-33 | 7-DaHall 1-PDU-02-30-33 | 220 | 30 | PDU-01 | 33 | 220 | 30 | PDU-02 | 33 | U3-7A-33 / 2P 30A | U3-7B-33 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 8.4039 | 8.1425 | 16.5465 | 1331.7 | 1295.8 | 2627.5 | 세종 인터넷(클라우드이음) | 신규 구성중
| C1004 | B06 | Sejong Telecom Inc. | 1.6 | ○ |  | 7-1-A2-30-31 | 7-1-B2-30-31 | 7-DaHall 1-PDU-01-30-31 | 7-DaHall 1-PDU-02-30-31 | 220 | 30 | PDU-01 | 31 | 220 | 30 | PDU-02 | 31 | U3-7A-31 / 2P 30A | U3-7B-31 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 3.983 | 3.2471 | 7.2301 | 661.9 | 506.7 | 1168.6 | 세종 인터넷(클라우드이음) | 신규 구성중
| C1005 | B05 | Sejong Telecom Inc. | 2.2 | ○ |  | 7-1-A2-30-39 | 7-1-B2-30-39 | 7-DaHall 1-PDU-01-30-39 | 7-DaHall 1-PDU-02-30-39 | 220 | 30 | PDU-01 | 39 | 220 | 30 | PDU-02 | 39 | U3-7A-39 / 2P 30A | U3-7B-39 / 2P 30A | [6 empty] | U3-7A(U7-5A) 4P 300A | U3-7B(U7-6B) 4P 300A | LV-7A #05 / 3P 320A (U7-5A) | LV-7B #06 / 3P 320A (U7-6B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.3576 | 1.9337 | 3.2913 | 135.4 | 252.6 | 388 | 세종 인터넷(클라우드이음)
| C1006 | B04 | 7F-B04 랙 | [34 empty] | 0 | 미설치 (랙 없음)
| C1007 | B03 | 7F-B03 랙 | [34 empty] | 0 | 미설치 (랙 없음)
| C1008 | B02 | 7F-B02 랙 | [34 empty] | 0 | 미설치 (랙 없음)
| C1009 | B01 | 7F-B01 랙 | [34 empty] | 0 | 미설치 (랙 없음)
A열 | C1101 | [36 empty] | 0
| C1102 | A08 | LG Hello Vision Co., Ltd. | 2.2 | ○ |  | 7-1-A3-50-8 | 7-1-B3-50-8 | 7-DaHall 1-RPP-03-50-8 | 7-DaHall 1-RPP-04-50-8 | 220 | 50 | RPP-03 | 8 | 220 | 50 | RPP-04 | 8 | UPS A2-08 / 2P 50A | UPS B2-08 / 2P 50A | UPS 출력분전반 A2 #08 | UPS 출력분전반 B2 #08 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.9608 | 1.859 | 3.8198 | 301.9 | 292.5 | 594.4 | IDC 고객(LG HELLOVISION)
| C1103 | A07 | LG Hello Vision Co., Ltd. | 2.2 | ○ |  | 7-1-A3-50-6 | 7-1-B3-50-6 | 7-DaHall 1-RPP-03-50-6 | 7-DaHall 1-RPP-04-50-6 | 220 | 50 | RPP-03 | 6 | 220 | 50 | RPP-04 | 6 | UPS A2-06 / 2P 50A | UPS B2-06 / 2P 50A | UPS 출력분전반 A2 #06 | UPS 출력분전반 B2 #06 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.5083 | 1.3512 | 2.8595 | 242.6 | 184.8 | 427.4 | IDC 고객(LG HELLOVISION)
| C1104 | A06 | LG Hello Vision Co., Ltd. | 2.2 | ○ |  | 7-1-A3-50-10 | 7-1-B3-50-10 | 7-DaHall 1-RPP-03-50-10 | 7-DaHall 1-RPP-04-50-10 | 220 | 50 | RPP-03 | 10 | 220 | 50 | RPP-04 | 10 | UPS A2-10 / 2P 50A | UPS B2-10 / 2P 50A | UPS 출력분전반 A2 #10 | UPS 출력분전반 B2 #10 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.6178 | 2.8469 | 5.4647 | 343.9 | 369.4 | 713.3 | IDC 고객(LG HELLOVISION)
| C1105 | A05 | LG Hello Vision Co., Ltd. | 2.2 | ○ |  | 7-1-A3-50-9 | 7-1-B3-50-9 | 7-DaHall 1-RPP-03-50-9 | 7-DaHall 1-RPP-04-50-9 | 220 | 50 | RPP-03 | 9 | 220 | 50 | RPP-04 | 9 | UPS A2-09 / 2P 50A | UPS B2-09 / 2P 50A | UPS 출력분전반 A2 #09 | UPS 출력분전반 B2 #09 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.6297 | 1.7102 | 4.3399 | 391.8 | 234.3 | 626.1 | IDC 고객(LG HELLOVISION)
| C1106 | A04 | LG Hello Vision Co., Ltd. |  |  | ○ | 7-1-B-5-35-42 | 7-1-A-5-35-42 | 7-DaHall 1-B-5-35-42 | 7-DaHall 1-A-5-35-42 | 48 | 35 | B-5 | 42 | 48 | 35 | A-5 | 42 | IPD B-5-F42(1) (구 IPD A) / 35A | IPD A-5-F42(1) (구 IPD B) / 35A | IPD B-5 (구 IPD A) | IPD A-5 (구 IPD B) | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | IDC 고객(LG HELLOVISION) | DC전원 장비직결
[6 empty] | ○ | 7-1-B-5-35-43 | 7-1-A-5-35-43 | 7-DaHall 1-B-5-35-43 | 7-DaHall 1-A-5-35-43 | 48 | 35 | B-5 | 43 | 48 | 35 | A-5 | 43 | IPD B-5-F43(2) (구 IPD A) / 35A | IPD A-5-F43(2) (구 IPD B) / 35A | IPD B-5 (구 IPD A) | IPD A-5 (구 IPD B) | 정류기 A -48V 1400A | 정류기 B -48V 1400A | UPS 출력 배전반A, #06 4P 225A | UPS 출력 배전반B, #01 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | [5 empty] | 0 | IDC 고객(LG HELLOVISION) | DC전원 장비직결
|  |  |  | 2.2 | ○ |  | 7-1-A3-50-7 | 7-1-B3-50-7 | 7-DaHall 1-RPP-03-50-7 | 7-DaHall 1-RPP-04-50-7 | 220 | 50 | RPP-03 | 7 | 220 | 50 | RPP-04 | 7 | UPS A2-07 / 2P 50A | UPS B2-07 / 2P 50A | UPS 출력분전반 A2 #07 | UPS 출력분전반 B2 #07 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.437 | 4.0821 | 6.5191 | 367.2 | 628.5 | 995.7 | IDC 고객(LG HELLOVISION) | DC전원 장비직결
| C1107 | A03 | LG Hello Vision Co., Ltd. | 2.2 | ○ |  | 7-1-A3-50-5 | 7-1-B3-50-5 | 7-DaHall 1-RPP-03-50-5 | 7-DaHall 1-RPP-04-50-5 | 220 | 50 | RPP-03 | 5 | 220 | 50 | RPP-04 | 5 | UPS A2-05 / 2P 50A | UPS B2-05 / 2P 50A | UPS 출력분전반 A2 #05 | UPS 출력분전반 B2 #05 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 3.3004 | 3.9282 | 7.2285 | 490 | 666.6 | 1156.6 | IDC 고객(LG HELLOVISION)
| C1108 | A02 | LG Hello Vision Co., Ltd. | 2.2 | ○ |  | 7-1-A3-50-3 | 7-1-B3-50-3 | 7-DaHall 1-RPP-03-50-3 | 7-DaHall 1-RPP-04-50-3 | 220 | 50 | RPP-03 | 3 | 220 | 50 | RPP-04 | 3 | UPS A2-03 / 2P 50A | UPS B2-03 / 2P 50A | UPS 출력분전반 A2 #03 | UPS 출력분전반 B2 #03 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 2.9106 | 3.5632 | 6.4738 | 377.8 | 486.8 | 864.6 | IDC 고객(LG HELLOVISION)
| C1109 | A01 | LG Hello Vision Co., Ltd. | 2.2 | ○ |  | 7-1-A3-50-1 | 7-1-B3-50-1 | 7-DaHall 1-RPP-03-50-1 | 7-DaHall 1-RPP-04-50-1 | 220 | 50 | RPP-03 | 1 | 220 | 50 | RPP-04 | 1 | UPS A2-01 / 2P 50A | UPS B2-01 / 2P 50A | UPS 출력분전반 A2 #01 | UPS 출력분전반 B2 #01 | UPS 출력 분전반A2, 4P 225A | UPS 출력 분전반B2, 4P 225A | UPS 출력 배전반A, #03 4P 225A | UPS 출력 배전반B, #04 3P 150A | UPS 출력 배전반A, 4P 400A | UPS 출력 배전반B, 4P 400A | LV-7A #06 / 3P 320A (U7-6A) | LV-7B #07 / 3P 320A (U7-7B) | TR-7A 1000kVA | TR-7B 1000kVA | 1.179 | 1.1786 | 2.3576 | 163.5 | 153 | 316.5 | IDC 고객(LG HELLOVISION)
|  |  | 신규BMS(20F TPS실) Rack | 2.2 | ○ |  |  | 7-1-B2-30-49 |  | 7-DaHall 1-PDU-02-30-49 |  |  |  |  | 220 | 30 | PDU-02 | 49 | B: U3-7B-49 / 2P 30A; B: U3-7B(U7-6B) 4P 300A; B: LV-7B #06 / 3P 320A (U7-6B); B: TR-7B 1000kVA; B전원: 1.081; 합계: 1.081; B전원: 101.5 | 101.5
|  |  | 신규BMS(7F TPS실) Rack | 2.2 | ○ |  |  | 7-1-B2-30-51 |  | 7-DaHall 1-PDU-02-30-51 |  |  |  |  | 220 | 30 | PDU-02 | 51 | B: U3-7B-51 / 2P 30A; B: U3-7B(U7-6B) 4P 300A; B: LV-7B #06 / 3P 320A (U7-6B); B: TR-7B 1000kVA; B전원: 0.81052; 합계: 0.81052; B전원: 71.8 | 71.8
|  |  | 8층 Office 분전반(창고) |  |  |  | 7-1-A4-225-2 |  | 7-DaHall 1-PDU-03-225-2 |  | 220 | 225 | PDU-03 | 2 |  |  |  |  | A전원: 14.8071; 합계: 14.8071 | 0
누락 회로 파악 불가 |  |  |  |  | ○ |  | 7-1-A1-20-1 |  | 7-DaHall 1-RPP-01-20-1 |  | 220 | 20 | RPP-01 | 1 |  |  |  |  | A: UPS A1-01 / 2P 20A; A: UPS 출력분전반 A1 #01; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 0 | 0 | W-DCS 8000
[5 empty] | ○ |  | 7-1-A1-30-2 |  | 7-DaHall 1-RPP-01-30-2 |  | 220 | 30 | RPP-01 | 2 |  |  |  |  | A: UPS A1-02 / 2P 30A; A: UPS 출력분전반 A1 #02; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 0 | 0 | TO 8F 보안실 UPS항온항습기 모니터용PC
[5 empty] | ○ |  | 7-1-A1-20-3 |  | 7-DaHall 1-RPP-01-20-3 |  | 220 | 20 | RPP-01 | 3 |  |  |  |  | A: UPS A1-03 / 2P 20A; A: UPS 출력분전반 A1 #03; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 0 | 0 | ?? (전송)
[5 empty] | ○ |  | 7-1-A1-20-5 |  | 7-DaHall 1-RPP-01-20-5 |  | 220 | 20 | RPP-01 | 5 |  |  |  |  | A: UPS A1-05 / 2P 20A; A: UPS 출력분전반 A1 #05; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 0 | 0 | ?? (전송)
[5 empty] | ○ |  | 7-1-A1-20-9 |  | 7-DaHall 1-RPP-01-20-9 |  | 220 | 20 | RPP-01 | 9 |  |  |  |  | A: UPS A1-09 / 2P 20A; A: UPS 출력분전반 A1 #09; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 2.4182; 합계: 2.4182; A전원: 0 | 0 | IDC (Voice사업팀 MMS용-B)
[5 empty] | ○ |  | 7-1-A1-20-13 |  | 7-DaHall 1-RPP-01-20-13 |  | 220 | 20 | RPP-01 | 13 |  |  |  |  | A: UPS A1-13 / 2P 20A; A: UPS 출력분전반 A1 #13; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 1.4136; 합계: 1.4136; A전원: 0 | 0 | ONS1064 SERVER
[5 empty] | ○ |  | 7-1-A1-20-15 |  | 7-DaHall 1-RPP-01-20-15 |  | 220 | 20 | RPP-01 | 15 |  |  |  |  | A: UPS A1-15 / 2P 20A; A: UPS 출력분전반 A1 #15; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 4.0936; 합계: 4.0936; A전원: 0 | 0 | NTT 하-1
[5 empty] | ○ |  | 7-1-A1-20-17 |  | 7-DaHall 1-RPP-01-20-17 |  | 220 | 20 | RPP-01 | 17 |  |  |  |  | A: UPS A1-17 / 2P 20A; A: UPS 출력분전반 A1 #17; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 0; 합계: 0; A전원: 68 | 68 | 8층 보안실 CCTV 모니터
[5 empty] | ○ |  | 7-1-A1-20-27 |  | 7-DaHall 1-RPP-01-20-27 |  | 220 | 20 | RPP-01 | 27 |  |  |  |  | A: UPS A1-27 / 2P 20A; A: UPS 출력분전반 A1 #27; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 3.8387; 합계: 3.8387; A전원: 404.7 | 404.7 | 전송 (NMS B-15)
[5 empty] | ○ |  | 7-1-A1-30-28 |  | 7-DaHall 1-RPP-01-30-28 |  | 220 | 30 | RPP-01 | 28 |  |  |  |  | A: UPS A1-28 / 2P 30A; A: UPS 출력분전반 A1 #28; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 1.8009; 합계: 1.8009; A전원: 126.6 | 126.6 | 운용실콘센트
[5 empty] | ○ |  | 7-1-A1-20-29 |  | 7-DaHall 1-RPP-01-20-29 |  | 220 | 20 | RPP-01 | 29 |  |  |  |  | A: UPS A1-29 / 2P 20A; A: UPS 출력분전반 A1 #29; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 3.7843; 합계: 3.7843; A전원: 126.6 | 126.6 | 전송 (NMS B-16)
[5 empty] | ○ |  | 7-1-A1-30-30 |  | 7-DaHall 1-RPP-01-30-30 |  | 220 | 30 | RPP-01 | 30 |  |  |  |  | A: UPS A1-30 / 2P 30A; A: UPS 출력분전반 A1 #30; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 3.8632; 합계: 3.8632; A전원: 503.7 | 503.7 | 운용실콘센트 창가1열
[5 empty] | ○ |  | 7-1-A1-20-31 |  | 7-DaHall 1-RPP-01-20-31 |  | 220 | 20 | RPP-01 | 31 |  |  |  |  | A: UPS A1-31 / 2P 20A; A: UPS 출력분전반 A1 #31; A: UPS 출력 분전반A1, 4P 400A; A: UPS 출력 분전반A, #01 4P 225A; A: UPS 출력 배전반A, 4P 400A; A: LV-7A #06 / 3P 320A (U7-6A); A: TR-7A 1000kVA; A전원: 5.6071; 합계: 5.6071; A전원: 570.1 | 570.1 | 전송 (??)
[5 empty] | ○ |  |  | 7-1-B2-30-50 |  | 7-DaHall 1-PDU-02-30-50 |  |  |  |  | 220 | 30 | PDU-02 | 50 | B: U3-7B-50 / 2P 30A; B: U3-7B(U7-6B) 4P 300A; B: LV-7B #06 / 3P 320A (U7-6B); B: TR-7B 1000kVA; B전원: 3.4265; 합계: 3.4265; B전원: 328.3 | 328.3 | 7층 출입카드(전층 출입통제)
[5 empty] | ○ |  |  | 7-1-B2-30-52 |  | 7-DaHall 1-PDU-02-30-52 |  |  |  |  | 220 | 30 | PDU-02 | 52 | B: U3-7B-52 / 2P 30A; B: U3-7B(U7-6B) 4P 300A; B: LV-7B #06 / 3P 320A (U7-6B); B: TR-7B 1000kVA; B전원: 3.2826; 합계: 3.2826; B전원: 0 | 0 | 20F MAIN (FMS)
[5 empty] | ○ |  |  | 7-1-B2-30-54 |  | 7-DaHall 1-PDU-02-30-54 |  |  |  |  | 220 | 30 | PDU-02 | 54 | B: U3-7B-54 / 2P 30A; B: U3-7B(U7-6B) 4P 300A; B: LV-7B #06 / 3P 320A (U7-6B); B: TR-7B 1000kVA; B전원: 0; 합계: 0; B전원: 0 | 0 | 7F MAIN (FMS)
[5 empty] | ○ |  | 7-1-A2-30-52 |  | 7-DaHall 1-PDU-01-30-52 |  | 220 | 30 | PDU-01 | 52 |  |  |  |  | A: U3-7A-52 / 2P 30A; A: U3-7A(U7-5A) 4P 300A; A: LV-7A #05 / 3P 320A (U7-5A); A: TR-7A 1000kVA; A전원: 0.0086132; 합계: 0.0086132; A전원: 0 | 0 | 7F NTT CCTV 전원
[5 empty] | ○ |  |  | 7-1-B1-20-1 |  | 7-DaHall 1-RPP-02-20-1 |  |  |  |  | 220 | 20 | RPP-02 | 1 | B: UPS B1-01 / 2P 20A; B: UPS 출력분전반 B1 #01; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 0; 합계: 0; B전원: 0 | 0 | 강남방향 창가열 콘센트
[5 empty] | ○ |  |  | 7-1-B1-30-2 |  | 7-DaHall 1-RPP-02-30-2 |  |  |  |  | 220 | 30 | RPP-02 | 2 | B: UPS B1-02 / 2P 30A; B: UPS 출력분전반 B1 #02; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 1.6103; 합계: 1.6103; B전원: 287.3 | 287.3 | 정면창가 콘센트
[5 empty] | ○ |  |  | 7-1-B1-20-3 |  | 7-DaHall 1-RPP-02-20-3 |  |  |  |  | 220 | 20 | RPP-02 | 3 | B: UPS B1-03 / 2P 20A; B: UPS 출력분전반 B1 #03; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 0.5364; 합계: 0.5364; B전원: 68.2 | 68.2 | ??
[5 empty] | ○ |  |  | 7-1-B1-30-6 |  | 7-DaHall 1-RPP-02-30-6 |  |  |  |  | 220 | 30 | RPP-02 | 6 | B: UPS B1-06 / 2P 30A; B: UPS 출력분전반 B1 #08; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 0; 합계: 0; B전원: 0 | 0 | 전송 (GAINS)
[5 empty] | ○ |  |  | 7-1-B1-20-7 |  | 7-DaHall 1-RPP-02-20-7 |  |  |  |  | 220 | 20 | RPP-02 | 7 | B: UPS B1-07 / 2P 20A; B: UPS 출력분전반 B1 #07; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 1.4434; 합계: 1.4434; B전원: 148.6 | 148.6 | C2C DWDM EMS RACK
[5 empty] | ○ |  |  | 7-1-B1-20-11 |  | 7-DaHall 1-RPP-02-20-11 |  |  |  |  | 220 | 20 | RPP-02 | 11 | B: UPS B1-11 / 2P 20A; B: UPS 출력분전반 B1 #11; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 0; 합계: 0; B전원: 0 | 0 | 전송 (ONS1064 SERVER)
[5 empty] | ○ |  |  | 7-1-B1-30-22 |  | 7-DaHall 1-RPP-02-30-22 |  |  |  |  | 220 | 30 | RPP-02 | 22 | B: UPS B1-22 / 2P 30A; B: UPS 출력분전반 B1 #22; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 0; 합계: 0; B전원: 0 | 0 | 운용실 바닥콘센트
[5 empty] | ○ |  |  | 7-1-B1-30-24 |  | 7-DaHall 1-RPP-02-30-24 |  |  |  |  | 220 | 30 | RPP-02 | 24 | B: UPS B1-24 / 2P 30A; B: UPS 출력분전반 B1 #24; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 2.5932; 합계: 2.5932; B전원: 204.5 | 204.5 | 운용실 콘센트 창가1열
[5 empty] | ○ |  |  | 7-1-B1-20-35 |  | 7-DaHall 1-RPP-02-20-35 |  |  |  |  | 220 | 20 | RPP-02 | 35 | B: UPS B1-35 / 2P 20A; B: UPS 출력분전반 B1 #35; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 2.4571; 합계: 2.4571; B전원: 292.1 | 292.1 | 7F NMS A-18
[5 empty] | ○ |  |  | 7-1-B1-20-37 |  | 7-DaHall 1-RPP-02-20-37 |  |  |  |  | 220 | 20 | RPP-02 | 37 | B: UPS B1-37 / 2P 20A; B: UPS 출력분전반 B1 #37; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 5.8717; 합계: 5.8717; B전원: 670.8 | 670.8 | 7F NMS A-19
[5 empty] | ○ |  |  | 7-1-B1-20-38 |  | 7-DaHall 1-RPP-02-20-38 |  |  |  |  | 220 | 20 | RPP-02 | 38 | B: UPS B1-38 / 2P 30A; B: UPS 출력분전반 B1 #38; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; 합계: 0; B전원: 745.2 | 745.2 | IDC MAN POP
[5 empty] | ○ |  |  | 7-1-B1-20-39 |  | 7-DaHall 1-RPP-02-20-39 |  |  |  |  | 220 | 20 | RPP-02 | 39 | B: UPS B1-39 / 2P 20A; B: UPS 출력분전반 B1 #39; B: UPS 출력 분전반B1, 4P 400A; B: UPS 출력 분전반B, #02 3P 150A; B: UPS 출력 분전반B 4P 400A; B: LV-7B #07 / 3P 320A (U7-7B); B: TR-7B 1000kVA; B전원: 3.1211; 합계: 3.1211; B전원: 242.9 | 242.9 | 7F NMS A-20
[35 empty] | 798.9848 | 19.5675
Note on L38: A-4-27 OSN550 A-4-33 코위버CWDM
Note on M38: A-4-27 OSN550 A-4-33 코위버CWDM
Note on N38: A-4-27 OSN550 A-4-33 코위버CWDM
Note on O38: A-4-27 OSN550 A-4-33 코위버CWDM
Note on P38: B-4-33 코위버CWDM B-4-57 OSN550
Note on Q38: B-4-33 코위버CWDM B-4-57 OSN550
Note on R38: B-4-33 코위버CWDM B-4-57 OSN550
Note on S38: B-4-33 코위버CWDM B-4-57 OSN550
Note on T38: A-4-27 OSN550 A-4-33 코위버CWDM
Note on U38: B-4-33 코위버CWDM B-4-57 OSN550
Note on L39: A-4-27 OSN550 A-4-33 코위버CWDM
Note on M39: A-4-27 OSN550 A-4-33 코위버CWDM
Note on N39: A-4-27 OSN550 A-4-33 코위버CWDM
Note on O39: A-4-27 OSN550 A-4-33 코위버CWDM
Note on P39: B-4-33 코위버CWDM B-4-57 OSN550
Note on Q39: B-4-33 코위버CWDM B-4-57 OSN550
Note on R39: B-4-33 코위버CWDM B-4-57 OSN550
Note on S39: B-4-33 코위버CWDM B-4-57 OSN550
Note on T39: A-4-27 OSN550 A-4-33 코위버CWDM
Note on U39: B-4-33 코위버CWDM B-4-57 OSN550
Note on R66: B-2-62 PDP B-2-63 장비직결
Note on S66: B-2-62 PDP B-2-63 장비직결
Note on T66: A-2-62 PDP A-2-63 장비직결
Note on U66: B-2-62 PDP B-2-63 장비직결
Note on R67: B-2-62 PDP B-2-63 장비직결
Note on S67: B-2-62 PDP B-2-63 장비직결
Note on T67: A-2-62 PDP A-2-63 장비직결
Note on U67: B-2-62 PDP B-2-63 장비직결
Note on C162: 이현상: 인터넷에서 어마무시하게 전기 실사용 중이라함 확인 필요(21.05.27)
Note on T225: 이현상: IPD / B-5_P48 C-1 랙 장비__A 인가? 정원용M 확인 필요...
Note on U225: 이현상: 이거 랙 번호가 정확한건가? 변익준M에 확인 필요..
Note on T241: 이현상: IPD / B-5_P42 A-5 랙 장비_A(1) 인가? 정원용M 확인 필요..
Note on U241: 이현상: IPD / B-5_P42 A-5 랙 장비_B(1) 인가?
Note on T242: 이현상: IPD / B-5_P43 A-5 랙 장비_A(2) 인가? 정원용M 확인 필요..
Note on U242: 이현상: IPD / B-5_P43 A-5 랙 장비_B(2) 인가?

## 6층_랙별_계통 및_부하량
6층 랙별 전기공급계통
[8 empty] | 층/분전반명/차단기용량/차단기번호 | [20 empty] | =AD5:AD250
DEKR No. | 랙 No. | 고객명 | 계약용량 | 리셉터클 Name |  | 차단기 정보 |  | DEK Naming Convention 적용 명칭(NEW) |  | 차단기 정보(수정) | [7 empty] | 분전반 정보 |  | 배전반 정보 |  | TR 정보 |  | 월 평균 전류 |  |  | 월 유효전력량 |  | 월간 사용전력량[kWh] | 비 고
|  |  | kW | A | B | A | B | A | B | A |  |  |  | B |  |  |  | A | B | A | B | A | B | A | B | 합계 | A | B
A101 | [28 empty] | 0 | 랙 미설치
A102 | 6F-AE19 | [24 empty] | 0 |  |  | 0 | 랙 미설치
A103 | 6F-AE18 | [24 empty] | 0 |  |  | 0 | 랙 미설치
A104 | 6F-AE17 | [24 empty] | 0 |  |  | 0 | 랙 미설치
A105 | 6F-AE16 |  |  | A6-2-4 | B6-2-4 | U6-A6-36 / 2P 30A | U6-B6-36 / 2P 30A | 6-DaHall 1-PDU-07-30-36 | 6-DaHall 1-PDU-08-30-36 | 220 | 30 | 07 | 36 | 220 | 30 | 08 | 36 | U6-A6 4P 300A | U6-B6 4P 300A | LV-6A #06, 3P 320A | LV-6B #02, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0
A106 | 6F-AE15 |  |  | A6-2-5 | B6-2-5 | U6-A6-38 / 2P 30A | U6-B6-38 / 2P 30A | 6-DaHall 1-PDU-07-30-38 | 6-DaHall 1-PDU-08-30-38 | 220 | 30 | 07 | 38 | 220 | 30 | 08 | 38 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A107 | 6F-AE14 |  |  | A6-2-6 | B6-2-6 | U6-A6-40 / 2P 30A | U6-B6-40 / 2P 30A | 6-DaHall 1-PDU-07-30-40 | 6-DaHall 1-PDU-08-30-40 | 220 | 30 | 07 | 40 | 220 | 30 | 08 | 40 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A108 | 6F-AE13 |  |  | A6-2-7 | B6-2-7 | U6-A6-42 / 2P 30A | U6-B6-42 / 2P 30A | 6-DaHall 1-PDU-07-30-42 | 6-DaHall 1-PDU-08-30-42 | 220 | 30 | 07 | 42 | 220 | 30 | 08 | 42 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A109 | 6F-AE12 |  |  | A6-2-8 | B6-2-8 | U6-A6-44 / 2P 30A | U6-B6-44 / 2P 30A | 6-DaHall 1-PDU-07-30-44 | 6-DaHall 1-PDU-08-30-44 | 220 | 30 | 07 | 44 | 220 | 30 | 08 | 44 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A110 | 6F-AE11 |  |  | A6-2-9 | B6-2-9 | U6-A6-46 / 2P 30A | U6-B6-46 / 2P 30A | 6-DaHall 1-PDU-07-30-46 | 6-DaHall 1-PDU-08-30-46 | 220 | 30 | 07 | 46 | 220 | 30 | 08 | 46 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A201 | [28 empty] | 0 | 랙 미설치
A202 | 6F-AD19 | [27 empty] | 0 | 랙 미설치
A203 | 6F-AD18 | [27 empty] | 0 | 랙 미설치
A204 | 6F-AD17 | [27 empty] | 0 | 랙 미설치
A205 | 6F-AD16 |  |  | A6-3-4 | B6-3-4 | U6-A6-54 / 2P 30A | U6-B6-54 / 2P 30A | 6-DaHall 1-PDU-07-30-54 | 6-DaHall 1-PDU-08-30-54 | 220 | 30 | 07 | 54 | 220 | 30 | 08 | 54 | U6-A6 4P 300A | U6-B6 4P 300A | LV-6A #06, 3P 320A | LV-6B #02, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0
A206 | 6F-AD15 |  |  | A6-3-5 | B6-3-5 | U6-A6-53 / 2P 30A | U6-B6-53 / 2P 30A | 6-DaHall 1-PDU-07-30-53 | 6-DaHall 1-PDU-08-30-53 | 220 | 30 | 07 | 53 | 220 | 30 | 08 | 53 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A207 | 6F-AD14 |  |  | A6-3-6 | B6-3-6 | U6-A6-51 / 2P 30A | U6-B6-51 / 2P 30A | 6-DaHall 1-PDU-07-30-51 | 6-DaHall 1-PDU-08-30-51 | 220 | 30 | 07 | 51 | 220 | 30 | 08 | 51 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A208 | 6F-AD13 |  |  | A6-3-7 | B6-3-7 | U6-A6-49 / 2P 30A | U6-B6-49 / 2P 30A | 6-DaHall 1-PDU-07-30-49 | 6-DaHall 1-PDU-08-30-49 | 220 | 30 | 07 | 49 | 220 | 30 | 08 | 49 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A209 | 6F-AD12 |  |  | A2-3-8 | B2-3-8 | U6-A2-16 / 2P 30A | U6-B2-16 / 2P 30A | 6-DaHall 1-PDU-03-30-16 | 6-DaHall 1-PDU-04-30-16 | 220 | 30 | 03 | 16 | 220 | 30 | 04 | 16 | U-A2 4P 200A | U-B2 4P 200A | UPS 출력배전반(A) #02, 4P 200A | UPS 출력배전반(B) #04, 4P 200A |  |  | 0 | 0 | 0 | 0 | 0 | 0
A210 | 6F-AD11 |  |  | A2-3-9 | B2-3-9 | U6-A2-18 / 2P 30A | U6-B2-18 / 2P 30A | 6-DaHall 1-PDU-03-30-18 | 6-DaHall 1-PDU-04-30-18 | 220 | 30 | 03 | 18 | 220 | 30 | 04 | 18 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A303 | 6F-AC18 | [27 empty] | 0 | 랙 미설치
A304 | 6F-AC17 | [27 empty] | 0 | 랙 미설치
A305 | 6F-AC16 |  |  | A6-4-4 | B6-4-4 | U6-A6-08 / 2P 30A | U6-B6-08 / 2P 30A | 6-DaHall 1-PDU-07-30-8 | 6-DaHall 1-PDU-08-30-8 | 220 | 30 | 07 | 8 | 220 | 30 | 08 | 8 | U6-A6 4P 300A | U6-B6 4P 300A | LV-6A #06, 3P 320A | LV-6B #02, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0
A306 | 6F-AC15 |  |  | A6-4-5 | B6-4-5 | U6-A6-10 / 2P 30A | U6-B6-10 / 2P 30A | 6-DaHall 1-PDU-07-30-10 | 6-DaHall 1-PDU-08-30-10 | 220 | 30 | 07 | 10 | 220 | 30 | 08 | 10 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A307 | 6F-AC14 |  |  | A6-4-6 | B6-4-6 | U6-A6-12 / 2P 30A | U6-B6-12 / 2P 30A | 6-DaHall 1-PDU-07-30-12 | 6-DaHall 1-PDU-08-30-12 | 220 | 30 | 07 | 12 | 220 | 30 | 08 | 12 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A308 | 6F-AC13 |  |  | A6-4-7 | B6-4-7 | U6-A6-14 / 2P 30A | U6-B6-14 / 2P 30A | 6-DaHall 1-PDU-07-30-14 | 6-DaHall 1-PDU-08-30-14 | 220 | 30 | 07 | 14 | 220 | 30 | 08 | 14 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A309 | 6F-AC12 |  |  | A1-4-8 | B1-4-8 | U-A1-48 / 2P 30A | U-B1-48 / 2P 30A | 6-DaHall 1-PDU-01-30-48 | 6-DaHall 1-PDU-02-30-48 | 220 | 30 | 01 | 48 | 220 | 30 | 02 | 48 | U-A1 4P 200A | U-B1 4P 200A | UPS 출력배전반(A) #04, 4P 200A | UPS 출력배전반(B) #02, 4P 200A |  |  | 0.53761 | 0 | 0.53761 | 0 | 0 | 0
A310 | 6F-AC11 |  |  | A5-4-9 | B5-4-9 | U6-A5-50 / 2P 30A | U6-B5-50 / 2P 30A | 6-DaHall 1-PDU-05-30-50 | 6-DaHall 1-PDU-06-30-50 | 220 | 30 | 05 | 50 | 220 | 30 | 06 | 50 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A |  |  | 0 | 0 | 0 | 0 | 0 | 0
A403 | 6F-AB18 | [27 empty] | 0 | 랙 미설치
A404 | 6F-AB17 | [27 empty] | 0 | 랙 미설치
A405 | 6F-AB16 |  |  | A6-5-4 | B6-5-4 | U6-A6-22 / 2P 30A | U6-B6-22 / 2P 30A | 6-DaHall 1-PDU-07-30-22 | 6-DaHall 1-PDU-08-30-22 | 220 | 30 | 07 | 22 | 220 | 30 | 08 | 22 | U6-A6 4P 300A | U6-B6 4P 300A | LV-6A #06, 3P 320A | LV-6B #02, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0
A406 | 6F-AB15 |  |  | A6-5-5 | B6-5-5 | U6-A6-24 / 2P 30A | U6-B6-24 / 2P 30A | 6-DaHall 1-PDU-07-30-24 | 6-DaHall 1-PDU-08-30-24 | 220 | 30 | 07 | 24 | 220 | 30 | 08 | 24 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A407 | 6F-AB14 |  |  | A6-5-6 | B6-5-6 | U6-A6-26 / 2P 30A | U6-B6-26 / 2P 30A | 6-DaHall 1-PDU-07-30-26 | 6-DaHall 1-PDU-08-30-26 | 220 | 30 | 07 | 26 | 220 | 30 | 08 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A408 | 6F-AB13 |  |  | A6-5-7 | B6-5-7 | U6-A6-28 / 2P 30A | U6-B6-28 / 2P 30A | 6-DaHall 1-PDU-07-30-28 | 6-DaHall 1-PDU-08-30-28 | 220 | 30 | 07 | 28 | 220 | 30 | 08 | 28 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A409 | 6F-AB12 |  |  | A2-5-8 | B2-5-8 | U-A2-33 / 2P 30A | U-B2-33 / 2P 30A | 6-DaHall 1-PDU-03-30-33 | 6-DaHall 1-PDU-04-30-33 | 220 | 30 | 03 | 33 | 220 | 30 | 04 | 33 | U-A2 4P 200A | U-B2 4P 200A | UPS 출력배전반(A) #02, 4P 200A | UPS 출력배전반(B) #04, 4P 200A |  |  | 0 | 0 | 0 | 0 | 0 | 0
A410 | 6F-AB11 |  |  | A2-5-9 | B2-5-9 | U-A2-35 / 2P 30A | U-B2-35 / 2P 30A | 6-DaHall 1-PDU-03-30-35 | 6-DaHall 1-PDU-04-30-35 | 220 | 30 | 03 | 35 | 220 | 30 | 04 | 35 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A503 | 6F-V18 | [24 empty] | 0 |  |  | 0 | 랙 미설치
A504 | 6F-V17 |  |  | A2-7-2 | B2-7-2 | U-A2-24 / 2P 30A | U-B2-24 / 2P 30A | 6-DaHall 1-PDU-03-30-24 | 6-DaHall 1-PDU-04-30-24 | 220 | 30 | 03 | 24 | 220 | 30 | 04 | 24 | U-A2 4P 200A | U-B2 4P 200A | UPS 출력배전반(A) #02, 4P 200A | UPS 출력배전반(B) #04, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | A2-7-1 | B2-7-1 | U-A2-22 / 2P 30A | U-B2-22 / 2P 30A | 6-DaHall 1-PDU-03-30-22 | 6-DaHall 1-PDU-04-30-22 | 220 | 30 | 03 | 22 | 220 | 30 | 04 | 22 | [6 empty] | 0 | 0 |  | 0 | 0
A505 | 6F-V16 |  |  | A2-7-3 | B2-7-3 | U-A2-26 / 2P 30A | U-B2-26 / 2P 30A | 6-DaHall 1-PDU-03-30-26 | 6-DaHall 1-PDU-04-30-26 | 220 | 30 | 03 | 26 | 220 | 30 | 04 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | A2-8-1 | B2-8-1 | U-A2-38 / 2P 30A | U-B2-38 / 2P 30A | 6-DaHall 1-PDU-03-30-38 | 6-DaHall 1-PDU-04-30-38 | 220 | 30 | 03 | 38 | 220 | 30 | 04 | 38 | [6 empty] | 0 | 0 |  | 0 | 0
A506 | 6F-V15 |  |  | A2-7-4 | B2-7-4 | U-A2-28 / 2P 30A | U-B2-28 / 2P 30A | 6-DaHall 1-PDU-03-30-28 | 6-DaHall 1-PDU-04-30-28 | 220 | 30 | 03 | 28 | 220 | 30 | 04 | 28 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A507 | 6F-V14 |  |  | A2-7-5 | B2-7-5 | U-A2-30 / 2P 30A | U-B2-30 / 2P 30A | 6-DaHall 1-PDU-03-30-30 | 6-DaHall 1-PDU-04-30-30 | 220 | 30 | 03 | 30 | 220 | 30 | 04 | 30 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A508 | 6F-V13 |  |  | A2-7-6 | B2-7-6 | U-A2-32 / 2P 30A | U-B2-32 / 2P 30A | 6-DaHall 1-PDU-03-30-32 | 6-DaHall 1-PDU-04-30-32 | 220 | 30 | 03 | 32 | 220 | 30 | 04 | 32 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A509 | 6F-V12 |  |  | A2-7-7 | B2-7-7 | U-A2-34 / 2P 30A | U-B2-34 / 2P 30A | 6-DaHall 1-PDU-03-30-34 | 6-DaHall 1-PDU-04-30-34 | 220 | 30 | 03 | 34 | 220 | 30 | 04 | 34 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A510 | 6F-V11 |  |  | A2-7-8 | B2-7-8 | U-A2-36 / 2P 30A | U-B2-36 / 2P 30A | 6-DaHall 1-PDU-03-30-36 | 6-DaHall 1-PDU-04-30-36 | 220 | 30 | 03 | 36 | 220 | 30 | 04 | 36 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6F-W19 | [24 empty] | 0 |  |  | 0 | 랙 미설치
A603 | 6F-W18 | [24 empty] | 0 |  |  | 0 | 랙 미설치
A604 | 6F-W17 |  |  | A2-8-2 | B2-8-2 | U-A2-40 / 2P 30A | U-B2-40 / 2P 30A | 6-DaHall 1-PDU-03-30-40 | 6-DaHall 1-PDU-04-30-40 | 220 | 30 | 03 | 40 | 220 | 30 | 04 | 40 | U-A2 4P 200A | U-B2 4P 200A | UPS 출력배전반(A) #02, 4P 200A | UPS 출력배전반(B) #04, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0
A605 | 6F-W16 |  |  | A2-8-3 | B2-8-3 | U-A2-42 / 2P 30A | U-B2-42 / 2P 30A | 6-DaHall 1-PDU-03-30-42 | 6-DaHall 1-PDU-04-30-42 | 220 | 30 | 03 | 42 | 220 | 30 | 04 | 42 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A606 | 6F-W15 |  |  | A2-8-4 | B2-8-4 | U-A2-44 / 2P 30A | U-B2-44 / 2P 30A | 6-DaHall 1-PDU-03-30-44 | 6-DaHall 1-PDU-04-30-44 | 220 | 30 | 03 | 44 | 220 | 30 | 04 | 44 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A607 | 6F-W14 |  |  | A2-8-5 | B2-8-5 | U-A2-46 / 2P 30A | U-B2-46 / 2P 30A | 6-DaHall 1-PDU-03-30-46 | 6-DaHall 1-PDU-04-30-46 | 220 | 30 | 03 | 46 | 220 | 30 | 04 | 46 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A608 | 6F-W13 |  |  | A2-8-6 | B2-8-6 | U-A2-48 / 2P 30A | U-B2-48 / 2P 30A | 6-DaHall 1-PDU-03-30-48 | 6-DaHall 1-PDU-04-30-48 | 220 | 30 | 03 | 48 | 220 | 30 | 04 | 48 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | A6-8-6(1) | B6-8-6(1) | U6-A6-45 / 2P 30A | U6-B6-47 / 2P 30A | 6-DaHall 1-PDU-07-30-45 | 6-DaHall 1-PDU-08-30-47 | 220 | 30 | 07 | 45 | 220 | 30 | 08 | 47 | U6-A6 4P 300A | U6-B6 4P 300A | LV-6A #06, 3P 320A | LV-6B #02, 3P 320A |  |  | 0 | 0 |  | 0 | 0
A609 | 6F-W12 |  |  | A5-8-7 | B5-8-7 | U6-A5-01 / 2P 30A | U6-B5-01 / 2P 30A | 6-DaHall 1-PDU-05-30-1 | 6-DaHall 1-PDU-06-30-1 | 220 | 30 | 05 | 1 | 220 | 30 | 06 | 1 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | A6-8-7(1) | B6-8-7(1) | U6-A6-43 / 2P 30A | U6-B6-45 / 2P 30A | 6-DaHall 1-PDU-07-30-43 | 6-DaHall 1-PDU-08-30-45 | 220 | 30 | 07 | 43 | 220 | 30 | 08 | 45 | U6-A6 4P 300A | U6-B6 4P 300A | LV-6A #06, 3P 320A | LV-6B #02, 3P 320A |  |  | 0 | 0 |  | 0 | 0
A610 | 6F-W11 |  |  | A5-8-8 | B5-8-8 | U6-A5-03 / 2P 30A | U6-B5-03 / 2P 30A | 6-DaHall 1-PDU-05-30-3 | 6-DaHall 1-PDU-06-30-3 | 220 | 30 | 05 | 3 | 220 | 30 | 06 | 3 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | A6-8-8(1) | B6-8-8(1) | U6-A6-41 / 2P 30A | U6-B6-43 / 2P 30A | 6-DaHall 1-PDU-07-30-41 | 6-DaHall 1-PDU-08-30-43 | 220 | 30 | 07 | 41 | 220 | 30 | 08 | 43 | U6-A6 4P 300A | U6-B6 4P 300A | LV-6A #06, 3P 320A | LV-6B #02, 3P 320A |  |  | 0 | 0 |  | 0 | 0
| 6F-X19 | [24 empty] | 0 |  |  | 0 | 랙 미설치
| 6F-X18 | [24 empty] | 0 |  |  | 0 | 랙 미설치
| 6F-X17 |  |  | A5-9-2 | B5-9-2 | U6-A5-07 / 2P 30A | U6-B5-07 / 2P 30A | 6-DaHall 1-PDU-05-30-7 | 6-DaHall 1-PDU-06-30-7 | 220 | 30 | 05 | 7 | 220 | 30 | 06 | 7 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 1.9103 | 3.3356 | 5.2459 | 0 | 0 | 0 | 랙 미설치
| 6F-X16 |  |  | A5-9-3 | B5-9-3 | U6-A5-09 / 2P 30A | U6-B5-09 / 2P 30A | 6-DaHall 1-PDU-05-30-9 | 6-DaHall 1-PDU-06-30-9 | 220 | 30 | 05 | 9 | 220 | 30 | 06 | 9 | [6 empty] | 0.89207 | 0.85562 | 1.7477 | 0 | 0 | 0 | 랙 미설치
A706 | 6F-X15 | 주식회사 씨엘엠앤에스 | 1.1 | A5-9-4 | B5-9-4 | U6-A5-11 / 2P 30A | U6-B5-11 / 2P 30A | 6-DaHall 1-PDU-05-30-11 | 6-DaHall 1-PDU-06-30-11 | 220 | 30 | 05 | 11 | 220 | 30 | 06 | 11 | [6 empty] | 1.679 | 1.844 | 3.523 | 157.4 | 187.3 | 344.7
A707 | 6F-X14 | 주식회사 씨엘엠앤에스 | 2.2 | A5-9-5 | B5-9-5 | U6-A5-13 / 2P 30A | U6-B5-13 / 2P 30A | 6-DaHall 1-PDU-05-30-13 | 6-DaHall 1-PDU-06-30-13 | 220 | 30 | 05 | 13 | 220 | 30 | 06 | 13 | [6 empty] | 2.1577 | 3.2965 | 5.4542 | 205.1 | 420.6 | 625.7
A708 | 6F-X13 | 주식회사 씨엘엠앤에스 | 2.2 | A5-9-6 | B5-9-6 | U6-A5-15 / 2P 30A | U6-B5-15 / 2P 30A | 6-DaHall 1-PDU-05-30-15 | 6-DaHall 1-PDU-06-30-15 | 220 | 30 | 05 | 15 | 220 | 30 | 06 | 15 | [6 empty] | 3.4769 | 2.8372 | 6.3141 | 481.3 | 430.9 | 912.2
A709 | 6F-X12 | 주식회사 씨엘엠앤에스 | 1.1 | A5-9-7 | B5-9-7 | U6-A5-17 / 2P 30A | U6-B5-17 / 2P 30A | 6-DaHall 1-PDU-05-30-17 | 6-DaHall 1-PDU-06-30-17 | 220 | 30 | 05 | 17 | 220 | 30 | 06 | 17 | [6 empty] | 0.98465 | 0.96036 | 1.945 | 121.8 | 115.9 | 237.7
A710 |  |  |  | A5-9-8 | B5-9-8 | U6-A5-19 / 2P 30A | U6-B5-19 / 2P 30A | 6-DaHall 1-PDU-05-30-19 | 6-DaHall 1-PDU-06-30-19 | 220 | 30 | 05 | 19 | 220 | 30 | 06 | 19 | [6 empty] | 6.0168 | 6.2576 | 12.2743 | 0 | 0 | 0
| 6F-Y19 | [24 empty] | 0 |  |  | 0 | 랙 미설치
| 6F-Y18 | [24 empty] | 0 |  |  | 0 | 랙 미설치
| 6F-Y17 |  |  | A5-10-2 | B5-10-2 | U6-A5-23 / 2P 30A | U6-B5-23 / 2P 30A | [10 empty] | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA |  |  | 0 |  |  | 0 | 랙 미설치
A806 | 6F-Y16 | Pyler | 12 | A5-10-3 | B5-10-3 | U6-A5-25 / 2P 30A | U6-B5-25 / 2P 30A | 6-DaHall 1-PDU-05-30-25 | 6-DaHall 1-PDU-06-30-25 | 220 | 30 | 05 | 25 | 220 | 30 | 06 | 25 | [6 empty] | 4.0564 | 2.3916 | 6.448 | 450.9 | 386.4 | 1647.4
| 6F-Y15 |  |  | A5-10-4 | B5-10-4 | U6-A5-27 / 2P 30A | U6-B5-27 / 2P 30A | 6-DaHall 1-PDU-05-30-27 | 6-DaHall 1-PDU-06-30-27 | 220 | 30 | 05 | 27 | 220 | 30 | 06 | 27 | [6 empty] | 3.8298 | 1.7876 | 5.6174 | 519 | 291.1
A807 | 6F-Y14 | Pyler | 12 | A5-10-5 | B5-10-5 | U6-A5-29 / 2P 30A | U6-B5-29 / 2P 30A | 6-DaHall 1-PDU-05-30-29 | 6-DaHall 1-PDU-06-30-29 | 220 | 30 | 05 | 29 | 220 | 30 | 06 | 29 | [6 empty] | 3.0856 | 1.9383 | 14.304 | 297.2 | 155.9 | 453.1
|  |  |  | A5-10-2 | B5-10-2 | U6-A5-23 / 2P 30A | U6-B5-23 / 2P 30A | 6-DaHall 1-PDU-05-30-23 | 6-DaHall 1-PDU-06-30-23 | 220 | 30 | 05 | 23 | 220 | 30 | 06 | 23 | [6 empty] | 4.6003 | 4.6799 |  | 0 | 0
A808 | 6F-Y13 | Servis | 1.6 | A5-10-6 | B5-10-6 | U6-A5-31 / 2P 30A | U6-B5-31 / 2P 30A | 6-DaHall 1-PDU-05-30-31 | 6-DaHall 1-PDU-06-30-31 | 220 | 30 | 05 | 31 | 220 | 30 | 06 | 31 | [6 empty] | 1.7472 | 0.94217 | 2.6893 | 241.5 | 43.9 | 285.4
A809 | 6F-Y12 | Terrapin Tech Co., Ltd. | 1.6 | A5-10-7 | B5-10-7 | U6-A5-33 / 2P 30A | U6-B5-33 / 2P 30A | 6-DaHall 1-PDU-05-30-33 | 6-DaHall 1-PDU-06-30-33 | 220 | 30 | 05 | 33 | 220 | 30 | 06 | 33 | [6 empty] | 1.1758 | 1.1485 | 2.3243 | 140.8 | 140 | 280.8
A810 | 6F-Y11 | Sejong Telecom Inc. | 1.6 | A5-10-8 | B5-10-8 | U6-A5-35 / 2P 30A | U6-B5-35 / 2P 30A | 6-DaHall 1-PDU-05-30-35 | 6-DaHall 1-PDU-06-30-35 | 220 | 30 | 05 | 35 | 220 | 30 | 06 | 35 | [6 empty] | 1.2189 | 1.0842 | 2.3031 | 84.7 | 43 | 127.7
B115 | [28 empty] | 0 | 랙 미설치
B116 | 6F-S11 |  |  | A4-36-3 | B4-36-3 | U-A4-23 / 2P 30A | U-B4-23 / 2P 30A | 6-DaHall 1-PDU-11-30-23 | 6-DaHall 1-PDU-12-30-23 | 220 | 30 | 11 | 23 | 220 | 30 | 12 | 23 | U-A4 4P 200A | U-B4 4P 200A | UPS 출력배전반(A) #01, 4P 200A | UPS 출력배전반(B) #01, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치
B117 | 6F-S12 |  |  | A4-36-4 | B4-36-4 | U-A4-25 / 2P 30A | U-B4-25 / 2P 30A | 6-DaHall 1-PDU-11-30-25 | 6-DaHall 1-PDU-12-30-25 | 220 | 30 | 11 | 25 | 220 | 30 | 12 | 25 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치
B118 | 6F-S13 |  |  | A4-36-5 | B4-36-5 | U-A4-27 / 2P 30A | U-B4-27 / 2P 30A | 6-DaHall 1-PDU-11-30-27 | 6-DaHall 1-PDU-12-30-27 | 220 | 30 | 11 | 27 | 220 | 30 | 12 | 27 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | U-A4-49 | U-B4-49 | U-A4-49 / 2P 30A | U-B4-49 / 2P 30A | 6-DaHall 1-PDU-11-30-49 | 6-DaHall 1-PDU-12-30-49 | 220 | 30 | 11 | 49 | 220 | 30 | 12 | 49 | [6 empty] | 0 | 0 | 0 | 0 | 0
B119 | 6F-S14 |  |  | A4-36-6 | B4-36-6 | U-A4-29 / 2P 30A | U-B4-29 / 2P 30A | 6-DaHall 1-PDU-11-30-29 | 6-DaHall 1-PDU-12-30-29 | 220 | 30 | 11 | 29 | 220 | 30 | 12 | 29 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
B120 | 6F-S15 |  |  | A4-36-7 | B4-36-7 | U-A4-31 / 2P 30A | U-B4-31 / 2P 30A | 6-DaHall 1-PDU-11-30-31 | 6-DaHall 1-PDU-12-30-31 | 220 | 30 | 11 | 31 | 220 | 30 | 12 | 31 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | U-A4-47 | U-B4-47 | U-A4-47 / 2P 30A | U-B4-47 / 2P 30A | 6-DaHall 1-PDU-11-30-47 | 6-DaHall 1-PDU-12-30-47 | 220 | 30 | 11 | 47 | 220 | 30 | 12 | 47 | [6 empty] | 0 | 0 | 0 | 0 | 0
B121 | 6F-S16 |  |  | A4-36-8 | B4-36-8 | U-A4-33 / 2P 30A | U-B4-33 / 2P 30A | 6-DaHall 1-PDU-11-30-33 | 6-DaHall 1-PDU-12-30-33 | 220 | 30 | 11 | 33 | 220 | 30 | 12 | 33 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
B122 | 6F-S17 | [27 empty] | 0 | 랙 미설치
B123 | 6F-S18 | [27 empty] | 0 | 랙 미설치
B124 | 6F-S19 | [27 empty] | 0 | 랙 미설치
B125 | [28 empty] | 0 | 랙 미설치
B201 |  | Net Target | 2.2 | A1-13-5 | B1-13-5 |  |  | 6-DaHall 1-PDU-01-30-25 | 6-DaHall 1-PDU-02-30-25 | 220 | 30 | 01 | 25 | 220 | 30 | 02 | 25 | U-A1 4P 200A | U-B1 4P 200A | UPS 출력배전반(A) #04, 4P 200A | UPS 출력배전반(B) #02, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 1.8536 | 2.1427 | 3.9963 | 285.8 | 335.9 | 621.7
B202 | 6F-AA11 | Digital Edge Korea | 2.2 | A1-13-1 | B1-13-1 | U-A1-27 / 2P 30A | U-B1-27 / 2P 30A | 6-DaHall 1-PDU-01-30-27 | 6-DaHall 1-PDU-02-30-27 | 220 | 30 | 01 | 27 | 220 | 30 | 02 | 27 | [6 empty] | 2.4816 | 1.4932 | 3.9748 | 301.3 | 180.4 | 481.7
B203 | 6F-AA12 | Digital Edge Korea | 2.2 | A1-13-2 | B1-13-2 | U-A1-29 / 2P 30A | U-B1-29 / 2P 30A | 6-DaHall 1-PDU-01-30-29 | 6-DaHall 1-PDU-02-30-29 | 220 | 30 | 01 | 29 | 220 | 30 | 02 | 29 | [6 empty] | 4.5167 | 3.0425 | 7.5592 | 0 | 0 | 0
B204 | 6F-AA13 | Net Target | 2.2 | A1-13-3 | B1-13-3 | U-A1-31 / 2P 30A | U-B1-31 / 2P 30A | 6-DaHall 1-PDU-01-30-31 | 6-DaHall 1-PDU-02-30-31 | 220 | 30 | 01 | 31 | 220 | 30 | 02 | 31 | [6 empty] | 3.0449 | 3.3323 | 6.3772 | 267.1 | 257.5 | 524.6
B205 | 6F-AA14 | Net Target | 2.2 | A1-13-4 | B1-13-4 | U-A1-33 / 2P 30A | U-B1-33 / 2P 30A | 6-DaHall 1-PDU-01-30-33 | 6-DaHall 1-PDU-02-30-33 | 220 | 30 | 01 | 33 | 220 | 30 | 02 | 33 | [6 empty] | 2.3846 | 2.5159 | 4.9006 | 240.4 | 273.7 | 514.1
B206 | 6F-AA15 | Net Target | 6 | A1-13-5 | B1-13-5 | U-A1-35 / 2P 30A | U-B1-35 / 2P 30A | 6-DaHall 1-PDU-01-30-35 | 6-DaHall 1-PDU-02-30-35 | 220 | 30 | 01 | 35 | 220 | 30 | 02 | 35 | [6 empty] | 0.66837 | 0.62026 | 1.2886 | 90.7 | 84.5 | 175.2
B207 | 6F-AA16 |  |  | A1-13-6 | B1-13-6 | U-A1-37 / 2P 30A | U-B1-37 / 2P 30A | 6-DaHall 1-PDU-01-30-37 | 6-DaHall 1-PDU-02-30-37 | 220 | 30 | 01 | 37 | 220 | 30 | 02 | 37 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
B208 | 6F-AA17 | Net Target | 2.2 | A1-13-7 | B1-13-7 | U-A1-39 / 2P 30A | U-B1-39 / 2P 30A | 6-DaHall 1-PDU-01-30-39 | 6-DaHall 1-PDU-02-30-39 | 220 | 30 | 01 | 39 | 220 | 30 | 02 | 39 | [6 empty] | 0.23171 | 0.21443 | 0.44615 | 34.3 | 30.8 | 65.1
B209 | 6F-AA18 | Piolink | 2.2 | A1-13-8 | B1-13-8 | U-A1-41 / 2P 30A | U-B1-41 / 2P 30A | 6-DaHall 1-PDU-01-30-41 | 6-DaHall 1-PDU-02-30-41 | 220 | 30 | 01 | 41 | 220 | 30 | 02 | 41 | [6 empty] | 0.79308 | 0.61769 | 1.4108 | 114.5 | 84.5 | 199
B210 | 6F-AA19 | RXN Co., Ltd. | 4.4 | A1-13-8(2) | B1-13-8(2) | U-A1-49 / 2P 30A | U-B1-30 / 2P 30A | 6-DaHall 1-PDU-01-30-49 | 6-DaHall 1-PDU-02-30-30 | 220 | 30 | 01 | 49 | 220 | 30 | 02 | 30 | [6 empty] | 7.7034 | 7.8247 | 15.5281 | 958 | 949.9 | 1907.9 | 랙 미설치
B211 | [7 empty] | 6-DaHall 1-PDU-01-30-44 | 6-DaHall 1-PDU-02-30-44 |  | 30 | 01 | 44 | 220 | 30 | 02 | 44 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치
B215 | [28 empty] | 0 | 랙 미설치
B216 | 6F-R11 |  |  | A1-16-1 | B1-16-1 | U-A1-45 / 2P 30A | U-B1-45 / 2P 30A | 6-DaHall 1-PDU-01-30-45 | 6-DaHall 1-PDU-02-30-45 | 220 | 30 | 01 | 45 | 220 | 30 | 02 | 45 | U-A1 4P 200A | U-B1 4P 200A | UPS 출력배전반(A) #04, 4P 200A | UPS 출력배전반(B) #02, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0
B217 | 6F-R12 |  |  | A1-16-2 | B1-16-2 | U-A1-47 / 2P 30A | U-B1-47 / 2P 30A | 6-DaHall 1-PDU-01-30-47 | 6-DaHall 1-PDU-02-30-47 | 220 | 30 | 01 | 47 | 220 | 30 | 02 | 47 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
B218 | 6F-R13 |  |  | A5-16-3 | B5-16-3 | U6-A5-48 / 2P 30A | U6-B5-48 / 2P 30A | 6-DaHall 1-PDU-05-30-48 | 6-DaHall 1-PDU-06-30-48 | 220 | 30 | 05 | 48 | 220 | 30 | 06 | 48 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A |  |  | 0 | 0 | 0 | 0 | 0 | 0
B219 | 6F-R14 |  |  | A1-16-4 | B1-16-4 | U-A1-18 / 2P 30A | U-B1-34 / 2P 30A | 6-DaHall 1-PDU-01-30-18 | 6-DaHall 1-PDU-02-30-34 | 220 | 30 | 01 | 18 | 220 | 30 | 02 | 34 | U-A1 4P 200A | U-B1 4P 200A | UPS 출력배전반(A) #04, 4P 200A | UPS 출력배전반(B) #02, 4P 200A |  |  | 0.65398 | 0 | 0.65398 | 0 | 0 | 0
B220 | 6F-R15 | 에네이 |  | A1-16-5 | B1-16-5 | U-A1-20 / 2P 30A | U-B1-20 / 2P 30A | 6-DaHall 1-PDU-01-30-20 | 6-DaHall 1-PDU-02-30-20 | 220 | 30 | 01 | 20 | 220 | 30 | 02 | 20 | [6 empty] | 0.2262 | 0.20942 | 0.43562 | 0 | 0 | 0 |  | 2023/04/13 장비 이동 확인 후 Off 할 것
B221 | 6F-R16 |  |  | A1-16-6 | B1-16-6 | U-A1-22 / 2P 30A | U-B1-22 / 2P 30A | 6-DaHall 1-PDU-01-30-22 | 6-DaHall 1-PDU-02-30-22 | 220 | 30 | 01 | 22 | 220 | 30 | 02 | 22 | [6 empty] | 4.1864 | 3.4016 | 7.588 | 0 | 0 | 0
B222 | 6F-R17 | 에네이 |  | A1-16-7 | B1-16-7 | U-A1-24 / 2P 30A | U-B1-24 / 2P 30A | 6-DaHall 1-PDU-01-30-24 | 6-DaHall 1-PDU-02-30-24 | 220 | 30 | 01 | 24 | 220 | 30 | 02 | 24 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023/04/13 장비 이동 확인 후 Off 할 것
B223 | 6F-R18 |  |  | A1-16-8 | B1-16-8 | U-A1-26 / 2P 30A | U-B1-26 / 2P 30A | 6-DaHall 1-PDU-01-30-26 | 6-DaHall 1-PDU-02-30-26 | 220 | 30 | 01 | 26 | 220 | 30 | 02 | 26 | [6 empty] | 1.8658 | 1.4034 | 3.2692 | 0 | 0 | 0
B224 | 6F-R19 |  |  | A1-16-9 | B1-16-9 | U-A1-28 / 2P 30A | U-B1-28 / 2P 30A | 6-DaHall 1-PDU-01-30-28 | 6-DaHall 1-PDU-02-30-28 | 220 | 30 | 01 | 28 | 220 | 30 | 02 | 28 | [6 empty] | 2.8519 | 4.9425 | 7.7944 | 0 | 0 | 0
B225 | [28 empty] | 0 | 랙 미설치
B301 | 6F-U10 | RXN Co., Ltd. | 2.2 | A5-14-1 | B5-14-1 | U6-A5-37 / 2P 30A | U6-B5-37 / 2P 30A | 6-DaHall 1-PDU-05-30-37 | 6-DaHall 1-PDU-06-30-37 | 220 | 30 | 05 | 37 | 220 | 30 | 06 | 37 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 2.8963 | 2.7648 | 5.6611 | 544.6 | 520.8 | 1065.4
B302 | 6F-U11 | DVS Network Korea Co., Ltd. | 2.2 | A5-14-2 | B5-14-2 | U6-A5-39 / 2P 30A | U6-B5-39 / 2P 30A | 6-DaHall 1-PDU-05-30-39 | 6-DaHall 1-PDU-06-30-39 | 220 | 30 | 05 | 39 | 220 | 30 | 06 | 39 | [6 empty] | 2.0485 | 1.8605 | 3.909 | 316 | 283.7 | 599.7
B303 | 6F-U12 | Du System Co., Ltd. | 1.1 | A5-14-3 | B5-14-3 | U6-A5-41 / 2P 30A | U6-B5-41 / 2P 30A | 6-DaHall 1-PDU-05-30-41 | 6-DaHall 1-PDU-06-30-41 | 220 | 30 | 05 | 41 | 220 | 30 | 06 | 41 | [6 empty] | 1.6434 | 0.52803 | 2.1714 | 249.4 | 70.3 | 319.7
B304 | 6F-U13 | RXN Co., Ltd. | 2.2 | A5-14-4 | B5-14-4 | U6-A5-43 / 2P 30A | U6-B5-43 / 2P 30A | 6-DaHall 1-PDU-05-30-43 | 6-DaHall 1-PDU-06-30-43 | 220 | 30 | 05 | 43 | 220 | 30 | 06 | 43 | [6 empty] | 5.6121 | 4.77 | 10.3821 | 838.9 | 731.8 | 1570.7
B305 | 6F-U14 | RXN Co., Ltd. | 2.2 | A5-14-5 | B5-14-5 | U6-A5-45 / 2P 30A | U6-B5-45 / 2P 30A | 6-DaHall 1-PDU-05-30-45 | 6-DaHall 1-PDU-06-30-45 | 220 | 30 | 05 | 45 | 220 | 30 | 06 | 45 | [6 empty] | 4.8328 | 4.9243 | 9.7571 | 684.6 | 714.9 | 1399.5
B306 | 6F-U15 | RXN Co., Ltd. | 2.2 | A5-14-6 | B5-14-6 | U6-A5-47 / 2P 30A | U6-B5-47 / 2P 30A | 6-DaHall 1-PDU-05-30-47 | 6-DaHall 1-PDU-06-30-47 | 220 | 30 | 05 | 47 | 220 | 30 | 06 | 47 | [6 empty] | 4.0582 | 3.7379 | 22.3061 | 655.8 | 606.3 | 3581
[8 empty] | 6-DaHall 1-PDU-05-30-51 | 6-DaHall 1-PDU-06-30-51 |  | 30 | 05 | 51 | 220 | 30 | 06 | 51 | [6 empty] | 3.9897 | 4.5523 |  | 624.3 | 721.9
[8 empty] | 6-DaHall 1-PDU-05-30-53 | 6-DaHall 1-PDU-06-30-53 |  | 30 | 05 | 53 | 220 | 30 | 06 | 53 | [6 empty] | 5.3934 | 0.57475 |  | 881.4 | 91.3
B307 | 6F-U16 | Piolink Co., Ltd. | 2.2 | A5-14-7 | B5-14-7 | U6-A5-49 / 2P 30A | U6-B5-49 / 2P 30A | 6-DaHall 1-PDU-05-30-49 | 6-DaHall 1-PDU-06-30-49 | 220 | 30 | 05 | 49 | 220 | 30 | 06 | 49 | [6 empty] | 8.0073 | 1.3018 | 9.3091 | 1205.7 | 187.5 | 1393.2
B308 | 6F-U17 | RXN Co., Ltd. | 2.2 | A5-14-8 | B5-14-8 | U6-A5-51 / 2P 30A | U6-B5-51 / 2P 30A | 6-DaHall 1-PDU-03-30-1 | 6-DaHall 1-PDU-04-30-1 | 220 | 30 | 03 | 1 | 220 | 30 | 04 | 1 | U-A2 4P 200A | U-B2 4P 200A | UPS 출력배전반(A) #02, 4P 200A | UPS 출력배전반(B) #04, 4P 200A |  |  | 4.5856 | 3.411 | 17.6215 | 730 | 534 | 2862.6
[8 empty] | 6-DaHall 1-PDU-03-30-3 | 6-DaHall 1-PDU-04-30-3 |  | 30 | 03 | 3 | 220 | 30 | 04 | 3 | [6 empty] | 3.382 | 3.6815 |  | 645.4 | 699.6
[8 empty] | 6-DaHall 1-PDU-03-30-5 | 6-DaHall 1-PDU-04-30-5 |  | 30 | 03 | 5 | 220 | 30 | 04 | 5 | [6 empty] | 1.208 | 1.3535 |  | 112.1 | 141.5
B309 | 6F-U18 | RXN Co., Ltd. | 2.2 | A5-14-9 | B5-14-9 | U6-A5-53 / 2P 30A | U6-B5-53 / 2P 30A | 6-DaHall 1-PDU-03-30-7 | 6-DaHall 1-PDU-04-30-7 | 220 | 30 | 03 | 7 | 220 | 30 | 04 | 7 | [6 empty] | 4.0385 | 3.7081 | 15.0292 | 562.8 | 604.9 | 2361
[8 empty] | 6-DaHall 1-PDU-03-30-9 | 6-DaHall 1-PDU-04-30-9 |  | 30 | 03 | 9 | 220 | 30 | 04 | 9 | [6 empty] | 3.4999 | 3.7827 |  | 562.4 | 630.9
B310 |  | RXN Co., Ltd. | 2.2 |  |  |  |  | 6-DaHall 1-PDU-03-30-11 | 6-DaHall 1-PDU-04-30-11 | 220 | 30 | 03 | 11 | 220 | 30 | 04 | 11 | [6 empty] | 2.8968 | 4.349 | 15.0135 | 465.8 | 710 | 2409.6
[8 empty] | 6-DaHall 1-PDU-03-30-13 | 6-DaHall 1-PDU-04-30-13 |  | 30 | 03 | 13 | 220 | 30 | 04 | 13 | [6 empty] | 5.0606 | 2.7069 |  | 799.8 | 434
B311 |  | RXN Co., Ltd. | 2.2 |  |  |  |  | 6-DaHall 1-PDU-03-30-15 | 6-DaHall 1-PDU-04-30-15 |  | 30 | 03 | 15 | 220 | 30 | 04 | 15 | [6 empty] | 3.9056 | 3.6241 | 11.3199 | 584.4 | 535.3 | 1661.4
[8 empty] | 6-DaHall 1-PDU-03-30-17 | 6-DaHall 1-PDU-04-30-17 | 220 | 30 | 03 | 17 | 220 | 30 | 04 | 17 | [6 empty] | 1.9962 | 1.794 |  | 287.9 | 253.8
B315 | [28 empty] | 0 | 랙 미설치
B316 | 6F-Q11 |  |  | A5-17-1 | B5-17-1 | U6-A5-20 / 2P 30A | U6-B5-20 / 2P 30A | 6-DaHall 1-PDU-05-30-20 | 6-DaHall 1-PDU-06-30-20 | 220 | 30 | 05 | 20 | 220 | 30 | 06 | 20 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 1.9902 | 1.8103 | 3.8005 | 0 | 0 | 0
B317 | 6F-Q12 |  |  | A5-17-2 | B5-17-2 | U6-A5-22 / 2P 30A | U6-B5-22 / 2P 30A | 6-DaHall 1-PDU-05-30-22 | 6-DaHall 1-PDU-06-30-22 | 220 | 30 | 05 | 22 | 220 | 30 | 06 | 22 | [6 empty] | 5.4581 | 4.6349 | 10.093 | 0 | 0 | 0
B318 | 6F-Q13 |  |  | A5-17-3 | B5-17-3 | U6-A5-24 / 2P 30A | U6-B5-24 / 2P 30A | 6-DaHall 1-PDU-05-30-24 | 6-DaHall 1-PDU-06-30-24 | 220 | 30 | 05 | 24 | 220 | 30 | 06 | 24 | [6 empty] | 3.9811 | 3.6619 | 7.643 | 0 | 0 | 0
B319 | 6F-Q14 |  |  | A5-17-4 | B5-17-4 | U6-A5-26 / 2P 30A | U6-B5-26 / 2P 30A | 6-DaHall 1-PDU-05-30-26 | 6-DaHall 1-PDU-06-30-26 | 220 | 30 | 05 | 26 | 220 | 30 | 06 | 26 | [6 empty] | 4.0684 | 4.6273 | 8.6957 | 0 | 0 | 0
B320 | 6F-Q15 |  |  | A5-17-5 | B5-17-5 | U6-A5-28 / 2P 30A | U6-B5-28 / 2P 30A | 6-DaHall 1-PDU-05-30-28 | 6-DaHall 1-PDU-06-30-28 | 220 | 30 | 05 | 28 | 220 | 30 | 06 | 28 | [6 empty] | 11.2911 | 10.2002 | 21.4913 | 0 | 0 | 0
B321 | 6F-Q16 |  |  | A5-17-6 | B5-17-6 | U6-A5-30 / 2P 30A | U6-B5-30 / 2P 30A | 6-DaHall 1-PDU-05-30-30 | 6-DaHall 1-PDU-06-30-30 | 220 | 30 | 05 | 30 | 220 | 30 | 06 | 30 | [6 empty] | 0.67087 | 0.65334 | 1.3242 | 0 | 0 | 0
B322 | 6F-Q17 |  |  | A5-17-7 | B5-17-7 | U6-A5-32 / 2P 30A | U6-B5-32 / 2P 30A | 6-DaHall 1-PDU-05-30-32 | 6-DaHall 1-PDU-06-30-32 | 220 | 30 | 05 | 32 | 220 | 30 | 06 | 32 | [6 empty] | 0.80332 | 0.51022 | 1.3135 | 0 | 0 | 0
B323 | 6F-Q18 |  |  | A5-17-8 | B5-17-8 | U6-A5-34 / 2P 30A | U6-B5-34 / 2P 30A | 6-DaHall 1-PDU-05-30-34 | 6-DaHall 1-PDU-06-30-34 | 220 | 30 | 05 | 34 | 220 | 30 | 06 | 34 | [6 empty] | 4.6033 | 3.0602 | 7.6635 | 0 | 0 | 0
B324 | 6F-Q19 |  |  | A5-17-9 | B5-17-9 | U6-A5-36 / 2P 30A | U6-B5-36 / 2P 30A | 6-DaHall 1-PDU-05-30-36 | 6-DaHall 1-PDU-06-30-36 | 220 | 30 | 05 | 36 | 220 | 30 | 06 | 36 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
B325 | [28 empty] | 0 | 랙 미설치
B401 |  | 주식회사 메타넷티플랫폼 | 2.2 | A5-15-5(2) | B5-15-5(2) | U6-A5-54 / 2P 30A | U6-B5-54 / 2P 30A | 6-DaHall 1-PDU-05-30-54 | 6-DaHall 1-PDU-06-30-54 | 220 | 30 | 05 | 54 | 220 | 30 | 06 | 54 | [6 empty] | 4.2204 | 2.4267 | 6.6471 | 592.4 | 352.1 | 944.5 | 랙 미설치 | 제로투세븐(메타넷) 이동설치 예정(4/15)
B402 | 6F-T11 | 주식회사 메타넷티플랫폼 | 2.2 | A5-15-1 | B5-15-1 | U6-A5-02 / 2P 30A | U6-B5-02 / 2P 30A | 6-DaHall 1-PDU-05-30-2 | 6-DaHall 1-PDU-06-30-2 | 220 | 30 | 05 | 2 | 220 | 30 | 06 | 2 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 11.2383 | 10.1692 | 21.4075 | 1818.7 | 1641 | 3459.7 | 랙 미설치 | 제로투세븐(메타넷) 이동설치 예정(4/15)
B403 | 6F-T12 | U.I.WINS | 2.2 | A5-15-2 | B5-15-2 | U6-A5-04 / 2P 30A | U6-B5-04 / 2P 30A | 6-DaHall 1-PDU-05-30-4 | 6-DaHall 1-PDU-06-30-4 | 220 | 30 | 05 | 4 | 220 | 30 | 06 | 4 | [6 empty] | 5.0572 | 3.9771 | 9.0343 | 745.1 | 608.4 | 1353.5
B404 | 6F-T13 | ETSIN Co., Ltd. | 2.2 | A5-15-3 | B5-15-3 | U6-A5-06 / 2P 30A | U6-B5-06 / 2P 30A | 6-DaHall 1-PDU-05-30-6 | 6-DaHall 1-PDU-06-30-6 | 220 | 30 | 05 | 6 | 220 | 30 | 06 | 6 | [6 empty] | 0.90135 | 0.91604 | 1.8174 | 92.8 | 89.4 | 182.2
B405 | 6F-T14 | Dongyang & I&C Co., Ltd. | 1.1 | A5-15-4 | B5-15-4 | U6-A5-08 / 2P 30A | U6-B5-08 / 2P 30A | 6-DaHall 1-PDU-05-30-8 | 6-DaHall 1-PDU-06-30-8 | 220 | 30 | 05 | 8 | 220 | 30 | 06 | 8 | [6 empty] | 2.8769 | 3.3545 | 6.2314 | 360.7 | 494.9 | 855.6
B406 | 6F-T15 |  | 2.2 | A5-15-5 | B5-15-5 | U6-A5-10 / 2P 30A | U6-B5-10 / 2P 30A | 6-DaHall 1-PDU-05-30-10 | 6-DaHall 1-PDU-06-30-10 | 220 | 30 | 05 | 10 | 220 | 30 | 06 | 10 | [6 empty] | 0.81076 | 0.52556 | 1.3363 | 103.3 | 68.9 | 172.2 |  | 제로투세븐(메타넷) 이동설치 예정(4/15)
B407 | 6F-T16 | ELIMNET Co., Ltd. | 0.55 | A5-15-6 | B5-15-6 | U6-A5-12 / 2P 30A | U6-B5-12 / 2P 30A | 6-DaHall 1-PDU-05-30-12 | 6-DaHall 1-PDU-06-30-12 | 220 | 30 | 05 | 12 | 220 | 30 | 06 | 12 | [6 empty] | 1.3706 | 0 | 1.3706 | 203.2 | 0 | 203.2
B408 | 6F-T17 | MarkPro | 2.2 | A5-15-7 | B5-15-7 | U6-A5-14 / 2P 30A | U6-B5-14 / 2P 30A | 6-DaHall 1-PDU-05-30-14 | 6-DaHall 1-PDU-06-30-14 | 220 | 30 | 05 | 14 | 220 | 30 | 06 | 14 | [6 empty] | 4.6426 | 2.8993 | 7.5419 | 740.1 | 433 | 1173.1
B409 | 6F-T18 | MarkPro | 2.2 | A5-15-8 | B5-15-8 | U6-A5-16 / 2P 30A | U6-B5-16 / 2P 30A | 6-DaHall 1-PDU-05-30-16 | 6-DaHall 1-PDU-06-30-16 | 220 | 30 | 05 | 16 | 220 | 30 | 06 | 16 | [6 empty] | 3.0141 | 3.516 | 6.5301 | 471.2 | 607.1 | 1078.3
B410 | 6F-T19 | Enei | 1.1 | A1-13-9 | B1-13-9 | U-A1-43 / 2P 30A | U-B1-43 / 2P 30A | 6-DaHall 1-PDU-01-30-43 | 6-DaHall 1-PDU-02-30-43 | 220 | 30 | 01 | 43 | 220 | 30 | 02 | 43 | U-A1 4P 200A | U-B1 4P 200A | UPS 출력배전반(A) #04, 4P 200A | UPS 출력배전반(B) #02, 4P 200A |  |  | 3.2719 | 3.5921 | 6.864 | 593.7 | 600.7 | 1194.4 | 2023/04/13 이설 후 전기사용예정
B411 |  | Enei | 2.2 |  |  | U-A1-42 / 2P 30A | U-B1-42 / 2P 30A | 6-DaHall 1-PDU-01-30-42 | 6-DaHall 1-PDU-02-30-42 | 220 | 30 | 01 | 42 | 220 | 30 | 02 | 42 | [6 empty] | 3.7994 | 3.956 | 7.7554 | 595 | 612.1 | 1207.1 | 2023/04/13 이설 후 전기사용예정
B415 | [28 empty] | 0 | 랙 미설치
B416 | 6F-P11 |  |  | A5-18-1 | B5-18-1 | U6-A5-38 / 2P 30A | U6-B5-38 / 2P 30A | 6-DaHall 1-PDU-05-30-38 | 6-DaHall 1-PDU-06-30-38 | 220 | 30 | 05 | 38 | 220 | 30 | 06 | 38 | U6-A5 4P 300A | U6-B5 4P 300A | LV-6A #05, 3P 320A | LV-6B #01, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치
B417 | 6F-P12 |  |  | A5-18-2 | B5-18-2 | U6-A5-40 / 2P 30A | U6-B5-40 / 2P 30A | 6-DaHall 1-PDU-05-30-40 | 6-DaHall 1-PDU-06-30-40 | 220 | 30 | 05 | 40 | 220 | 30 | 06 | 40 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치
B418 | 6F-P13 |  |  | A5-18-3 | B5-18-3 | U6-A5-42 / 2P 30A | U6-B5-42 / 2P 30A | 6-DaHall 1-PDU-05-30-42 | 6-DaHall 1-PDU-06-30-42 | 220 | 30 | 05 | 42 | 220 | 30 | 06 | 42 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치
B419 | 6F-P14 |  |  | A5-18-4 | B5-18-4 | U6-A5-44 / 2P 30A | U6-B5-44 / 2P 30A | 6-DaHall 1-PDU-05-30-44 | 6-DaHall 1-PDU-06-30-44 | 220 | 30 | 05 | 44 | 220 | 30 | 06 | 44 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치
B420 | 6F-P15 |  |  | A5-18-5 | B5-18-5 | U6-A5-46 / 2P 30A | U6-B5-46 / 2P 30A | 6-DaHall 1-PDU-05-30-46 | 6-DaHall 1-PDU-06-30-46 | 220 | 30 | 05 | 46 | 220 | 30 | 06 | 46 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치
B421 | 6F-P16 |  |  | A7-18-6 | B7-18-6 | U6-A7-01 / 2P 30A | U6-B7-01 / 2P 30A | 6-DaHall 1-PDU-13-30-1 | 6-DaHall 1-PDU-14-30-1 | 220 | 30 | 13 | 1 | 220 | 30 | 14 | 1 | U6-A7 4P 300A | U6-B7 4P 300A | LV-6A #07, 3P 320A | LV-6B #03, 3P 320A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치
B422 | 6F-P17 |  |  | A7-18-7 | B7-18-7 | U6-A7-03 / 2P 30A | U6-B7-03 / 2P 30A | 6-DaHall 1-PDU-13-30-3 | 6-DaHall 1-PDU-14-30-3 | 220 | 30 | 13 | 3 | 220 | 30 | 14 | 3 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치
B423 | 6F-P18 |  |  | A7-18-8 | B7-18-8 | U6-A7-05 / 2P 30A | U6-B7-05 / 2P 30A | 6-DaHall 1-PDU-13-30-5 | 6-DaHall 1-PDU-14-30-5 | 220 | 30 | 13 | 5 | 220 | 30 | 14 | 5 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치
B424 | 6F-P19 |  |  | A7-18-9 | B7-18-9 | U6-A7-07 / 2P 30A | U6-B7-07 / 2P 30A | 6-DaHall 1-PDU-13-30-7 | 6-DaHall 1-PDU-14-30-7 | 220 | 30 | 13 | 7 | 220 | 30 | 14 | 7 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치
B425 | [28 empty] | 0 | 랙 미설치
C101 | [28 empty] | 0 | 랙 미설치
C102 | 6F-O11 |  |  | A4-19-1 | B4-19-1 | U6-A7-52 / 2P 30A | U6-B7-52 / 2P 30A | 6-DaHall 1-PDU-13-30-52 | 6-DaHall 1-PDU-14-30-52 | 220 | 30 | 13 | 52 | 220 | 30 | 14 | 52 | U6-A7 4P 300A | U6-B7 4P 300A | LV-6A #07, 3P 320A | LV-6B #03, 3P 320A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0
C103 | 6F-O12 |  |  | A4-19-2 | B4-19-2 | U-A4-03 / 2P 30A | U-B4-03 / 2P 30A | 6-DaHall 1-PDU-11-30-3 | 6-DaHall 1-PDU-12-30-3 | 220 | 30 | 11 | 3 | 220 | 30 | 12 | 3 | U-A4 4P 200A | U-B4 4P 200A | UPS 출력배전반(A) #01, 4P 200A | UPS 출력배전반(B) #01, 4P 200A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 철거완료(9/1)
C104 | 6F-O13 |  |  | A4-19-3 | B4-19-3 | U-A4-05 / 2P 30A | U-B4-05 / 2P 30A | 6-DaHall 1-PDU-11-30-5 | 6-DaHall 1-PDU-12-30-5 | 220 | 30 | 11 | 5 | 220 | 30 | 12 | 5 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C105 | 6F-O14 |  |  | A4-19-4 | B4-19-4 | U-A4-07 / 2P 30A | U-B4-07 / 2P 30A | 6-DaHall 1-PDU-11-30-7 | 6-DaHall 1-PDU-12-30-7 | 220 | 30 | 11 | 7 | 220 | 30 | 12 | 7 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C106 | 6F-O15 |  |  | A4-19-5 | B4-19-5 | U-A4-09 / 2P 30A | U-B4-09 / 2P 30A | 6-DaHall 1-PDU-11-30-9 | 6-DaHall 1-PDU-12-30-9 | 220 | 30 | 11 | 9 | 220 | 30 | 12 | 9 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 철거완료(9/1)
C107 | 6F-O16 |  |  | A4-19-6 | B4-19-6 | U-A4-11 / 2P 30A | U-B4-11 / 2P 30A | 6-DaHall 1-PDU-11-30-11 | 6-DaHall 1-PDU-12-30-11 | 220 | 30 | 11 | 11 | 220 | 30 | 12 | 11 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 철거완료(9/1)
C108 | 6F-O17 |  |  | A4-19-7 | B4-19-7 | U-A4-13 / 2P 30A | U-A3-31 / 2P 30A | 6-DaHall 1-PDU-11-30-13 | 6-DaHall 1-PDU-09-30-31 | 220 | 30 | 11 | 13 | 220 | 30 | 09 | 31 |  | U-A3 4P 200A |  | UPS 출력배전반(A) #03, 4P 200A |  | TR-6A 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 철거완료(9/1)
C109 | 6F-O18 |  |  | A4-19-8 | B4-19-8 | U-A4-15 / 2P 30A | U-B4-15 / 2P 30A | 6-DaHall 1-PDU-11-30-15 | 6-DaHall 1-PDU-12-30-15 | 220 | 30 | 11 | 15 | 220 | 30 | 12 | 15 |  | U-B4 4P 200A |  | UPS 출력배전반(B) #01, 4P 200A |  | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | 철거완료(9/1)
C110 | 6F-O19 |  |  | A4-19-9 | B4-19-9 | U-A4-17 / 2P 30A | U-B4-17 / 2P 30A | 6-DaHall 1-PDU-11-30-17 | 6-DaHall 1-PDU-12-30-17 | 220 | 30 | 11 | 17 | 220 | 30 | 12 | 17 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C201 | [28 empty] | 0 | 랙 미설치
C202 | 6F-N11 |  |  | A4-20-1 | B4-20-1 | U-A4-02 / 2P 30A | U-B4-02 / 2P 30A | 6-DaHall 1-PDU-11-30-2 | 6-DaHall 1-PDU-12-30-2 | 220 | 30 | 11 | 2 | 220 | 30 | 12 | 2 | U-A4 4P 200A | U-B4 4P 200A | UPS 출력배전반(A) #01, 4P 200A | UPS 출력배전반(B) #01, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0 | CB Off (22년 5월)
C203 | 6F-N12 |  |  | A4-20-2 | B4-20-2 | U-A4-04 / 2P 30A | U-B4-04 / 2P 30A | 6-DaHall 1-PDU-11-30-4 | 6-DaHall 1-PDU-12-30-4 | 220 | 30 | 11 | 4 | 220 | 30 | 12 | 4 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | CB Off (22년 5월)
C204 | 6F-N13 |  |  | A4-20-3 | B4-20-3 | U-A4-06 / 2P 30A | U-B4-06 / 2P 30A | 6-DaHall 1-PDU-11-30-6 | 6-DaHall 1-PDU-12-30-6 | 220 | 30 | 11 | 6 | 220 | 30 | 12 | 6 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | CB Off (22년 5월)
C205 | 6F-N14 |  |  | A4-20-4 | B4-20-4 | U-A4-08 / 2P 30A | U-B4-08 / 2P 30A | 6-DaHall 1-PDU-11-30-8 | 6-DaHall 1-PDU-12-30-8 | 220 | 30 | 11 | 8 | 220 | 30 | 12 | 8 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | CB Off (22년 5월)
C206 | 6F-N15 |  |  | A4-20-5 | B4-20-5 | U-A4-10 / 2P 30A | U-B4-10 / 2P 30A | 6-DaHall 1-PDU-11-30-10 | 6-DaHall 1-PDU-12-30-10 | 220 | 30 | 11 | 10 | 220 | 30 | 12 | 10 | [6 empty] | 4.9703 | 4.9403 | 9.9106 | 0 | 0 | 0 | '22/02/22 전기투입
C207 | 6F-N16 |  |  | A4-20-6 | B4-20-6 | U-A4-12 / 2P 30A | U-B4-12 / 2P 30A | 6-DaHall 1-PDU-11-30-12 | 6-DaHall 1-PDU-12-30-12 | 220 | 30 | 11 | 12 | 220 | 30 | 12 | 12 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C208 | 6F-N17 |  |  | A4-20-7 | #B3-20-7 | U-A4-14 / 2P 30A | U-B3-21 / 2P 30A | 6-DaHall 1-PDU-11-30-14 | 6-DaHall 1-PDU-10-30-21 | 220 | 30 | 11 | 14 | 220 | 30 | 10 | 21 |  | U-B3 4P 200A |  | UPS 출력배전반(B) #03, 4P 200A |  |  | 0 | 0 | 0 | 0 | 0 | 0
C209 | 6F-N18 |  |  | A4-20-8 | B4-20-8 | U-A4-16 / 2P 30A | U-B4-16 / 2P 30A | 6-DaHall 1-PDU-11-30-16 | 6-DaHall 1-PDU-12-30-16 | 220 | 30 | 11 | 16 | 220 | 30 | 12 | 16 |  | U-B4 4P 200A |  | UPS 출력배전반(B) #01, 4P 200A |  |  | 0 | 0 | 0 | 0 | 0 | 0
C210 | 6F-N19 |  |  | A4-20-9 | B4-20-9 | U-A4-18 / 2P 30A | U-B4-18 / 2P 30A | 6-DaHall 1-PDU-11-30-18 | 6-DaHall 1-PDU-12-30-18 | 220 | 30 | 11 | 18 | 220 | 30 | 12 | 18 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C301 | [28 empty] | 0 | 랙 미설치
C302 | 6F-M11 |  |  | A3-21-1 | B3-21-1 | U-A3-01 / 2P 30A | U-B3-01 / 2P 30A | 6-DaHall 1-PDU-09-30-1 | 6-DaHall 1-PDU-10-30-1 | 220 | 30 | 09 | 1 | 220 | 30 | 10 | 1 | U-A3 4P 200A | U-B3 4P 200A | UPS 출력배전반(A) #03, 4P 200A | UPS 출력배전반(B) #03, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0
C303 | 6F-M12 |  |  | A3-21-2 | B3-21-2 | U-A3-03 / 2P 30A | U-B3-03 / 2P 30A | 6-DaHall 1-PDU-09-30-3 | 6-DaHall 1-PDU-10-30-3 | 220 | 30 | 09 | 3 | 220 | 30 | 10 | 3 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C304 | 6F-M13 |  |  | A3-21-3 | B3-21-3 | U-A3-05 / 2P 30A | U-B3-05 / 2P 30A | 6-DaHall 1-PDU-09-30-5 | 6-DaHall 1-PDU-10-30-5 | 220 | 30 | 09 | 5 | 220 | 30 | 10 | 5 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | A7-21-3(2) | B7-21-3(2) | U6-A7-32 / 2P 30A | U6-B7-34 / 2P 30A | 6-DaHall 1-PDU-13-30-32 | 6-DaHall 1-PDU-14-30-34 | 220 | 30 | 13 | 32 | 220 | 30 | 14 | 34 | U6-A7 4P 300A | U6-B7 4P 300A | LV-6A #07, 3P 320A | LV-6B #03, 3P 320A |  |  | 0 | 0 |  | 0 | 0 | 0
|  |  |  | A7-21-3(3) | B7-21-3(3) | U6-A7-30 / 2P 30A | U6-B7-30 / 2P 30A | 6-DaHall 1-PDU-13-30-30 | 6-DaHall 1-PDU-14-30-30 | 220 | 30 | 13 | 30 | 220 | 30 | 14 | 30 | [6 empty] | 0 | 0 |  | 0 | 0 | 0
C305 | 6F-M14 |  |  | A3-21-4 | B3-21-4 | U-A3-07 / 2P 30A | U-B3-07 / 2P 30A | 6-DaHall 1-PDU-09-30-7 | 6-DaHall 1-PDU-10-30-7 | 220 | 30 | 09 | 7 | 220 | 30 | 10 | 7 | U-A3 4P 200A | U-B3 4P 200A | UPS 출력배전반(A) #03, 4P 200A | UPS 출력배전반(B) #03, 4P 200A |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | A7-21-4(2) | B7-21-4(2) | U6-A7-34 / 2P 30A | U6-B7-32 / 2P 30A | 6-DaHall 1-PDU-13-30-34 | 6-DaHall 1-PDU-14-30-32 | 220 | 30 | 13 | 34 | 220 | 30 | 14 | 32 | U6-A7 4P 300A | U6-B7 4P 300A | LV-6A #07, 3P 320A | LV-6B #03, 3P 320A |  |  | 0 | 0 |  | 0 | 0
|  |  |  | A7-21-4(3) | B7-21-4(3) | U6-A7-28 / 2P 30A | U6-B7-28 / 2P 30A | 6-DaHall 1-PDU-13-30-28 | 6-DaHall 1-PDU-14-30-28 | 220 | 30 | 13 | 28 | 220 | 30 | 14 | 28 | [6 empty] | 0 | 0 |  | 0 | 0
C306 | 6F-M15 |  |  | A3-21-5 | B3-21-5 | U-A3-09 / 2P 30A | U-B3-09 / 2P 30A | 6-DaHall 1-PDU-09-30-9 | 6-DaHall 1-PDU-10-30-9 | 220 | 30 | 09 | 9 | 220 | 30 | 10 | 9 | U-A3 4P 200A | U-B3 4P 200A | UPS 출력배전반(A) #03, 4P 200A | UPS 출력배전반(B) #03, 4P 200A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2022/07/01, 알렉스엔 증설예정
C307 | 6F-M16 |  |  | A3-21-6 | B3-21-6 | U-A3-11 / 2P 30A | U-B3-11 / 2P 30A | 6-DaHall 1-PDU-09-30-11 | 6-DaHall 1-PDU-10-30-11 | 220 | 30 | 09 | 11 | 220 | 30 | 10 | 11 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C308 | 6F-M17 |  |  | A3-21-7 | B3-21-7 | U-A3-13 / 2P 30A | U-B3-13 / 2P 30A | 6-DaHall 1-PDU-09-30-13 | 6-DaHall 1-PDU-10-30-13 | 220 | 30 | 09 | 13 | 220 | 30 | 10 | 13 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C309 | 6F-M18 |  |  | A3-21-8 | B3-21-8 | U-A3-15 / 2P 30A | U-B3-15 / 2P 30A | 6-DaHall 1-PDU-09-30-15 | 6-DaHall 1-PDU-10-30-15 | 220 | 30 | 09 | 15 | 220 | 30 | 10 | 15 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C310 | 6F-M19 |  |  | A3-21-9 | B3-21-9 | U-A3-17 / 2P 30A | U-B3-17 / 2P 30A | 6-DaHall 1-PDU-09-30-17 | 6-DaHall 1-PDU-10-30-17 | 220 | 30 | 09 | 17 | 220 | 30 | 10 | 17 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C401 | [28 empty] | 0 | 랙 미설치
C402 | 6F-L11 |  |  | A3-22-1 | B3-22-1 | U-A3-02 / 2P 30A | U-B3-02 / 2P 30A | 6-DaHall 1-PDU-09-30-2 | 6-DaHall 1-PDU-10-30-2 | 220 | 30 | 09 | 2 | 220 | 30 | 10 | 2 | U-A3 4P 200A | U-B3 4P 200A | UPS 출력배전반(A) #03, 4P 200A | UPS 출력배전반(B) #03, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0
C403 | 6F-L12 |  |  | A3-22-2 | B3-22-2 | U-A3-04 / 2P 30A | U-B3-04 / 2P 30A | 6-DaHall 1-PDU-09-30-4 | 6-DaHall 1-PDU-10-30-4 | 220 | 30 | 09 | 4 | 220 | 30 | 10 | 4 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C404 | 6F-L13 |  |  | A3-22-3 | B3-22-3 | U-A3-06 / 2P 30A | U-B3-06 / 2P 30A | 6-DaHall 1-PDU-09-30-6 | 6-DaHall 1-PDU-10-30-6 | 220 | 30 | 09 | 6 | 220 | 30 | 10 | 6 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C405 | 6F-L14 |  |  | A3-22-4 | B3-22-4 | U-A3-08 / 2P 30A | U-B3-08 / 2P 30A | 6-DaHall 1-PDU-09-30-8 | 6-DaHall 1-PDU-10-30-8 | 220 | 30 | 09 | 8 | 220 | 30 | 10 | 8 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 제로투세븐(메타넷) 이동 및 현위치 철거 예정(4/15)
C406 | 6F-L15 |  |  | A3-22-5 | B3-22-5 | U-A3-10 / 2P 30A | U-B3-10 / 2P 30A | 6-DaHall 1-PDU-09-30-10 | 6-DaHall 1-PDU-10-30-10 | 220 | 30 | 09 | 10 | 220 | 30 | 10 | 10 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 제로투세븐(메타넷) 이동 및 현위치 철거 예정(4/15)
C407 | 6F-L16 |  |  | A3-22-6 | B3-22-6 | U-A3-12 / 2P 30A | U-B3-12 / 2P 30A | 6-DaHall 1-PDU-09-30-12 | 6-DaHall 1-PDU-10-30-12 | 220 | 30 | 09 | 12 | 220 | 30 | 10 | 12 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 제로투세븐(메타넷) 이동 및 현위치 철거 예정(4/15)
C408 | 6F-L17 |  |  | A3-22-7 | B3-22-7 | U-A3-14 / 2P 30A | U-B3-14 / 2P 30A | 6-DaHall 1-PDU-09-30-14 | 6-DaHall 1-PDU-10-30-14 | 220 | 30 | 09 | 14 | 220 | 30 | 10 | 14 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C409 | 6F-L18 |  |  | A3-22-8 | B3-22-8 | U-A3-16 / 2P 30A | U-B3-16 / 2P 30A | 6-DaHall 1-PDU-09-30-16 | 6-DaHall 1-PDU-10-30-16 | 220 | 30 | 09 | 16 | 220 | 30 | 10 | 16 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 철거완료(9/1)
C410 | 6F-L19 |  |  | A3-22-9 | B3-22-9 | U-A3-18 / 2P 30A | U-B3-18 / 2P 30A | 6-DaHall 1-PDU-09-30-18 | 6-DaHall 1-PDU-10-30-18 | 220 | 30 | 09 | 18 | 220 | 30 | 10 | 18 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 철거완료(9/1)
C501 | [28 empty] | 0 | 랙 미설치
C502 | 6F-K11 |  |  | A3-23-1 | B3-23-1 | U-A3-20 / 2P 30A | U-B3-20 / 2P 30A | 6-DaHall 1-PDU-09-30-20 | 6-DaHall 1-PDU-10-30-20 | 220 | 30 | 09 | 20 | 220 | 30 | 10 | 20 | U-A3 4P 200A | U-B3 4P 200A | UPS 출력배전반(A) #03, 4P 200A | UPS 출력배전반(B) #03, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 0 | 0 | 0 | 0 | 0 | 0
C503 | 6F-K12 |  |  | A3-23-2 | B3-23-2 | U-A3-22 / 2P 30A | U-B3-22 / 2P 30A | 6-DaHall 1-PDU-09-30-22 | 6-DaHall 1-PDU-10-30-22 | 220 | 30 | 09 | 22 | 220 | 30 | 10 | 22 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C504 | 6F-K13 |  |  | A3-23-3 | B3-23-3 | U-A3-24 / 2P 30A | U-B3-48 / 2P 30A | 6-DaHall 1-PDU-09-30-24 | 6-DaHall 1-PDU-10-30-48 | 220 | 30 | 09 | 24 | 220 | 30 | 10 | 48 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 여기서부터 다시 작성 필요합니다 ㅠㅠ
C505 | 6F-K14 |  |  | A3-23-4 | B3-23-4 | U-A3-26 / 2P 30A | U-B3-26 / 2P 30A | 6-DaHall 1-PDU-09-30-26 | 6-DaHall 1-PDU-10-30-26 | 220 | 30 | 09 | 26 | 220 | 30 | 10 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C506 | 6F-K15 |  |  | A3-23-5 | B3-23-5 | U-A3-28 / 2P 30A | U-B3-28 / 2P 30A | 6-DaHall 1-PDU-09-30-28 | 6-DaHall 1-PDU-10-30-28 | 220 | 30 | 09 | 28 | 220 | 30 | 10 | 28 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C507 | 6F-K16 |  |  | A3-23-6 | B3-23-6 | U-A3-30 / 2P 30A | U-B3-30 / 2P 30A | 6-DaHall 1-PDU-09-30-30 | 6-DaHall 1-PDU-10-30-30 | 220 | 30 | 09 | 30 | 220 | 30 | 10 | 30 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C508 | 6F-K17 |  |  | A3-23-7 | B3-23-7 | U-A3-32 / 2P 30A | U-B3-32 / 2P 30A | 6-DaHall 1-PDU-09-30-32 | 6-DaHall 1-PDU-10-30-32 | 220 | 30 | 09 | 32 | 220 | 30 | 10 | 32 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C509 | 6F-K18 |  |  | A3-23-8 | B3-23-8 | U-A3-34 / 2P 30A | U-B3-34 / 2P 30A | 6-DaHall 1-PDU-09-30-34 | 6-DaHall 1-PDU-10-30-34 | 220 | 30 | 09 | 34 | 220 | 30 | 10 | 34 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
C510 | 6F-K19 |  |  | A3-23-9 | B3-23-9 | U-A3-36 / 2P 30A | U-B3-36 / 2P 30A | 6-DaHall 1-PDU-09-30-36 | 6-DaHall 1-PDU-10-30-36 | 220 | 30 | 09 | 36 | 220 | 30 | 10 | 36 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6F-AF11 |  |  | A1-1-9 | B1-1-9 | U-A1-17 / 2P 30A | U-B1-17 / 2P 30A | 6-DaHall 1-PDU-01-30-17 | 6-DaHall 1-PDU-02-30-17 | 220 | 30 | 01 | 17 | 220 | 30 | 02 | 17 | U-A1 4P 200A | U-B1 4P 200A | UPS 출력배전반(A) #04, 4P 200A | UPS 출력배전반(B) #02, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | [5 empty] | 0 |  | 랙 배제결정('22.01.11) 차단기는 off 후 미사용 표기로 변경할 것
| 6F-AF12 |  |  | A1-1-8 | B1-1-8 | U-A1-15 / 2P 30A | U-B1-15 / 2P 30A | 6-DaHall 1-PDU-01-30-15 | 6-DaHall 1-PDU-02-30-15 | 220 | 30 | 01 | 15 | 220 | 30 | 02 | 15 | [11 empty] | 0
| 6F-AF13 |  |  | A1-1-7 | B1-1-7 | U-A1-13 / 2P 30A | U-B1-13 / 2P 30A | 6-DaHall 1-PDU-01-30-13 | 6-DaHall 1-PDU-02-30-13 | 220 | 30 | 01 | 13 | 220 | 30 | 02 | 13 | [11 empty] | 0
| 6F-AF14 |  |  | A1-1-6 | B1-1-6 | U-A1-11 / 2P 30A | U-B1-11 / 2P 30A | 6-DaHall 1-PDU-01-30-11 | 6-DaHall 1-PDU-02-30-11 | 220 | 30 | 01 | 11 | 220 | 30 | 02 | 11 | [11 empty] | 0
| 6F-AF15 |  |  | A1-1-5 | B1-1-5 | U-A1-09 / 2P 30A | U-B1-09 / 2P 30A | 6-DaHall 1-PDU-01-30-9 | 6-DaHall 1-PDU-02-30-9 | 220 | 30 | 01 | 9 | 220 | 30 | 02 | 9 | [11 empty] | 0
| 6F-AF16 |  |  | A1-1-4 | B1-1-4 | U-A1-07 / 2P 30A | U-B1-07 / 2P 30A | 6-DaHall 1-PDU-01-30-7 | 6-DaHall 1-PDU-02-30-7 | 220 | 30 | 01 | 7 | 220 | 30 | 02 | 7 | [11 empty] | 0
| 6F-AF17 | [6 empty] | 6-DaHall 1-PDU--30- | 6-DaHall 1-PDU--30- | 220 | 30 |  |  | 220 | 30 | [10 empty] | 0 |  |  | 0 | 랙 미설치
| 6F-AF18 | [6 empty] | 6-DaHall 1-PDU--30- | 6-DaHall 1-PDU--30- | 220 | 30 |  |  | 220 | 30 | [10 empty] | 0 |  |  | 0 | 랙 미설치
| 6F-AF19 | [6 empty] | 6-DaHall 1-PDU--30- | 6-DaHall 1-PDU--30- | 220 | 30 |  |  | 220 | 30 | [10 empty] | 0 |  |  | 0 | 랙 미설치
G1101 | 6F-AG10 | 피플펀드 | 2.2 | A1-35-1 | B1-35-1 | U-A1-02 / 2P 30A | U-B1-02 / 2P 30A | 6-DaHall 1-PDU-01-30-2 | 6-DaHall 1-PDU-02-30-2 | 220 | 30 | 01 | 2 | 220 | 30 | 02 | 2 | U-A1 4P 200A | U-B1 4P 200A | UPS 출력배전반(A) #04, 4P 200A | UPS 출력배전반(B) #02, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 1.9073 | 1.4397 | 3.347 | 236.8 | 167.9 | 404.7 | 22/09/19 투입(임대장비 설정으로 선투입요청)
G1102 | 6F-AG11 | 피플펀드 | 2.2 | A1-35-1(2) | B1-35-1(2) | U-A1-36 / 2P 30A | U-B1-36 / 2P 30A | 6-DaHall 1-PDU-01-30-36 | 6-DaHall 1-PDU-02-30-36 | 220 | 30 | 01 | 36 | 220 | 30 | 02 | 36 | [6 empty] | 1.0053 | 1.556 | 2.5613 | 145.3 | 197 | 342.3 | 22/09/23 투입
|  |  |  | A1-35-2(2) | B1-35-2(2) | U-A1-38 / 2P 30A | U-B1-38 / 2P 30A | 6-DaHall 1-PDU-01-30-38 | 6-DaHall 1-PDU-02-30-38 | 220 | 30 | 01 | 38 | 220 | 30 | 02 | 38 | [6 empty] | 0 | 0 |  | 0 | 0 |  | B전원 : 도어락&CCTV 전원 포함
G1103 | 6F-AG12 | 피플펀드 | 2.2 | A1-35-2 | B1-35-2 | U-A1-04 / 2P 30A | U-B1-04 / 2P 30A | 6-DaHall 1-PDU-01-30-4 | 6-DaHall 1-PDU-02-30-4 | 220 | 30 | 01 | 4 | 220 | 30 | 02 | 4 | [6 empty] | 3.3293 | 2.2968 | 5.6261 | 508 | 358.2 | 866.2 | 22/09/23 투입
G2101 | 6F-AG13 | 삼성물산(주)패션부문 | 2.2 | A1-35-3 | B1-35-3 | U-A1-06 / 2P 30A | U-B1-06 / 2P 30A | 6-DaHall 1-PDU-01-30-6 | 6-DaHall 1-PDU-02-30-6 | 220 | 30 | 01 | 6 | 220 | 30 | 02 | 6 | U-A1 4P 200A | U-B1 4P 200A | UPS 출력배전반(A) #04, 4P 200A | UPS 출력배전반(B) #02, 4P 200A | TR-6A 1000kVA | TR-6B 1000kVA | 2.9359 | 5.0405 | 7.9764 | 403.2 | 739.6 | 1142.8
G2102 | 6F-AG14 | 삼성물산(주)패션부문 | 2.2 | A1-35-4 | B1-35-4 | U-A1-08 / 2P 30A | U-B1-08 / 2P 30A | 6-DaHall 1-PDU-01-30-8 | 6-DaHall 1-PDU-02-30-8 | 220 | 30 | 01 | 8 | 220 | 30 | 02 | 8 | [6 empty] | 4.6096 | 3.1141 | 7.7236 | 698.1 | 423.4 | 1121.5
G2103 | 6F-AG15 | 삼성물산(주)패션부문 | 2.2 | A1-35-5 | B1-35-5 | U-A1-10 / 2P 30A | U-B1-10 / 2P 30A | 6-DaHall 1-PDU-01-30-10 | 6-DaHall 1-PDU-02-30-10 | 220 | 30 | 01 | 10 | 220 | 30 | 02 | 10 | [6 empty] | 7.6267 | 7.3766 | 15.0032 | 1222.8 | 1180.2 | 2403
G2104 | 6F-AG16 | 삼성물산(주)패션부문 | 2.2 | A1-35-6 | B1-35-6 | U-A1-12 / 2P 30A | U-B1-12 / 2P 30A | 6-DaHall 1-PDU-01-30-12 | 6-DaHall 1-PDU-02-30-12 | 220 | 30 | 01 | 12 | 220 | 30 | 02 | 12 | [6 empty] | 7.1786 | 9.177 | 16.3556 | 1161.9 | 1497.4 | 2659.3
G2105 | 6F-AG17 | 삼성물산(주)패션부문 | 2.2 | A1-35-7 | B1-35-7 | U-A1-14 / 2P 30A | U-B1-14 / 2P 30A | 6-DaHall 1-PDU-01-30-14 | 6-DaHall 1-PDU-02-30-14 | 220 | 30 | 01 | 14 | 220 | 30 | 02 | 14 | [6 empty] | 4.742 | 5.9326 | 10.6746 | 821 | 1102.4 | 1923.4
G2106 | 6F-AG18 | 삼성물산(주)패션부문 | 2.2 | A1-35-8 | B1-35-8 | U-A1-16 / 2P 30A | U-B1-16 / 2P 30A | 6-DaHall 1-PDU-01-30-16 | 6-DaHall 1-PDU-02-30-16 | 220 | 30 | 01 | 16 | 220 | 30 | 02 | 16 | [6 empty] | 4.3582 | 4.3999 | 8.7581 | 721.6 | 744.1 | 1465.7
G2107 | 6F-AG19 | 삼성물산(주)패션부문 | 2.2 | A4-36-1 | B4-36-1 | U-A4-19 / 2P 30A | U-B4-19 / 2P 30A | 6-DaHall 1-PDU-11-30-19 | 6-DaHall 1-PDU-12-30-19 | 220 | 30 | 11 | 19 | 220 | 30 | 12 | 19 | U-A4 4P 200A | U-B4 4P 200A | UPS 출력배전반(A) #01, 4P 200A | UPS 출력배전반(B) #01, 4P 200A |  |  | 5.1988 | 5.1819 | 10.3807 | 806 | 802.3 | 1608.3
G2108 | 6F-AG20 |  | 2.2 | A4-36-9 | B4-36-9 | U-A4-44 / 2P 30A | U-B4-44 / 2P 30A | 6-DaHall 1-PDU-11-30-44 | 6-DaHall 1-PDU-12-30-44 | 220 | 30 | 11 | 44 | 220 | 30 | 12 | 44 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2022/06/09 전기투입 (임시사용 랙)
| DE운용실 사무#1 | DEK 사무실 |  | A7-30-8 |  | U6-A7-02 / 2P 30 |  | 6-DaHall 1-PDU-13-30-2 |  | 220 | 30 | 13 | 2 |  |  |  |  | U6-A7 4P 300A |  | LV-6A #07, 3P 320A |  | TR-6A 1000kVA |  | 0 |  | 0 | 0 |  | 0 | 2022.05.26 차단기 ON
| DE 출입통제Desk |  |  | A7-31-1 |  | U6-A7-04 / 2P 30A |  | 6-DaHall 1-PDU-13-30-4 |  | 220 | 30 | 13 | 4 | [10 empty] | 0 |  | 0 | 0 |  | 0 | 2022.05.26 차단기 ON
| DE운용실 감시모니터 |  |  |  | B7-30-8 |  | U6-B7-02 / 2P 30 |  | 6-DaHall 1-PDU-14-30-2 |  |  |  |  | 220 | 30 | 14 | 2 |  | U6-B7 4P 300A |  | LV-6B #03, 3P 320A |  | TR-6B 1000kVA |  | 0 | 0 |  | 0 | 0 | 2022.05.26 차단기 ON
| DE운용실 사무#2 |  |  |  | B7-31-1 |  | U6-B7-04 / 2P 30 |  | 6-DaHall 1-PDU-14-30-4 |  |  |  |  | 220 | 30 | 14 | 4 | [7 empty] | 0 | 0 |  | 0 | 0 | 2022.05.26 차단기 ON
| 6층 사무실 |  |  |  | B7-32-1 |  | U6-B7-20 / 2P 30A |  | 6-DaHall 1-PDU-14-30-20 |  |  |  |  | 220 | 30 | 14 | 20 |  | U6-B7 4P 300A |  | LV-6B #03, 3P 320A |  | TR-6B 1000kVA |  | 0 | 0 |  | 0 | 0
| 6층 인터넷장비 |  |  | A7-28-9 |  | U6-A7-40 / 2P 30A |  | 6-DaHall 1-PDU-13-30-40 |  | 220 | 30 | 13 | 40 |  |  |  |  | U6-A7 4P 300A |  | LV-6A #07, 3P 320A |  | TR-6A 1000kVA |  | 0 |  | 0 | 0 |  | 0
| FMS 6층 전원 |  |  |  |  | U-A1-50 / 2P 30A |  | 6-DaHall 1-PDU-01-30-50 |  | 220 | 30 | 01 | 50 |  |  |  |  | U-A1 4P 200A |  | UPS 출력배전반(A) #04, 4P 200A |  |  |  | 0 |  | 0 | 0 |  | 0
| 신규 BMS(6F TPS실) Rack |  | 2.2 |  |  |  |  | 6-DaHall 1-PDU-01-30-46 |  | 220 | 30 | 01 | 46 |  |  |  |  | U-A1 4P 200A |  | UPS 출력배전반(A) #04, 4P 200A |  |  |  | 1.1849 |  | 1.1849 | 75.1 |  | 75.1
[26 empty] | 496.4937 | 28.784
[25 empty] | 오차 | #REF!

## 5층_랙별_계통 및_부하량
5층 랙별 전기공급계통
=AD5:AD315
DEKR No. | 랙 No. | 고객명 | 계약용량 | 리셉터클 Name |  | 차단기 정보 |  | DEK Naming Convention 적용 명칭(NEW) |  | 차단기 정보(수정) | [7 empty] | 분전반 정보 |  | 배전반 정보 |  | TR 정보 |  | 월 평균 전류 |  |  | 월 유효전력량 |  | 월간 사용전력량[kWh] | 비 고
|  |  | kW | A | B | A | B | A | B | A |  |  |  | B |  |  |  | A | B | A | B | A | B | A | B | 합계 | A | B
A501 | 5F-A10 | Digital Edge Korea | 2.2 | 1A-1-1 | 1B-1-1 | PDU(A)-1-03 / 3P 30A | PDU(B)-1-03 / 3P 30A | 5-DaHall1-PDU-11-30-3 | 5-DaHall1-PDU-12-30-3 | 220 | 30 | 11 | 3 | 220 | 30 | 12 | 3 | PDU(A)-1 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #03 3P 150A | UPS출력 배전반(B), #03 3P 150A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0
A502 | 5F-A11 |  |  | 1A-1-2 | 1B-1-2 | PDU(A)-1-05 / 3P 30A | PDU(B)-1-05 / 3P 30A | 5-DaHall1-PDU-11-30-5 | 5-DaHall1-PDU-12-30-5 | 220 | 30 | 11 | 5 | 220 | 30 | 12 | 5 | [6 empty] | 4.9924 | 2.7999 | 7.7923 | 0 | 0 | 0
A503 | 5F-A12 | PCCW Global Korea Limited | 2.2 | 1A-1-3 | 1B-1-3 | PDU(A)-1-09 / 3P 30A | PDU(B)-1-26 / 3P 20A | 5-DaHall1-PDU-11-30-9 | 5-DaHall1-PDU-12-20-26 | 220 | 30 | 11 | 9 | 220 | 20 | 12 | 26 | [6 empty] | 5.0854 | 4.8527 | 21.2171 | 800.3 | 767.5 | 3413.8
|  |  |  | A1-1-3(2) | B1-1-3(2) | PDU(A)-1-26 / 3P 20A | PDU(B)-1-30 / 3P 20A | 5-DaHall1-PDU-11-20-26 | 5-DaHall1-PDU-12-20-30 | 220 | 20 | 11 | 26 | 220 | 20 | 12 | 30 | [6 empty] | 4.9259 | 6.3531 |  | 841 | 1005
A504 | 5F-A13 | PCCW Global Korea Limited | 2.2 | 1A-1-4 | 1B-1-4 | PDU(A)-1-11 / 3P 30A | PDU(B)-1-09 / 3P 30A | 5-DaHall1-PDU-11-30-11 | 5-DaHall1-PDU-12-30-9 | 220 | 30 | 11 | 11 | 220 | 30 | 12 | 9 | [6 empty] | 2.4235 | 2.8494 | 11.5727 | 0 | 441.3 | 735
|  |  |  | 1A-1-4(2) | 1B-1-4(2) | PDU(A)-1-13 / 3P 30A | PDU(B)-1-11 / 3P 30A | 5-DaHall1-PDU-11-30-13 | 5-DaHall1-PDU-12-30-11 | 220 | 30 | 11 | 13 | 220 | 30 | 12 | 11 | [6 empty] | 1.8986 | 4.4011 |  | 293.7 | 0
A505 | 5F-A14 | PCCW Global Korea Limited | 2.2 | 9A-1-5 | 9B-1-5 | PDU(A)-9-01 / 3P 30A | PDU(B)-9-07 / 3P 30A | 5-DaHall1-PDU-07-30-1 | 5-DaHall1-PDU-08-30-7 | 220 | 30 | 07 | 1 | 220 | 30 | 08 | 7 | PDU(A)-9 4P 200A | PDU(B)-9 4P 200A | UPS출력 배전반(A), #09 3P 200A | UPS출력 배전반(B), #09 3P 200A |  |  | 7.7743 | 5.2714 | 13.0457 | 1196.9 | 776.2 | 1973.1
A506 | 5F-A15 | PCCW Global Korea Limited | 2.2 | 9A-1-6 | 9B-1-6 | PDU(A)-9-03 / 3P 30A | PDU(B)-9-03 / 3P 30A | 5-DaHall1-PDU-07-30-3 | 5-DaHall1-PDU-08-30-3 | 220 | 30 | 07 | 3 | 220 | 30 | 08 | 3 | [6 empty] | 1.0896 | 1.3681 | 2.4577 | 101.4 | 120.2 | 221.6
A507 | 5F-A16 | PCCW Global Korea Limited | 2.2 | 9A-1-7 | 9B-1-7 | PDU(A)-9-05 / 3P 30A | PDU(B)-9-05 / 3P 30A | 5-DaHall1-PDU-07-30-5 | 5-DaHall1-PDU-08-30-5 | 220 | 30 | 07 | 5 | 220 | 30 | 08 | 5 | [6 empty] | 0.39038 | 0 | 0.39038 | 54.9 | 0 | 54.9
A508 | 5F-A17 | Lumen Technologies Korea | 2.2 | 9A-1-8 | 9B-1-8 | PDU(A)-9-02 / 3P 30A | PDU(B)-9-02 / 3P 30A | 5-DaHall1-PDU-07-30-2 | 5-DaHall1-PDU-08-30-2 | 220 | 30 | 07 | 2 | 220 | 30 | 08 | 2 | [6 empty] | 1.0427 | 1.2448 | 12.8421 | 106.3 | 146.7 | 1989.7
|  |  |  | A1-1-8(2) | B1-1-8(2) | PDU(A)-1-28 / 3P 20A | PDU(B)-1-28 / 3P 20A | 5-DaHall1-PDU-11-20-28 | 5-DaHall1-PDU-12-20-28 | 220 | 20 | 11 | 28 | 220 | 20 | 12 | 28 | PDU(A)-1 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #03 3P 150A | UPS출력 배전반(B), #03 3P 150A |  |  | 5.279 | 5.2757 |  | 842.7 | 894
A509 | 5F-A18 |  |  | 9A-1-9 | 9B-1-9 | PDU(A)-9-04 / 3P 30A | PDU(B)-9-04 / 3P 30A | 5-DaHall1-PDU-07-30-4 | 5-DaHall1-PDU-08-30-4 | 220 | 30 | 07 | 4 | 220 | 30 | 08 | 4 | PDU(A)-9 4P 200A | PDU(B)-9 4P 200A | UPS출력 배전반(A), #09 3P 200A | UPS출력 배전반(B), #09 3P 200A |  |  | 0 | 5.2088 | 5.2088 | 0 | 0 | 0
A510 | 5F-A19 | Digital Edge Korea | 2.2 | 9A-1-10 | 9B-1-10 | PDU(A)-9-06 / 3P 30A | PDU(B)-9-06 / 3P 30A | 5-DaHall1-PDU-07-30-6 | 5-DaHall1-PDU-08-30-6 | 220 | 30 | 07 | 6 | 220 | 30 | 08 | 6 | [6 empty] | 0.3788 | 1.328 | 1.7068 | 58.1 | 180.2 | 238.3
A601 | 5F-B10 | Digital Edge Korea | 2.2 | A1-2-1 | B1-2-1 | PDU(A)-1-15 / 3P 20A | PDU(B)-1-13 / 3P 20A | 5-DaHall1-PDU-11-20-15 | 5-DaHall1-PDU-12-20-13 | 220 | 20 | 11 | 15 | 220 | 20 | 12 | 13 | PDU(A)-1 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #03 3P 150A | UPS출력 배전반(B), #03 3P 150A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 3.1179 | 3.1179 | 0 | 0 | 0 | 국제연동망 테스트
A602 | 5F-B11 |  |  | A1-2-2 | B1-2-2 | PDU(A)-1-17 / 3P 20A | PDU(B)-1-15 / 3P 20A | 5-DaHall1-PDU-11-20-17 | 5-DaHall1-PDU-12-20-15 | 220 | 20 | 11 | 17 | 220 | 20 | 12 | 15 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A603 |  | Sejong Telecom Inc. | 2.2 |  |  |  |  | 5-DaHall1-PDU-15-30-11 | 5-DaHall1-PDU-16-30-11 | 220 | 30 | 15 | 11 | 220 | 30 | 16 | 11 | PDU(A)-3 4P 300A | PDU(B)-3 4P 300A | UPS출력 배전반(A), #01 3P 300A | UPS출력 배전반(B), #01 3P 300A |  |  | 0.0031944 | 0.40296 | 3.6066 | 0 | 0.1 | 368.5 | 23/08/23 차단기 투입
[8 empty] | 5-DaHall1-PDU-15-30-14 | 5-DaHall1-PDU-16-30-14 | 220 | 30 | 15 | 14 | 220 | 30 | 16 | 14 | [6 empty] | 1.5309 | 1.6695 |  | 170.5 | 197.9
| 5F-B12 |  |  | A1-2-3 | B1-2-3 | PDU(A)-1-19 / 3P 20A | PDU(B)-1-17 / 3P 20A | 5-DaHall1-PDU-11-20-19 | 5-DaHall1-PDU-12-20-17 | 220 | 20 | 11 | 19 | 220 | 20 | 12 | 17 | PDU(A)-1 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #03 3P 150A | UPS출력 배전반(B), #03 3P 150A |  |  | 1.9028 | 0 | 1.9028 | 0 | 0
A604 | 5F-B13 | Dakos Co., Ltd. | 2.2 | A1-2-4 | B1-2-4 | PDU(A)-1-21 / 3P 20A | PDU(B)-1-19 / 3P 20A | 5-DaHall1-PDU-11-20-21 | 5-DaHall1-PDU-12-20-19 | 220 | 20 | 11 | 21 | 220 | 20 | 12 | 19 | [6 empty] | 2.4821 | 2.8563 | 5.3383 | 346.6 | 373.7 | 720.3
A605 | 5F-B14 | Ebiz Networks | 2.2 | A1-2-5 | B1-2-5 | PDU(A)-1-23 / 3P 20A | PDU(B)-1-21 / 3P 20A | 5-DaHall1-PDU-11-20-23 | 5-DaHall1-PDU-12-20-21 | 220 | 20 | 11 | 23 | 220 | 20 | 12 | 21 | [6 empty] | 4.7745 | 4.4338 | 9.2083 | 741.6 | 669.9 | 1411.5 | 22/09/23, 06시 전기투입
A606 | 5F-B15 | NTT KOREA Co., Ltd. | 1.1 | A1-2-6 | B1-2-6 | PDU(A)-1-25 / 3P 20A | PDU(B)-1-23 / 3P 20A | 5-DaHall1-PDU-11-20-25 | 5-DaHall1-PDU-12-20-23 | 220 | 20 | 11 | 25 | 220 | 20 | 12 | 23 | [6 empty] | 2.8546 | 0 | 3.835 | 0 | 0 | 96.5
|  |  |  | A3-2-6(2) | B3-2-6(2) | PDU(A)-3-28 / 3P 20A | PDU(B)-3-28 / 3P 20A | 5-DaHall1-PDU-15-20-28 | 5-DaHall1-PDU-16-20-28 | 220 | 20 | 15 | 28 | 220 | 20 | 16 | 28 | PDU(A)-3 4P 300A | PDU(B)-3 4P 300A | UPS출력 배전반(A), #01 3P 300A | UPS출력 배전반(B), #01 3P 300A |  |  | 0.69019 | 0.29024 |  | 75.7 | 20.8
A607 | 5F-B16 | Zeus Networks Co., Ltd. | 1.1 | A1-2-7 | B1-2-7 | PDU(A)-1-27 / 3P 20A | PDU(B)-1-25 / 3P 20A | 5-DaHall1-PDU-11-20-27 | 5-DaHall1-PDU-12-20-25 | 220 | 20 | 11 | 27 | 220 | 20 | 12 | 25 | PDU(A)-1 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #03 3P 150A | UPS출력 배전반(B), #03 3P 150A |  |  | 2.4187 | 3.2839 | 5.7026 | 376.3 | 483.3 | 859.6
A608 | 5F-B17 | Sejong Telecom Inc. | 2.2 | A1-2-8 | B1-2-8 | PDU(A)-1-29 / 3P 20A | PDU(B)-1-27 / 3P 20A | 5-DaHall1-PDU-11-20-29 | 5-DaHall1-PDU-12-20-27 | 220 | 20 | 11 | 29 | 220 | 20 | 12 | 27 | [6 empty] | 5.2037 | 0 | 15.2432 | 0 | 0 | 1577.6 | 미사용
|  |  |  | PDU(A)-3-07 | PDU(B)-3-07 | PDU(A)-3-07 / 3P 30A | PDU(B)-3-07 / 3P 30A | 5-DaHall1-PDU-15-30-7 | 5-DaHall1-PDU-16-30-7 | 220 | 30 | 15 | 7 | 220 | 30 | 16 | 7 | DU(A)-3 4P 300A | PDU(B)-3 4P 300A | UPS출력 배전반(A), #01 3P 300A | UPS출력 배전반(B), #01 3P 300A |  |  | 3.1077 | 3.4715 |  | 561.7 | 599.1 |  | '21/10/29 신규구성
|  |  |  | PDU(A)-3-09 | PDU(B)-3-09 | PDU(A)-3-09 / 3P 30A | PDU(B)-3-09 / 3P 30A | 5-DaHall1-PDU-15-30-9 | 5-DaHall1-PDU-16-30-9 | 220 | 30 | 15 | 9 | 220 | 30 | 16 | 9 | [6 empty] | 1.7053 | 1.7549 |  | 203.6 | 213.2
A609 | 5F-B18 | 한비로 | 2.2 | A2-2-9 | B1-2-9 | PDU(A)-2-03 / 3P 30A | PDU(B)-1-32 / 3P 20A | 5-DaHall1-PDU-13-30-3 | 5-DaHall1-PDU-12-20-32 | 220 | 30 | 13 | 3 | 220 | 20 | 12 | 32 | PDU(A)-2 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #04 3P 150A | UPS출력 배전반(B), #03 3P 150A |  |  | 5.2809 | 3.2036 | 8.4845 | 862.6 | 467.4 | 1330
A610 | 5F-B19 | PCCW Global Korea Limited | 2.2 | A2-2-10 | B2-2-10 | PDU(A)-2-05 / 3P 30A | PDU(B)-2-03 / 3P 30A | 5-DaHall1-PDU-13-30-5 | 5-DaHall1-PDU-14-30-3 | 220 | 30 | 13 | 5 | 220 | 30 | 14 | 3 |  | PDU(B)-2 4P 150A |  | UPS출력 배전반(B), #04 3P 150A |  |  | 3.8315 | 3.1702 | 7.0017 | 568.5 | 457 | 1025.5
A702 | [29 empty] | 랙 미설치
A703 | 5F-C12 | Sejong Telecom Inc. | 2.2 | A1-3-3 | B1-3-3 | PDU(A)-1-06 / 3P 30A | PDU(B)-1-04 / 3P 30A | 5-DaHall1-PDU-11-30-6 | 5-DaHall1-PDU-12-30-4 | 220 | 30 | 11 | 6 | 220 | 30 | 12 | 4 | PDU(A)-1 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #03 3P 150A | UPS출력 배전반(B), #03 3P 150A | TR-5A 1000KVA | TR-5B 1000KVA | 1.9354 | 1.852 | 3.7874 | 268 | 241.9 | 509.9 | 21/11/30 전기투입
A704 | 5F-C13 | Sejong Telecom Inc. | 2.2 | A1-3-4 | B1-3-4 | PDU(A)-1-08 / 3P 20A | PDU(B)-1-06 / 3P 30A | 5-DaHall1-PDU-11-20-8 | 5-DaHall1-PDU-12-30-6 | 220 | 20 | 11 | 8 | 220 | 30 | 12 | 6 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | QDF 전기 미사용
A705 | 5F-C14 |  |  | A1-3-5 | B1-3-5 | PDU(A)-1-10 / 3P 20A | PDU(B)-1-08 / 3P 30A | 5-DaHall1-PDU-11-20-10 | 5-DaHall1-PDU-12-30-8 | 220 | 20 | 11 | 10 | 220 | 30 | 12 | 8 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A706 | 5F-C15 |  |  | A1-3-6 | B1-3-6 | PDU(A)-1-12 / 3P 20A | PDU(B)-1-10 / 3P 20A | 5-DaHall1-PDU-11-20-12 | 5-DaHall1-PDU-12-20-10 | 220 | 20 | 11 | 12 | 220 | 20 | 12 | 10 | [6 empty] | 4.7449 | 2.824 | 7.5689 | 0 | 0 | 0
A707 | 5F-C16 |  |  | A1-3-7 | B1-3-7 | PDU(A)-1-14 / 3P 20A | PDU(B)-1-12 / 3P 20A | 5-DaHall1-PDU-11-20-14 | 5-DaHall1-PDU-12-20-12 | 220 | 20 | 11 | 14 | 220 | 20 | 12 | 12 | [6 empty] | 2.4231 | 0 | 2.4231 | 0 | 0 | 0
A708 | 5F-C17 | CHANEL KOREA | 2.2 | A1-3-8 | B1-3-8 | PDU(A)-1-16 / 3P 20A | PDU(B)-1-14 / 3P 20A | 5-DaHall1-PDU-11-20-16 | 5-DaHall1-PDU-12-20-14 | 220 | 20 | 11 | 16 | 220 | 20 | 12 | 14 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
A709 | 5F-C18 | CHANEL KOREA | 2.2 | A1-3-9 | B1-3-9 | PDU(A)-1-18 / 3P 20A | PDU(B)-1-16 / 3P 20A | 5-DaHall1-PDU-11-20-18 | 5-DaHall1-PDU-12-20-16 | 220 | 20 | 11 | 18 | 220 | 20 | 12 | 16 | [6 empty] | 3.0066 | 5.9409 | 8.9475 | 421.2 | 928.1 | 1349.3
A710 | 5F-C19 | CHANEL KOREA | 2.2 | A1-3-10 | B1-3-10 | PDU(A)-1-20 / 3P 20A | PDU(B)-1-18 / 3P 20A | 5-DaHall1-PDU-11-20-20 | 5-DaHall1-PDU-12-20-18 | 220 | 20 | 11 | 20 | 220 | 20 | 12 | 18 | [6 empty] | 2.9667 | 3.1234 | 6.0902 | 323.6 | 462.8 | 786.4
| 5F-D12 |  |  | A2-4-3 | B2-4-3 | PDU(A)-2-11 / 3P 20A | PDU(B)-2-09 / 3P 30A | 5-DaHall1-PDU-13-20-11 | 5-DaHall1-PDU-14-30-9 | 220 | 20 | 13 | 11 | 220 | 30 | 14 | 9 | PDU(A)-2 4P 150A | PDU(B)-2 4P 150A | UPS출력 배전반(A), #04 3P 150A | UPS출력 배전반(B), #04 3P 150A | TR-5A 1000KVA | TR-5B 1000KVA | 3.0406 | 0.91896 | 3.9596 | 0 | 0 | 0 | 랙 미설치
A804 | 5F-D13 | Digital Edge Korea | 2.2 | A2-4-4 | B2-4-4 | PDU(A)-2-13 / 3P 20A | PDU(B)-2-11 / 3P 20A | 5-DaHall1-PDU-13-20-13 | 5-DaHall1-PDU-14-20-11 | 220 | 20 | 13 | 13 | 220 | 20 | 14 | 11 | [6 empty] | 1.1149 | 3.2292 | 4.3442 | 68.3 | 0 | 68.3
A805 | 5F-D14 | PCCW Global Korea Limited | 3.3 | A2-4-5 | B2-4-5 | PDU(A)-2-15 / 3P 20A | PDU(B)-2-13 / 3P 20A | 5-DaHall1-PDU-13-20-15 | 5-DaHall1-PDU-14-20-13 | 220 | 20 | 13 | 15 | 220 | 20 | 14 | 13 | [6 empty] | 0 | 1.6831 | 1.6831 | 0 | 234.9 | 234.9
A806 | 5F-D15 | Sejong Telecom Inc. | 3 | A2-4-6 | B2-4-6 | PDU(A)-2-17 / 3P 20A | PDU(B)-2-15 / 3P 20A | 5-DaHall1-PDU-13-20-17 | 5-DaHall1-PDU-14-20-15 | 220 | 20 | 13 | 17 | 220 | 20 | 14 | 15 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 600.4 | 랙 미설치
|  |  |  | PDU(A)-3-A-12 | PDU(B)-3-B-12 | PDU(A)-3-A-12 / 3P 30A | PDU(B)-3-B-12 / 3P 30A | 5-DaHall1-PDU-15-30-12 | 5-DaHall1-PDU-16-30-12 | 220 | 30 | 15 | 12 | 220 | 30 | 16 | 12 | PDU(A)-3 4P 300A | PDU(B)-3 4P 300A | UPS출력 배전반(A), #01 3P 300A | UPS출력 배전반(B), #01 3P 300A |  |  | 2.3146 | 2.4929 | 4.8076 | 293.6 | 306.8 |  | '21.09.29 전기투입
A807 | 5F-D16 | Sejong Telecom Inc. | 2.2 | A2-4-7 | B2-4-7 | PDU(A)-2-19 / 3P 20A | PDU(B)-2-17 / 3P 20A | 5-DaHall1-PDU-13-20-19 | 5-DaHall1-PDU-14-20-17 | 220 | 20 | 13 | 19 | 220 | 20 | 14 | 17 | PDU(A)-2 4P 150A | PDU(B)-2 4P 150A | UPS출력 배전반(A), #04 3P 150A | UPS출력 배전반(B), #04 3P 150A |  |  | 5.5747 | 0.93687 | 6.5116 | 868.8 | 116.9 | 985.7 | 랙 미설치
|  |  |  | A1-4-7(2) | B1-4-7(2) | PDU(A)-1-22 / 3P 20A | PDU(B)-1-22 / 3P 20A | 5-DaHall1-PDU-11-20-22 | 5-DaHall1-PDU-12-20-22 | 220 | 20 | 11 | 22 | 220 | 20 | 12 | 22 | PDU(A)-1 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #03 3P 150A | UPS출력 배전반(B), #03 3P 150A |  |  | 0 | 0 |  | 0 | 0
A808 | 5F-D17 | Sejong Telecom Inc. | 2.2 | A2-4-8 | B2-4-8 | PDU(A)-2-21 / 3P 20A | PDU(B)-2-19 / 3P 20A | 5-DaHall1-PDU-13-20-21 | 5-DaHall1-PDU-14-20-19 | 220 | 20 | 13 | 21 | 220 | 20 | 14 | 19 | PDU(A)-2 4P 150A | PDU(B)-2 4P 150A | UPS출력 배전반(A), #04 3P 150A | UPS출력 배전반(B), #04 3P 150A |  |  | 3.0988 | 2.6305 | 5.7294 | 413.2 | 378.8 | 792
A809 | 5F-D18 | 한국보안기술 | 3.3 | A2-4-9 | B2-4-9 | PDU(A)-2-23 / 3P 20A | PDU(B)-2-21 / 3P 20A | 5-DaHall1-PDU-13-20-23 | 5-DaHall1-PDU-14-20-21 | 220 | 20 | 13 | 23 | 220 | 20 | 14 | 21 | [6 empty] | 8.95 | 3.2902 | 17.4795 | 1452.3 | 536.2 | 1988.5
|  |  |  | - |  | PDU(A)-1-30 / 3P 20A |  | 5-DaHall1-PDU-11-20-30 |  | 220 | 20 | 11 | 30 |  |  |  |  | PDU(A)-1 4P 150A |  | UPS출력 배전반(A), #03 3P 150A |  |  |  | 5.2394 |  |  | 0 |  |  | 임시
A810 | 5F-D19 | 한국보안기술 | 3.3 | A2-4-10 | B2-4-10 | PDU(A)-2-25 / 3P 20A | PDU(B)-2-23 / 3P 20A | 5-DaHall1-PDU-13-20-25 | 5-DaHall1-PDU-14-20-23 | 220 | 20 | 13 | 25 | 220 | 20 | 14 | 23 | PDU(A)-2 4P 150A | PDU(B)-2 4P 150A | UPS출력 배전반(A), #04 3P 150A | UPS출력 배전반(B), #04 3P 150A |  | TR-5B 1000KVA | 2.4387 | 2.7028 | 5.1415 | 371.8 | 391.7 | 763.5
| 5F-E12 |  |  | A2-5-3 | B2-5-3 | PDU(A)-2-31 / 3P 20A | PDU(B)-2-29 / 3P 20A | 5-DaHall1-PDU-13-20-31 | 5-DaHall1-PDU-14-20-29 | 220 | 20 | 13 | 31 | 220 | 20 | 14 | 29 | PDU(A)-2 4P 150A | PDU(B)-2 4P 150A | UPS출력 배전반(A), #04 3P 150A | UPS출력 배전반(B), #04 3P 150A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치
| 5F-E13 |  |  | A2-5-4 | B2-5-4 | PDU(A)-2-04 / 3P 30A | PDU(B)-2-31 / 3P 20A | 5-DaHall1-PDU-13-30-4 | 5-DaHall1-PDU-14-20-31 | 220 | 30 | 13 | 4 | 220 | 20 | 14 | 31 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치
A905 | 5F-E14 | Onse Telink | 2.2 | A2-5-5 | B2-5-5 | PDU(A)-2-06 / 3P 30A | PDU(B)-2-04 / 3P 30A | 5-DaHall1-PDU-13-30-6 | 5-DaHall1-PDU-14-30-4 | 220 | 30 | 13 | 6 | 220 | 30 | 14 | 4 | [6 empty] | 5.7186 | 6.784 | 12.5026 | 888.8 | 1046.5 | 1935.3
A906 | 5F-E15 | Onse Telink | 2.2 | A2-5-6 | B2-5-6 | PDU(A)-2-08 / 3P 30A | PDU(B)-2-06 / 3P 30A | 5-DaHall1-PDU-13-30-8 | 5-DaHall1-PDU-14-30-6 | 220 | 30 | 13 | 8 | 220 | 30 | 14 | 6 | [6 empty] | 4.1143 | 2.7567 | 6.871 | 595.2 | 411.3 | 1006.5
A907 | 5F-E16 |  |  | A2-5-7 | B2-5-7 | PDU(A)-2-10 / 3P 30A | PDU(B)-2-08 / 3P 30A | 5-DaHall1-PDU-13-30-10 | 5-DaHall1-PDU-14-30-8 | 220 | 30 | 13 | 10 | 220 | 30 | 14 | 8 | [6 empty] | 5.4351 | 0 | 5.4351 | 0 | 0 | 0
A908 | 5F-E17 |  |  | A2-5-8 | B2-5-8 | PDU(A)-2-12 / 3P 20A | PDU(B)-2-10 / 3P 30A | 5-DaHall1-PDU-13-20-12 | 5-DaHall1-PDU-14-30-10 | 220 | 20 | 13 | 12 | 220 | 30 | 14 | 10 | [6 empty] | 8.8344 | 2.4612 | 11.2955 | 0 | 0 | 0
A909 | 5F-E18 |  |  | A2-5-9 | B2-5-9 | PDU(A)-2-14 / 3P 20A | PDU(B)-2-12 / 3P 20A | 5-DaHall1-PDU-13-20-14 | 5-DaHall1-PDU-14-20-12 | 220 | 20 | 13 | 14 | 220 | 20 | 14 | 12 | [6 empty] | 0 | 2.4455 | 2.4455 | 0 | 0 | 0
A910 | 5F-E19 | PCCW Global Korea Limited | 2.2 | A2-5-10 | B2-5-10 | PDU(A)-2-16 / 3P 20A | PDU(B)-2-14 / 3P 20A | 5-DaHall1-PDU-13-20-16 | 5-DaHall1-PDU-14-20-14 | 220 | 20 | 13 | 16 | 220 | 20 | 14 | 14 | [6 empty] | 3.7659 | 3.1126 | 10.9915 | 610.6 | 502.5 | 1662.6
|  |  |  | A1-5-10(2) | B1-5-10(2) | PDU(A)-1-24 / 3P 20A | PDU(B)-1-24 / 3P 20A | 5-DaHall1-PDU-11-20-24 | 5-DaHall1-PDU-12-20-24 | 220 | 20 | 11 | 24 | 220 | 20 | 12 | 24 | PDU(A)-1 4P 150A | PDU(B)-1 4P 150A | UPS출력 배전반(A), #03 3P 150A | UPS출력 배전반(B), #03 3P 150A |  |  | 0 | 4.113 |  | 0 | 549.5
| 5F-F12 |  |  | A2-6-3 | B2-6-3 | PDU(A)-2-22 / 3P 20A | PDU(B)-2-20 / 3P 20A | 5-DaHall1-PDU-13-20-22 | 5-DaHall1-PDU-14-20-20 | 220 | 20 | 13 | 22 | 220 | 20 | 14 | 20 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 랙 미설치
| 5F-F13 |  |  | A2-6-4 | B2-6-4 | PDU(A)-2-24 / 3P 20A | PDU(B)-2-22 / 3P 20A | 5-DaHall1-PDU-13-20-24 | 5-DaHall1-PDU-14-20-22 | 220 | 20 | 13 | 24 | 220 | 20 | 14 | 22 | [6 empty] | 3.7088 | 0 | 3.7088 | 0 | 0 | 0 | 랙 미설치
A1005 | 5F-F14 | Onse Telink | 2.2 | A2-6-5 | B2-6-5 | PDU(A)-2-26 / 3P 20A | PDU(B)-2-24 / 3P 20A | 5-DaHall1-PDU-13-20-26 | 5-DaHall1-PDU-14-20-24 | 220 | 20 | 13 | 26 | 220 | 20 | 14 | 24 | [6 empty] | 1.8314 | 5.2254 | 7.0568 | 262.8 | 776.1 | 1038.9
A1006 | 5F-F15 | ITNEST | 6.6 |  |  |  |  | 5-DaHall1-PDU-15-30-10 | 5-DaHall1-PDU-16-30-10 |  | 30 | 15 | 10 |  | 30 | 16 | 10 | [6 empty] | 6.5942 | 0.9712 | 7.5654 | 1074.7 | 26.3 | 1101
|  |  |  | A2-6-6 | B2-6-6 | PDU(A)-2-28 / 3P 20A | PDU(B)-2-26 / 3P 20A | 5-DaHall1-PDU-13-20-28 | 5-DaHall1-PDU-14-20-26 | 220 | 20 | 13 | 28 | 220 | 20 | 14 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 21/11/30해지
A1007 | 5F-F16 | Lumen Technology | 6 |  |  |  |  | 5-DaHall1-PDU-15-30-8 | 5-DaHall1-PDU-16-30-8 |  | 30 | 15 | 8 |  | 30 | 16 | 8 | [6 empty] | 4.1937 | 4.3362 | 8.53 | 600.6 | 676.2 | 1276.8
|  |  |  | A2-6-7 | B2-6-7 | PDU(A)-2-30 / 3P 20A | PDU(B)-2-28 / 3P 20A | 5-DaHall1-PDU-13-20-30 | 5-DaHall1-PDU-14-20-28 | 220 | 20 | 13 | 30 | 220 | 20 | 14 | 28 | [6 empty] | 0 | 5.1566 | 5.1566 | 0 | 0
A1008 | 5F-F17 | Lumen Technology |  | A2-6-8 | B2-6-8 | PDU(A)-2-32 / 3P 20A | PDU(B)-2-30 / 3P 20A | 5-DaHall1-PDU-13-20-32 | 5-DaHall1-PDU-14-20-30 | 220 | 20 | 13 | 32 | 220 | 20 | 14 | 30 | [6 empty] | 0 | 0.00020326 | 0.00020326 | 0 | 0 | 0
B116 | R12 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-32 | 5-DaHall1-PDU-04-30-32 |  | 30 | 03 | 32 |  | 30 | 04 | 32 | [6 empty] | 2.4898 | 0.27074 | 2.7606 | 248.5 | 22.2 | 270.7
B117 | R11 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-34 | 5-DaHall1-PDU-04-30-34 |  | 30 | 03 | 34 |  | 30 | 04 | 34 | [6 empty] | 2.1696 | 0.28991 | 2.4595 | 214.9 | 15.6 | 230.5
B118 | R10 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-36 | 5-DaHall1-PDU-04-30-36 |  | 30 | 03 | 36 |  | 30 | 04 | 36 | [6 empty] | 2.17 | 2.2939 | 4.4639 | 226 | 246.3 | 472.3
B119 | R9 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-38 | 5-DaHall1-PDU-04-30-38 |  | 30 | 03 | 38 |  | 30 | 04 | 38 | [6 empty] | 2.435 | 2.5978 | 5.0328 | 264.8 | 272.5 | 537.3
B120 | R8 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-40 | 5-DaHall1-PDU-04-30-40 |  | 30 | 03 | 40 |  | 30 | 04 | 40 | [6 empty] | 1.3683 | 1.4562 | 2.8245 | 165.4 | 180.9 | 346.3
B121 | R7 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-42 | 5-DaHall1-PDU-04-30-42 |  | 30 | 03 | 42 |  | 30 | 04 | 42 | [6 empty] | 1.7892 | 1.5857 | 3.375 | 209 | 177.2 | 386.2
B122 | R6 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-44 | 5-DaHall1-PDU-04-30-44 |  | 30 | 03 | 44 |  | 30 | 04 | 44 | [6 empty] | 2.9436 | 2.3215 | 5.2651 | 440.3 | 326.7 | 767
B216 | R5 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-46 | 5-DaHall1-PDU-04-30-46 |  | 30 | 03 | 46 |  | 30 | 04 | 46 | [6 empty] | 2.912 | 2.3525 | 5.2645 | 430.2 | 327 | 757.2
B217 | R4 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-48 | 5-DaHall1-PDU-04-30-48 |  | 30 | 03 | 48 |  | 30 | 04 | 48 | [6 empty] | 3.7191 | 3.1823 | 6.9014 | 565.6 | 471.6 | 1037.2
B218 | R3 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-50 | 5-DaHall1-PDU-04-30-50 |  | 30 | 03 | 50 |  | 30 | 04 | 50 | [6 empty] | 4.1031 | 3.9494 | 8.0525 | 622.5 | 604.6 | 1227.1
B219 | R2 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-47 | 5-DaHall1-PDU-04-30-47 |  | 30 | 03 | 47 |  | 30 | 04 | 47 | [6 empty] | 4.0462 | 4.3953 | 8.4416 | 596.6 | 635.5 | 1232.1
B220 | R1 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-49 | 5-DaHall1-PDU-04-30-49 |  | 30 | 03 | 49 |  | 30 | 04 | 49 | [6 empty] | 5.699 | 5.4287 | 11.1277 | 873.4 | 828.1 | 1701.5
B221 | R13 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-2 | 5-DaHall1-PDU-04-30-2 |  | 30 | 03 | 2 |  | 30 | 04 | 2 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 5-DaHall1-PDU-03-30-4 | 5-DaHall1-PDU-04-30-4 |  | 30 | 03 | 4 |  | 30 | 04 | 4 | [6 empty] | 0 | 0 |  | 0 | 0
[8 empty] | 5-DaHall1-PDU-03-30-41 | 5-DaHall1-PDU-04-30-41 |  | 30 | 03 | 41 |  | 30 | 04 | 41 | [6 empty] | 0 | 0 |  | 0 | 0
B222 | R14 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-6 | 5-DaHall1-PDU-04-30-6 |  | 30 | 03 | 6 |  | 30 | 04 | 6 | [6 empty] | 0.56815 | 0.56831 | 9.182 | 84.7 | 85.7 | 1385.3
[8 empty] | 5-DaHall1-PDU-03-30-8 | 5-DaHall1-PDU-04-30-8 |  | 30 | 03 | 8 |  | 30 | 04 | 8 | [6 empty] | 1.4133 | 1.7195 |  | 214.1 | 261
[8 empty] | 5-DaHall1-PDU-03-30-43 | 5-DaHall1-PDU-04-30-43 |  | 30 | 03 | 43 |  | 30 | 04 | 43 | [6 empty] | 2.4187 | 2.494 |  | 362.5 | 377.3
B316 | R15 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-10 | 5-DaHall1-PDU-04-30-10 |  | 30 | 03 | 10 |  | 30 | 04 | 10 | [6 empty] | 3.5687 | 3.5462 | 10.7073 | 545.4 | 541.7 | 1630.3
[8 empty] | 5-DaHall1-PDU-03-30-12 | 5-DaHall1-PDU-04-30-12 |  | 30 | 03 | 12 |  | 30 | 04 | 12 | [6 empty] | 1.7762 | 1.8162 |  | 269.1 | 274.1
[8 empty] | 5-DaHall1-PDU-03-30-45 | 5-DaHall1-PDU-04-30-45 |  | 30 | 03 | 45 |  | 30 | 04 | 45 | [6 empty] | 0 | 0 |  | 0 | 0
B317 | R16 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-14 | 5-DaHall1-PDU-04-30-14 |  | 30 | 03 | 14 |  | 30 | 04 | 14 | [6 empty] | 0.35629 | 0.64036 | 8.1944 | 44.5 | 92.4 | 1184.2
[8 empty] | 5-DaHall1-PDU-03-30-37 | 5-DaHall1-PDU-04-30-37 |  | 30 | 03 | 37 |  | 30 | 04 | 37 | [6 empty] | 3.3377 | 3.86 |  | 481.2 | 566.1
B318 | R17 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-16 | 5-DaHall1-PDU-04-30-16 |  | 30 | 03 | 16 |  | 30 | 04 | 16 | [6 empty] | 3.8993 | 3.8896 | 10.0749 | 608.9 | 608.7 | 1248.1
[8 empty] | 5-DaHall1-PDU-03-30-39 | 5-DaHall1-PDU-04-30-39 |  | 30 | 03 | 39 |  | 30 | 04 | 39 | [6 empty] | 1.3727 | 0.91329 |  | 19.5 | 11
B319 | R18 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-18 | 5-DaHall1-PDU-04-30-18 |  | 30 | 03 | 18 |  | 30 | 04 | 18 | [6 empty] | 4.6474 | 4.4966 | 9.144 | 730.3 | 705 | 1435.3
B320 | R19 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-20 | 5-DaHall1-PDU-04-30-20 |  | 30 | 03 | 20 |  | 30 | 04 | 20 | [6 empty] | 2.8041 | 1.8441 | 4.6482 | 399.1 | 399.1 | 798.2
B321 | R20 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-22 | 5-DaHall1-PDU-04-30-22 |  | 30 | 03 | 22 |  | 30 | 04 | 22 | [6 empty] | 3.3989 | 4.7166 | 8.1154 | 461.9 | 461.9 | 923.8
B322 | R21 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-24 | 5-DaHall1-PDU-04-30-24 |  | 30 | 03 | 24 |  | 30 | 04 | 24 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
B416 | R22 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-26 | 5-DaHall1-PDU-04-30-26 |  | 30 | 03 | 26 |  | 30 | 04 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
B417 | R23 | KG이니시스 | 2.2 |  |  |  |  | 5-DaHall1-PDU-03-30-28 | 5-DaHall1-PDU-04-30-28 |  | 30 | 03 | 28 |  | 30 | 04 | 28 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
B418 | R24 | KG이니시스 | [5 empty] | 5-DaHall1-PDU-03-30-30 | 5-DaHall1-PDU-04-30-30 |  | 30 | 03 | 30 |  | 30 | 04 | 30 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 9.0784
B425 | 5F-M-08 | Digital Edge Korea | 2.2 | 1A-4-3 | 1B-4-3 | U5-1A-46 / 2P 30A | U5-1B-46 / 2P 30A | 5-DaHall1-PDU-01-30-46 | 5-DaHall1-PDU-02-30-46 | 220 | 30 | 01 | 46 | 220 | 30 | 02 | 46 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0.61537 | 0.65748 | 1.2729 | 77.2 | 86.5 | 163.7 | 변익준M 랙
| 5F-O18 |  |  | 2A-4-8 | 2B-4-8 | U5-2A-05 / 2P 30A | U5-2B-05 / 2P 30A | 5-DaHall1-PDU-03-30-5 | 5-DaHall1-PDU-04-30-5 | 220 | 30 | 03 | 5 | 220 | 30 | 04 | 5 | U5-2A 4P 300A | U5-2B 4P 300A | LV-5A #02 3P 320A | LV-5B #02 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0
| 5F-O19 |  |  | 2A-4-9 | 2B-4-9 | U5-2A-07 / 2P 30A | U5-2B-07 / 2P 30A | 5-DaHall1-PDU-03-30-7 | 5-DaHall1-PDU-04-30-7 | 220 | 30 | 03 | 7 | 220 | 30 | 04 | 7 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-O20 |  |  | 2A-4-10 | 2B-4-10 | U5-2A-09 / 2P 30A | U5-2B-09 / 2P 30A | 5-DaHall1-PDU-03-30-9 | 5-DaHall1-PDU-04-30-9 | 220 | 30 | 03 | 9 | 220 | 30 | 04 | 9 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-O21 |  |  | 2A-4-11 | 2B-4-11 | U5-2A-11 / 2P 30A | U5-2B-11 / 2P 30A | 5-DaHall1-PDU-03-30-11 | 5-DaHall1-PDU-04-30-11 | 220 | 30 | 03 | 11 | 220 | 30 | 04 | 11 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-O22 |  |  | 2A-4-12 | 2B-4-12 | U5-2A-13 / 2P 30A | U5-2B-13 / 2P 30A | 5-DaHall1-PDU-03-30-13 | 5-DaHall1-PDU-04-30-13 | 220 | 30 | 03 | 13 | 220 | 30 | 04 | 13 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-O23 |  |  | 2A-4-13 | 2B-4-13 | U5-2A-15 / 2P 30A | U5-2B-15 / 2P 30A | 5-DaHall1-PDU-03-30-15 | 5-DaHall1-PDU-04-30-15 | 220 | 30 | 03 | 15 | 220 | 30 | 04 | 15 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-O24 |  |  | 2A-4-14 | 2B-4-14 | U5-2A-17 / 2P 30A | U5-2B-17 / 2P 30A | 5-DaHall1-PDU-03-30-17 | 5-DaHall1-PDU-04-30-17 | 220 | 30 | 03 | 17 | 220 | 30 | 04 | 17 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-N18 |  |  | 2A-5-8 | 2B-5-8 | U5-2A-35 / 2P 30A | U5-2B-35 / 2P 30A | 5-DaHall1-PDU-03-30-35 | 5-DaHall1-PDU-04-30-35 | 220 | 30 | 03 | 35 | 220 | 30 | 04 | 35 | U5-2A 4P 300A | U5-2B 4P 300A | LV-5A #02 3P 320A | LV-5B #02 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0
5F-N19
5F-N20
5F-N21
5F-N22
5F-N23
5F-N24
5F-M11
5F-M12
5F-M13
5F-M14
5F-M15
5F-M16
| 5F-K11 |  |  | 3A-8-1 | 3B-8-1 | U5-3A-01 / 2P 30A | U5-3B-01 / 2P 30A | 5-DaHall1-PDU-05-30-1 | 5-DaHall1-PDU-06-30-1 | 220 | 30 | 05 | 1 | 220 | 30 | 06 | 1 | U5-3A 4P 300A | U5-3B 4P 300A | LV-5A #03 3P 320A | LV-5B #03 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0
| 5F-K12 |  |  | 3A-8-2 | 3B-8-2 | U5-3A-03 / 2P 30A | U5-3B-03 / 2P 30A | 5-DaHall1-PDU-05-30-3 | 5-DaHall1-PDU-06-30-3 | 220 | 30 | 05 | 3 | 220 | 30 | 06 | 3 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-K13 |  |  | 3A-8-3 | 3B-8-3 | U5-3A-05 / 2P 30A | U5-3B-05 / 2P 30A | 5-DaHall1-PDU-05-30-5 | 5-DaHall1-PDU-06-30-5 | 220 | 30 | 05 | 5 | 220 | 30 | 06 | 5 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-K14 |  |  | 3A-8-4 | 3B-8-4 | U5-3A-09 / 2P 30A | U5-3B-07 / 2P 30A | 5-DaHall1-PDU-05-30-9 | 5-DaHall1-PDU-06-30-7 | 220 | 30 | 05 | 9 | 220 | 30 | 06 | 7 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-K15 |  |  | 3A-8-5 | 3B-8-5 | U5-3A-11 / 2P 30A | U5-3B-09 / 2P 30A | 5-DaHall1-PDU-05-30-11 | 5-DaHall1-PDU-06-30-9 | 220 | 30 | 05 | 11 | 220 | 30 | 06 | 9 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-K16 |  |  | 3A-8-6 | 3B-8-6 | U5-3A-13 / 2P 30A | U5-3B-11 / 2P 30A | 5-DaHall1-PDU-05-30-13 | 5-DaHall1-PDU-06-30-11 | 220 | 30 | 05 | 13 | 220 | 30 | 06 | 11 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-K17 |  |  | 3A-8-7 | 3B-8-7 | U5-3A-15 / 2P 30A | U5-3B-15 / 2P 30A | 5-DaHall1-PDU-05-30-15 | 5-DaHall1-PDU-06-30-15 | 220 | 30 | 05 | 15 | 220 | 30 | 06 | 15 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-K18 |  |  | 3A-8-8 | 3B-8-8 | U5-3A-17 / 2P 30A | U5-3B-17 / 2P 30A | 5-DaHall1-PDU-05-30-17 | 5-DaHall1-PDU-06-30-17 | 220 | 30 | 05 | 17 | 220 | 30 | 06 | 17 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-J11 |  |  | 3A-9-1 | 3B-9-1 | U5-3A-19 / 2P 30A | U5-3B-19 / 2P 30A | 5-DaHall1-PDU-05-30-19 | 5-DaHall1-PDU-06-30-19 | 220 | 30 | 05 | 19 | 220 | 30 | 06 | 19 | U5-3A 4P 300A | U5-3B 4P 300A | LV-5A #03 3P 320A | LV-5B #03 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0
| 5F-J12 |  |  | 3A-9-2 | 3B-9-2 | U5-3A-21 / 2P 30A | U5-3B-21 / 2P 30A | 5-DaHall1-PDU-05-30-21 | 5-DaHall1-PDU-06-30-21 | 220 | 30 | 05 | 21 | 220 | 30 | 06 | 21 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-J13 |  |  | 3A-9-3 | 3B-9-3 | U5-3A-23 / 2P 30A | U5-3B-23 / 2P 30A | 5-DaHall1-PDU-05-30-23 | 5-DaHall1-PDU-06-30-23 | 220 | 30 | 05 | 23 | 220 | 30 | 06 | 23 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-J14 |  |  | 3A-9-4 | 3B-9-4 | U5-3A-27 / 2P 30A | U5-3B-25 / 2P 30A | 5-DaHall1-PDU-05-30-27 | 5-DaHall1-PDU-06-30-25 | 220 | 30 | 05 | 27 | 220 | 30 | 06 | 25 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-J15 |  |  | 3A-9-5 | 3B-9-5 | U5-3A-29 / 2P 30A | U5-3B-27 / 2P 30A | 5-DaHall1-PDU-05-30-29 | 5-DaHall1-PDU-06-30-27 | 220 | 30 | 05 | 29 | 220 | 30 | 06 | 27 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-J16 |  |  | 3A-9-6 | 3B-9-6 | U5-3A-31 / 2P 30A | U5-3B-29 / 2P 30A | 5-DaHall1-PDU-05-30-31 | 5-DaHall1-PDU-06-30-29 | 220 | 30 | 05 | 31 | 220 | 30 | 06 | 29 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-J17 |  |  | 3A-9-7 | 3B-9-7 | U5-3A-33 / 2P 30A | U5-3B-33 / 2P 30A | 5-DaHall1-PDU-05-30-33 | 5-DaHall1-PDU-06-30-33 | 220 | 30 | 05 | 33 | 220 | 30 | 06 | 33 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-J18 |  |  | 3A-9-8 | 3B-9-8 | U5-3A-35 / 2P 30A | U5-3B-35 / 2P 30A | 5-DaHall1-PDU-05-30-35 | 5-DaHall1-PDU-06-30-35 | 220 | 30 | 05 | 35 | 220 | 30 | 06 | 35 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-I11 |  |  | 3A-10-1 | 3B-10-1 | U5-3A-37 / 2P 30A | U5-3B-37 / 2P 30A | 5-DaHall1-PDU-05-30-37 | 5-DaHall1-PDU-06-30-37 | 220 | 30 | 05 | 37 | 220 | 30 | 06 | 37 | U5-3A 4P 300A | U5-3B 4P 300A | LV-5A #03 3P 320A | LV-5B #03 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 4.9826e-05 | 4.9826e-05 | 9.9652e-05 | 0 | 0 | 0 | OFF
| 5F-I12 |  |  | 3A-10-2 | 3B-10-2 | U5-3A-39 / 2P 30A | U5-3B-39 / 2P 30A | 5-DaHall1-PDU-05-30-39 | 5-DaHall1-PDU-06-30-39 | 220 | 30 | 05 | 39 | 220 | 30 | 06 | 39 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | OFF
| 5F-I13 |  |  | 3A-10-3 | 3B-10-3 | U5-3A-41 / 2P 30A | U5-3B-41 / 2P 30A | 5-DaHall1-PDU-05-30-41 | 5-DaHall1-PDU-06-30-41 | 220 | 30 | 05 | 41 | 220 | 30 | 06 | 41 | [6 empty] | 0 | 2.4334e-05 | 2.4334e-05 | 0 | 0 | 0 | OFF
| 5F-I14 |  |  | 3A-10-4 | 3B-10-4 | U5-3A-45 / 2P 30A | U5-3B-43 / 2P 30A | 5-DaHall1-PDU-05-30-45 | 5-DaHall1-PDU-06-30-43 | 220 | 30 | 05 | 45 | 220 | 30 | 06 | 43 | [6 empty] | 0 | 3.4758e-05 | 3.4758e-05 | 0 | 0 | 0 | OFF
| 5F-I15 |  |  | 3A-10-5 | 3B-10-5 | U5-3A-47 / 2P 30A | U5-3B-45 / 2P 30A | 5-DaHall1-PDU-05-30-47 | 5-DaHall1-PDU-06-30-45 | 220 | 30 | 05 | 47 | 220 | 30 | 06 | 45 | [6 empty] | 0 | 3.4758e-05 | 3.4758e-05 | 0 | 0 | 0 | OFF
| 5F-I16 |  |  | 3A-10-6 | 3B-10-6 | U5-3A-49 / 2P 30A | U5-3B-47 / 2P 30A | 5-DaHall1-PDU-05-30-49 | 5-DaHall1-PDU-06-30-47 | 220 | 30 | 05 | 49 | 220 | 30 | 06 | 47 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | OFF
| 5F-I17 |  |  | 3A-10-7 | 3B-10-7 | U5-3A-51 / 2P 30A | U5-3B-51 / 2P 30A | 5-DaHall1-PDU-05-30-51 | 5-DaHall1-PDU-06-30-51 | 220 | 30 | 05 | 51 | 220 | 30 | 06 | 51 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | OFF
| 5F-I18 |  |  | 3A-10-8 | 3B-10-8 | U5-3A-53 / 2P 30A | U5-3B-53 / 2P 30A | 5-DaHall1-PDU-05-30-53 | 5-DaHall1-PDU-06-30-53 | 220 | 30 | 05 | 53 | 220 | 30 | 06 | 53 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | OFF
C304 | 예비Rack#04/R-6-4 | LG CNS | 13 | 예비Rack#4 / R6-4-1 | 예비Rack#4 / R6-4-2 | LG PDU(A1), #22 / 2P 50A | LG PDU (B1), #22 /2P 50A | 5-DaHall1-PDU-19-50-22 | 5-DaHall1-PDU-20-50-22 | 220 | 50 | 19 | 22 | 220 | 50 | 20 | 22 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | 예비Rack#4 / R6-4-3 | 예비Rack#4 / R6-4-4 | LG PDU(A2), #22 / 2P 50A | LG PDU (B2), #22 / 2P 50A | 5-DaHall1-PDU-21-50-22 | 5-DaHall1-PDU-22-50-22 | 220 | 50 | 21 | 22 | 220 | 50 | 22 | 22 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C305 | 예비Rack#03/R6-3 | LG CNS | 13 | 예비Rack#3 / R6-3-1 | 예비Rack#3 / R6-3-2 | LG PDU(A1), #20 / 2P 50A | LG PDU (B1), #20 /2P 50A | 5-DaHall1-PDU-19-50-20 | 5-DaHall1-PDU-20-50-20 | 220 | 50 | 19 | 20 | 220 | 50 | 20 | 20 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | 예비Rack#3 / R6-3-3 | 예비Rack#3 / R6-3-4 | LG PDU(A2), #20 / 2P 50A | LG PDU (B2), #20 / 2P 50A | 5-DaHall1-PDU-21-50-20 | 5-DaHall1-PDU-22-50-20 | 220 | 50 | 21 | 20 | 220 | 50 | 22 | 20 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C306 | 예비Rack#02/R6-2 | LG CNS | 13 | 예비Rack#2 / R6-2-1 | 예비Rack#2 / R6-2-2 | LG PDU(A1), #18 / 2P 50A | LG PDU (B1), #18 /2P 50A | 5-DaHall1-PDU-19-50-18 | 5-DaHall1-PDU-20-50-18 | 220 | 50 | 19 | 18 | 220 | 50 | 20 | 18 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | 예비Rack#2 / R6-2-3 | 예비Rack#2 / R6-2-4 | LG PDU(A2), #18 / 2P 50A | LG PDU (B2), #18 / 2P 50A | 5-DaHall1-PDU-21-50-18 | 5-DaHall1-PDU-22-50-18 | 220 | 50 | 21 | 18 | 220 | 50 | 22 | 18 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C307 | 예비Rack#01/R6-1 | LG CNS | 13 | 예비Rack#1 / R6-1-1 | 예비Rack#1 / R6-1-2 | LG PDU(A1), #16 / 2P 50A | LG PDU (B1), #16 /2P 50A | 5-DaHall1-PDU-19-50-16 | 5-DaHall1-PDU-20-50-16 | 220 | 50 | 19 | 16 | 220 | 50 | 20 | 16 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | 예비Rack#1 / R6-1-3 | 예비Rack#1 / R6-1-4 | LG PDU(A2), #16 / 2P 50A | LG PDU (B2), #16 / 2P 50A | 5-DaHall1-PDU-21-50-16 | 5-DaHall1-PDU-22-50-16 | 220 | 50 | 21 | 16 | 220 | 50 | 22 | 16 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C404 | R5-4 | LG CNS | [5 empty] | 5-DaHall1-PDU-19-30-21 | 5-DaHall1-PDU-20-30-21 | 220 | 30 | 19 | 21 | 220 | 30 | 20 | 21 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A | '23.11.10 준비완료
[8 empty] | 5-DaHall1-PDU-21-30-21 | 5-DaHall1-PDU-22-30-21 | 220 | 30 | 21 | 21 | 220 | 30 | 22 | 21 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C405 | DGX Rack#3 / R5-3 | LG CNS | 13 | DGX Rack#3 / R5-3-1 | DGX Rack#3 / R5-3-2 | LG PDU(A1), #19 / 2P 30A | LG PDU (B1), #19 /2P 30A | 5-DaHall1-PDU-19-30-19 | 5-DaHall1-PDU-20-30-19 | 220 | 30 | 19 | 19 | 220 | 30 | 20 | 19 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | DGX Rack#3 / R5-3-3 | DGX Rack#3 / R5-3-4 | LG PDU(A2), #19 / 2P 30A | LG PDU (B2), #19 / 2P 30A | 5-DaHall1-PDU-21-30-19 | 5-DaHall1-PDU-22-30-19 | 220 | 30 | 21 | 19 | 220 | 30 | 22 | 19 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C406 | DGX Rack#2 / R5-2 | LG CNS | 13 | DGX Rack#2 / R5-2-1 | DGX Rack#2 / R5-2-2 | LG PDU(A1), #17 / 2P 30A | LG PDU (B1), #17 /2P 30A | 5-DaHall1-PDU-19-30-17 | 5-DaHall1-PDU-20-30-17 | 220 | 30 | 19 | 17 | 220 | 30 | 20 | 17 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | DGX Rack#2 / R5-2-3 | DGX Rack#2 / R5-2-4 | LG PDU(A2), #17 / 2P 30A | LG PDU (B2), #17 / 2P 30A | 5-DaHall1-PDU-21-30-17 | 5-DaHall1-PDU-22-30-17 | 220 | 30 | 21 | 17 | 220 | 30 | 22 | 17 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C407 | DGX Rack#1 / R5-1 | LG CNS | 13 | DGX Rack#1 / R5-1-1 | DGX Rack#1 / R5-1-2 | LG PDU(A1), #15 / 2P 30A | LG PDU (B1), #15 /2P 30A | 5-DaHall1-PDU-19-30-15 | 5-DaHall1-PDU-20-30-15 | 220 | 30 | 19 | 15 | 220 | 30 | 20 | 15 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | DGX Rack#1 / R5-1-3 | DGX Rack#1 / R5-1-4 | LG PDU(A2), #15 / 2P 30A | LG PDU (B2), #15 / 2P 30A | 5-DaHall1-PDU-21-30-15 | 5-DaHall1-PDU-22-30-15 | 220 | 30 | 21 | 15 | 220 | 30 | 22 | 15 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C504 | NetApp AFF#2 / R4-4 | LG CNS | 13 | NetApp AFF#2 / R4-4-1 | NetApp AFF#2 / R4-4-2 | LG PDU(A1), #14 / 2P 30A | LG PDU (B1), #14 /2P 30A | 5-DaHall1-PDU-19-30-14 | 5-DaHall1-PDU-20-30-14 | 220 | 30 | 19 | 14 | 220 | 30 | 20 | 14 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | NetApp AFF#2 / R4-4-3 | NetApp AFF#2 / R4-4-4 | LG PDU(A2), #14 / 2P 30A | LG PDU (B2), #14 / 2P 30A | 5-DaHall1-PDU-21-30-14 | 5-DaHall1-PDU-22-30-14 | 220 | 30 | 21 | 14 | 220 | 30 | 22 | 14 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C505 | NetApp FAS#1 / R4-3 | LG CNS | 13 | NetApp FAS#1 / R4-3-1 | NetApp FAS#1 / R4-3-2 | LG PDU(A1), #12 / 2P 30A | LG PDU (B1), #12 /2P 30A | 5-DaHall1-PDU-19-30-12 | 5-DaHall1-PDU-20-30-12 | 220 | 30 | 19 | 12 | 220 | 30 | 20 | 12 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | NetApp FAS#1 / R4-3-2 | NetApp FAS#1 / R4-3-4 | LG PDU(A2), #12 / 2P 30A | LG PDU (B2), #12 / 2P 30A | 5-DaHall1-PDU-21-30-12 | 5-DaHall1-PDU-22-30-12 | 220 | 30 | 21 | 12 | 220 | 30 | 22 | 12 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C506 | A40 Rack#2 / R4-2 | LG CNS | 13 | A40 Rack#2 / R4-2-1 | A40 Rack#2 / R4-2-2 | LG PDU(A1), #10 / 2P 50A | LG PDU (B1), #10 /2P 50A | 5-DaHall1-PDU-19-50-10 | 5-DaHall1-PDU-20-50-10 | 220 | 50 | 19 | 10 | 220 | 50 | 20 | 10 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | A40 Rack#2 / R4-2-3 | A40 Rack#2 / R4-2-4 | LG PDU(A2), #10 / 2P 50A | LG PDU (B2), #10 / 2P 50A | 5-DaHall1-PDU-21-50-10 | 5-DaHall1-PDU-22-50-10 | 220 | 50 | 21 | 10 | 220 | 50 | 22 | 10 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C507 | A40 Rack#1 / R4-1 | LG CNS | 13 | A40 Rack#1 / R4-1-1 | A40 Rack#1 / R4-1-2 | LG PDU(A1), #08 / 2P 50A | LG PDU (B1), #08 /2P 50A | 5-DaHall1-PDU-19-50-8 | 5-DaHall1-PDU-20-50-8 | 220 | 50 | 19 | 8 | 220 | 50 | 20 | 8 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | A40 Rack#1 / R4-1-3 | A40 Rack#1 / R4-1-4 | LG PDU(A2), #08 / 2P 50A | LG PDU (B2), #08 / 2P 50A | 5-DaHall1-PDU-21-50-8 | 5-DaHall1-PDU-22-50-8 | 220 | 50 | 21 | 8 | 220 | 50 | 22 | 8 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C604 | R3-4 | LG CNS | [5 empty] | 5-DaHall1-PDU-19-50-24 | 5-DaHall1-PDU-20-50-24 | 220 | 50 | 19 | 24 | 220 | 50 | 20 | 24 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A | '23.11.10 준비완료
[8 empty] | 5-DaHall1-PDU-21-50-24 | 5-DaHall1-PDU-22-50-24 | 220 | 50 | 21 | 24 | 220 | 50 | 22 | 24 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C605 | NW/Mgmt Rack / R3-3 | LG CNS | 13 | NW/Mgmt Rack / R3-3-1 | NW/Mgmt Rack / R3-3-2 | LG PDU(A1), #06 / 2P 30A | LG PDU (B1), #06 /2P 30A | 5-DaHall1-PDU-19-30-6 | 5-DaHall1-PDU-20-30-6 | 220 | 30 | 19 | 6 | 220 | 30 | 20 | 6 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | NW/Mgmt Rack / R3-3-3 | NW/Mgmt Rack / R3-3-4 | LG PDU(A2), #06 / 2P 30A | LG PDU (B2), #06 / 2P 30A | 5-DaHall1-PDU-21-30-6 | 5-DaHall1-PDU-22-30-6 | 220 | 30 | 21 | 6 | 220 | 30 | 22 | 6 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C606 | RTX Rack#9 / R3-2 | LG CNS | 13 | RTX Rack#9 / R3-2-1 | RTX Rack#9 / R3-2-2 | LG PDU(A1), #04 / 2P 50A | LG PDU (B1), #04 /2P 50A | 5-DaHall1-PDU-19-50-4 | 5-DaHall1-PDU-20-50-4 | 220 | 50 | 19 | 4 | 220 | 50 | 20 | 4 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | RTX Rack#9 / R3-2-3 | RTX Rack#9 / R3-2-4 | LG PDU(A2), #04 / 2P 50A | LG PDU (B2), #04 / 2P 50A | 5-DaHall1-PDU-21-50-4 | 5-DaHall1-PDU-22-50-4 | 220 | 50 | 21 | 4 | 220 | 50 | 22 | 4 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C607 | RTX Rack#8 / R3-1 | LG CNS | 13 | RTX Rack#8 / R3-1-1 | RTX Rack#8 / R3-1-2 | LG PDU(A1), #02 / 2P 50A | LG PDU (B1), #02 /2P 50A | 5-DaHall1-PDU-19-50-2 | 5-DaHall1-PDU-20-50-2 | 220 | 50 | 19 | 2 | 220 | 50 | 20 | 2 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | RTX Rack#8 / R3-1-3 | RTX Rack#8 / R3-1-4 | LG PDU(A2), #02 / 2P 50A | LG PDU (B2), #02 / 2P 50A | 5-DaHall1-PDU-21-50-2 | 5-DaHall1-PDU-22-50-2 | 220 | 50 | 21 | 2 | 220 | 50 | 22 | 2 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C704 | RTX Rack#7 / R2-4 | LG CNS | 13 | RTX Rack#7 / R2-4-1 | RTX Rack#7 / R2-4-2 | LG PDU(A1), #13 / 2P 50A | LG PDU (B1), #13 /2P 50A | 5-DaHall1-PDU-19-50-13 | 5-DaHall1-PDU-20-50-13 | 220 | 50 | 19 | 13 | 220 | 50 | 20 | 13 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | RTX Rack#7 / R2-4-3 | RTX Rack#7 / R2-4-4 | LG PDU(A2), #13 / 2P 50A | LG PDU (B2), #13 / 2P 50A | 5-DaHall1-PDU-21-50-13 | 5-DaHall1-PDU-22-50-13 | 220 | 50 | 21 | 13 | 220 | 50 | 22 | 13 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C705 | RTX Rack#6 / R2-3 | LG CNS | 13 | RTX Rack#6 / R2-3-1 | RTX Rack#6 / R2-3-2 | LG PDU(A1), #11 / 2P 50A | LG PDU (B1), #11 /2P 50A | 5-DaHall1-PDU-19-50-11 | 5-DaHall1-PDU-20-50-11 | 220 | 50 | 19 | 11 | 220 | 50 | 20 | 11 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | RTX Rack#6 / R2-3-3 | RTX Rack#6 / R2-3-4 | LG PDU(A2), #11 / 2P 50A | LG PDU (B2), #11 / 2P 50A | 5-DaHall1-PDU-21-50-11 | 5-DaHall1-PDU-22-50-11 | 220 | 50 | 21 | 11 | 220 | 50 | 22 | 11 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C706 | RTX Rack#5 / R2-2 | LG CNS | 13 | RTX Rack#5 / R2-2-1 | RTX Rack#5 / R2-2-2 | LG PDU(A1), #09 / 2P 50A | LG PDU (B1), #09 /2P 50A | 5-DaHall1-PDU-19-50-9 | 5-DaHall1-PDU-20-50-9 | 220 | 50 | 19 | 9 | 220 | 50 | 20 | 9 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | RTX Rack#5 / R2-2-3 | RTX Rack#5 / R2-2-4 | LG PDU(A2), #09 / 2P 50A | LG PDU (B2), #09 / 2P 50A | 5-DaHall1-PDU-21-50-9 | 5-DaHall1-PDU-22-50-9 | 220 | 50 | 21 | 9 | 220 | 50 | 22 | 9 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C707 | RTX Rack#4 / R2-1 | LG CNS | 13 | RTX Rack#4 / R2-1-1 | RTX Rack#4 / R2-1-2 | LG PDU(A1), #07 / 2P 50A | LG PDU (B1), #07 /2P 50A | 5-DaHall1-PDU-19-50-7 | 5-DaHall1-PDU-20-50-7 | 220 | 50 | 19 | 7 | 220 | 50 | 20 | 7 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | RTX Rack#4 / R2-1-3 | RTX Rack#4 / R2-1-4 | LG PDU(A2), #07 / 2P 50A | LG PDU (B2), #07 / 2P 50A | 5-DaHall1-PDU-21-50-7 | 5-DaHall1-PDU-22-50-7 | 220 | 50 | 21 | 7 | 220 | 50 | 22 | 7 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C804 | RTX Rack#4 / R1-4 | LG CNS | 13 | RTX Rack#4 / R1-4-1 | RTX Rack#4 / R1-4-2 |  |  | 5-DaHall1-PDU-19-50-23 | 5-DaHall1-PDU-20-50-23 | 220 | 50 | 19 | 23 | 220 | 50 | 20 | 23 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A | '23.12.05 투입
|  |  |  | RTX Rack#4 / R1-4-3 | RTX Rack#4 / R1-4-4 |  |  | 5-DaHall1-PDU-21-50-23 | 5-DaHall1-PDU-22-50-23 | 220 | 50 | 21 | 23 | 220 | 50 | 22 | 23 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C805 | RTX Rack#3 / R1-3 | LG CNS | 13 | RTX Rack#3 / R1-3-1 | RTX Rack#3 / R1-3-2 | LG PDU(A1), #05 / 2P 50A | LG PDU (B1), #05 /2P 50A | 5-DaHall1-PDU-19-50-5 | 5-DaHall1-PDU-20-50-5 | 220 | 50 | 19 | 5 | 220 | 50 | 20 | 5 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | RTX Rack#3 / R1-3-3 | RTX Rack#3 / R1-3-4 | LG PDU(A2), #05 / 2P 50A | LG PDU (B2), #05 / 2P 50A | 5-DaHall1-PDU-21-50-5 | 5-DaHall1-PDU-22-50-5 | 220 | 50 | 21 | 5 | 220 | 50 | 22 | 5 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C806 | RTX Rack#2 / R1-2 | LG CNS | 13 | RTX Rack#2 / R1-2-1 | RTX Rack#2 / R1-2-2 | LG PDU(A1), #03 / 2P 50A | LG PDU (B1), #03 /2P 50A | 5-DaHall1-PDU-19-50-3 | 5-DaHall1-PDU-20-50-3 | 220 | 50 | 19 | 3 | 220 | 50 | 20 | 3 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | RTX Rack#2 / R1-2-3 | RTX Rack#2 / R1-2-4 | LG PDU(A2), #03 / 2P 50A | LG PDU (B2), #03 / 2P 50A | 5-DaHall1-PDU-21-50-3 | 5-DaHall1-PDU-22-50-3 | 220 | 50 | 21 | 3 | 220 | 50 | 22 | 3 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A
C807 | RTX Rack#1 / R1-1 | LG CNS | 13 | RTX Rack#1 / R1-1-1 | RTX Rack#1 / R1-1-2 | LG PDU(A1), #01 / 2P 50A | LG PDU (B1), #01 /2P 50A | 5-DaHall1-PDU-19-50-1 | 5-DaHall1-PDU-20-50-1 | 220 | 50 | 19 | 1 | 220 | 50 | 20 | 1 | LG PDU (A1) | LG PDU (B1) | LV-5A, #05 3P 320A | LV-5B, #04 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | #N/A | #N/A | #N/A
|  |  |  | RTX Rack#1 / R1-1-3 | RTX Rack#1 / R1-1-4 | LG PDU(A2), #01 / 2P 50A | LG PDU (B2), #01 / 2P 50A | 5-DaHall1-PDU-21-50-1 | 5-DaHall1-PDU-22-50-1 | 220 | 50 | 21 | 1 | 220 | 50 | 22 | 1 | LG PDU (A2) | LG PDU (B2) | LV-5A, #06 3P 320A | LV-5B, #05 3P 320A |  |  | 0 | 0 |  | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0
C901 | 5F-H11 |  |  | 3A-11-1 | 3B-11-1 | U5-3A-02 / 2P 30A | U5-3B-02 / 2P 30A | 5-DaHall1-PDU-05-30-2 | 5-DaHall1-PDU-06-30-2 | 220 | 30 | 05 | 2 | 220 | 30 | 06 | 2 | U5-3A 4P 300A | U5-3B 4P 300A | LV-5A #03 3P 320A | LV-5B #03 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0 | OFF
C902 | 5F-H12 |  |  | 3A-11-2 | 3B-11-2 | U5-3A-04 / 2P 30A | U5-3B-04 / 2P 30A | 5-DaHall1-PDU-05-30-4 | 5-DaHall1-PDU-06-30-4 | 220 | 30 | 05 | 4 | 220 | 30 | 06 | 4 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | OFF
C903 | 5F-H13 |  |  | 3A-11-3 | 3B-11-3 | U5-3A-06 / 2P 30A | U5-3B-06 / 2P 30A | 5-DaHall1-PDU-05-30-6 | 5-DaHall1-PDU-06-30-6 | 220 | 30 | 05 | 6 | 220 | 30 | 06 | 6 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | OFF
C904 | 5F-H14 |  |  | 3A-11-4 | 3B-11-4 | U5-3A-08 / 2P 30A | U5-3B-08 / 2P 30A | 5-DaHall1-PDU-05-30-8 | 5-DaHall1-PDU-06-30-8 | 220 | 30 | 05 | 8 | 220 | 30 | 06 | 8 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | OFF
C905 | 5F-H15 |  |  | 3A-11-5 | 3B-11-5 | U5-3A-10 / 2P 30A | U5-3B-10 / 2P 30A | 5-DaHall1-PDU-05-30-10 | 5-DaHall1-PDU-06-30-10 | 220 | 30 | 05 | 10 | 220 | 30 | 06 | 10 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | OFF
C906 | 5F-H16 |  |  | 3A-11-6 | 3B-11-6 | U5-3A-12 / 2P 30A | U5-3B-12 / 2P 30A | 5-DaHall1-PDU-05-30-12 | 5-DaHall1-PDU-06-30-12 | 220 | 30 | 05 | 12 | 220 | 30 | 06 | 12 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | OFF
C907 | 5F-H17 |  |  | 3A-11-7 | 3B-11-7 | U5-3A-14 / 2P 30A | U5-3B-16 / 2P 30A | 5-DaHall1-PDU-05-30-14 | 5-DaHall1-PDU-06-30-16 | 220 | 30 | 05 | 14 | 220 | 30 | 06 | 16 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | OFF
C908 | 5F-H18 |  |  | 3A-11-8 | 3B-11-8 | U5-3A-16 / 2P 30A | U5-3B-18 / 2P 30A | 5-DaHall1-PDU-05-30-16 | 5-DaHall1-PDU-06-30-18 | 220 | 30 | 05 | 16 | 220 | 30 | 06 | 18 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | OFF
C909
C910
C1001 | 5F-G11 |  |  | 3A-12-1 | 3B-12-1 | U5-3A-18 / 2P 30A | U5-3B-20 / 2P 30A | 5-DaHall1-PDU-05-30-18 | 5-DaHall1-PDU-06-30-20 | 220 | 30 | 05 | 18 | 220 | 30 | 06 | 20 | U5-3A 4P 300A | U5-3B 4P 300A | LV-5A #03 3P 320A | LV-5B #03 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0 | OFF
C1002 | 5F-G12 |  |  | 3A-12-2 | 3B-12-2 | U5-3A-20 / 2P 30A | U5-3B-22 / 2P 30A | 5-DaHall1-PDU-05-30-20 | 5-DaHall1-PDU-06-30-22 | 220 | 30 | 05 | 20 | 220 | 30 | 06 | 22 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | OFF
C1003 | 5F-G13 |  |  | 3A-12-3 | 3B-12-3 | U5-3A-22 / 2P 30A | U5-3B-24 / 2P 30A | 5-DaHall1-PDU-05-30-22 | 5-DaHall1-PDU-06-30-24 | 220 | 30 | 05 | 22 | 220 | 30 | 06 | 24 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | OFF
C1004 | 5F-G14 |  |  | 3A-12-4 | 3B-12-4 | U5-3A-24 / 2P 30A | U5-3B-26 / 2P 30A | 5-DaHall1-PDU-05-30-24 | 5-DaHall1-PDU-06-30-26 | 220 | 30 | 05 | 24 | 220 | 30 | 06 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | OFF
C1005 | 5F-G15 |  |  | 3A-12-5 | 3B-12-5 | U5-3A-26 / 2P 30A | U5-3B-28 / 2P 30A | 5-DaHall1-PDU-05-30-26 | 5-DaHall1-PDU-06-30-28 | 220 | 30 | 05 | 26 | 220 | 30 | 06 | 28 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | OFF
C1006 | 5F-G16 |  |  | 3A-12-6 | 3B-12-6 | U5-3A-28 / 2P 30A | U5-3B-30 / 2P 30A | 5-DaHall1-PDU-05-30-28 | 5-DaHall1-PDU-06-30-30 | 220 | 30 | 05 | 28 | 220 | 30 | 06 | 30 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | OFF
C1007 | 5F-G17 |  |  | 3A-12-7 | 3B-12-7 | U5-3A-30 / 2P 30A | U5-3B-34 / 2P 30A | 5-DaHall1-PDU-05-30-30 | 5-DaHall1-PDU-06-30-34 | 220 | 30 | 05 | 30 | 220 | 30 | 06 | 34 | [6 empty] | 0 | 0.00082609 | 0.00082609 | 0 | 0 | 0 | OFF
C1008 | 5F-G18 |  |  | 3A-12-8 | 3B-12-8 | U5-3A-32 / 2P 30A | U5-3B-36 / 2P 30A | 5-DaHall1-PDU-05-30-32 | 5-DaHall1-PDU-06-30-36 | 220 | 30 | 05 | 32 | 220 | 30 | 06 | 36 | [6 empty] | 0 | 0.00040088 | 0.00040088 | 0 | 0 | 0 | OFF
C1009
C1010
|  |  |  | 1A-1-1 | 1B-1-1 | U5-1A-01 / 2P 30A | U5-1B-01 / 2P 30A | 5-DaHall1-PDU-01-30-1 | 5-DaHall1-PDU-02-30-1 | 220 | 30 | 01 | 1 | 220 | 30 | 02 | 1 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0
| 5F-R12 |  |  | 1A-1-2 | 1B-1-2 | U5-1A-03 / 2P 30A | U5-1B-03 / 2P 30A | 5-DaHall1-PDU-01-30-3 | 5-DaHall1-PDU-02-30-3 | 220 | 30 | 01 | 3 | 220 | 30 | 02 | 3 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-R13 |  |  | 1A-1-3 | 1B-1-3 | U5-1A-05 / 2P 30A | U5-1B-05 / 2P 30A | 5-DaHall1-PDU-01-30-5 | 5-DaHall1-PDU-02-30-5 | 220 | 30 | 01 | 5 | 220 | 30 | 02 | 5 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-R14 |  |  | 1A-1-4 | 1B-1-4 | U5-1A-07 / 2P 30A | U5-1B-07 / 2P 30A | 5-DaHall1-PDU-01-30-7 | 5-DaHall1-PDU-02-30-7 | 220 | 30 | 01 | 7 | 220 | 30 | 02 | 7 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
G1101 | 5F-R15 | Cloudflare | 5 | 1A-1-5 | 1B-1-5 | U5-1A-09 / 2P 30A | U5-1B-09 / 2P 30A | 5-DaHall1-PDU-01-30-9 | 5-DaHall1-PDU-02-30-9 | 220 | 30 | 01 | 9 | 220 | 30 | 02 | 9 | [6 empty] | 13.8976 | 11.6589 | 25.5566 | 2138 | 1792.6 | 3930.6
G1102 | 5F-R16 | Cloudflare | 5 | 1A-1-6 | 1B-1-6 | U5-1A-11 / 2P 30A | U5-1B-11 / 2P 30A | 5-DaHall1-PDU-01-30-11 | 5-DaHall1-PDU-02-30-11 | 220 | 30 | 01 | 11 | 220 | 30 | 02 | 11 | [6 empty] | 11.3149 | 12.8737 | 24.1886 | 1693.2 | 1939.7 | 3632.9
G1103 | 5F-R17 | Cloudflare | 5 | 1A-1-7 | 1B-1-7 | U5-1A-13 / 2P 30A | U5-1B-13 / 2P 30A | 5-DaHall1-PDU-01-30-13 | 5-DaHall1-PDU-02-30-13 | 220 | 30 | 01 | 13 | 220 | 30 | 02 | 13 | [6 empty] | 13.7686 | 11.4483 | 25.217 | 2079.2 | 1716.3 | 3795.5
G1104 | 5F-R18 | Cloudflare | 5 | 1A-1-8 | 1B-1-8 | U5-1A-15 / 2P 30A | U5-1B-15 / 2P 30A | 5-DaHall1-PDU-01-30-15 | 5-DaHall1-PDU-02-30-15 | 220 | 30 | 01 | 15 | 220 | 30 | 02 | 15 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
G1105 | 5F-R19 | Cloudflare | 5 | 1A-1-9 | 1B-1-9 | U5-1A-17 / 2P 30A | U5-1B-17 / 2P 30A | 5-DaHall1-PDU-01-30-17 | 5-DaHall1-PDU-02-30-17 | 220 | 30 | 01 | 17 | 220 | 30 | 02 | 17 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
G1201 | 번호없음 | Cloudflare | 5 | 1A-2-1 | 1B-2-1 | U5-1A-31 / 2P 30A | U5-1B-31 / 2P 30A | 5-DaHall1-PDU-01-30-31 | 5-DaHall1-PDU-02-30-31 | 220 | 30 | 01 | 31 | 220 | 30 | 02 | 31 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA |  | 11.0998 | 11.4642 | 22.564 | 1747.7 | 1800.8 | 3548.5
G1202 | 5F-Q12 | Cloudflare | 5 | 1A-2-2 | 1B-2-2 | U5-1A-33 / 2P 30A | U5-1B-33 / 2P 30A | 5-DaHall1-PDU-01-30-33 | 5-DaHall1-PDU-02-30-33 | 220 | 30 | 01 | 33 | 220 | 30 | 02 | 33 | [6 empty] | 9.9455 | 11.5709 | 21.5164 | 1565.8 | 1829.4 | 3395.2
G1203 | 5F-Q13 | Cloudflare | 5 | 1A-2-3 | 1B-2-3 | U5-1A-35 / 2P 30A | U5-1B-35 / 2P 30A | 5-DaHall1-PDU-01-30-35 | 5-DaHall1-PDU-02-30-35 | 220 | 30 | 01 | 35 | 220 | 30 | 02 | 35 | [6 empty] | 11.6982 | 9.7301 | 21.4283 | 1854.4 | 1541 | 3395.4
G1204 | 5F-Q14 | Cloudflare | 5 | 1A-2-4 | 1B-2-4 | U5-1A-37 / 2P 30A | U5-1B-37 / 2P 30A | 5-DaHall1-PDU-01-30-37 | 5-DaHall1-PDU-02-30-37 | 220 | 30 | 01 | 37 | 220 | 30 | 02 | 37 | [6 empty] | 9.5055 | 11.348 | 20.8535 | 1503.8 | 1798.5 | 3302.3
G1205 | 5F-Q15 | Cloudflare | 5 | 1A-2-5 | 1B-2-5 | U5-1A-39 / 2P 30A | U5-1B-39 / 2P 30A | 5-DaHall1-PDU-01-30-39 | 5-DaHall1-PDU-02-30-39 | 220 | 30 | 01 | 39 | 220 | 30 | 02 | 39 | [6 empty] | 11.8317 | 9.5155 | 21.3472 | 1763.3 | 1409.5 | 3172.8 |  |  | 14.3454
| 5F-Q16 |  |  | 1A-2-6 | 1B-2-6 | U5-1A-41 / 2P 30A | U5-1B-41 / 2P 30A | 5-DaHall1-PDU-01-30-41 | 5-DaHall1-PDU-02-30-41 | 220 | 30 | 01 | 41 | 220 | 30 | 02 | 41 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-Q17 |  |  | 1A-2-7 | 1B-2-7 | U5-1A-43 / 2P 30A | U5-1B-43 / 2P 30A | 5-DaHall1-PDU-01-30-43 | 5-DaHall1-PDU-02-30-43 | 220 | 30 | 01 | 43 | 220 | 30 | 02 | 43 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-Q18 |  |  | 1A-2-8 | 1B-2-8 | U5-1A-45 / 2P 30A | U5-1B-45 / 2P 30A | 5-DaHall1-PDU-01-30-45 | 5-DaHall1-PDU-02-30-45 | 220 | 30 | 01 | 45 | 220 | 30 | 02 | 45 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-Q19 |  |  | 1A-2-9 | 1B-2-9 | U5-1A-47 / 2P 30A | U5-1B-47 / 2P 30A | 5-DaHall1-PDU-01-30-47 | 5-DaHall1-PDU-02-30-47 | 220 | 30 | 01 | 47 | 220 | 30 | 02 | 47 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
G2101 | 5F-P-12 | LG U Plus | 2.2 | 1A-1-10 | 1B-1-10 | U5-1A-19 / 2P 30A | U5-1B-19 / 2P 30A | 5-DaHall1-PDU-01-30-19 | 5-DaHall1-PDU-02-30-19 | 220 | 30 | 01 | 19 | 220 | 30 | 02 | 19 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 1.0405 | 0 | 1.0405 | 123.4 | 0 | 123.4 | 구글104
G2102 | 5F-P-13 | LG U Plus | 2.2 | 1A-1-11 | 1B-1-11 | U5-1A-21 / 2P 30A | U5-1B-21 / 2P 30A | 5-DaHall1-PDU-01-30-21 | 5-DaHall1-PDU-02-30-21 | 220 | 30 | 01 | 21 | 220 | 30 | 02 | 21 | [6 empty] | 1.4766 | 1.6313 | 3.108 | 186.7 | 218.5 | 405.2 | 구글103
G2103 | 5F-P-14 | LG U Plus | 2.2 | 1A-1-12 | 1B-1-12 | U5-1A-23 / 2P 30A | U5-1B-23 / 2P 30A | 5-DaHall1-PDU-01-30-23 | 5-DaHall1-PDU-02-30-23 | 220 | 30 | 01 | 23 | 220 | 30 | 02 | 23 | [6 empty] | 1.5398 | 1.3209 | 2.8607 | 226.1 | 192.6 | 418.7 | 구글102
G2104 | 5F-P-15 | LG U Plus | 2.2 | 1A-1-13 | 1B-1-13 | U5-1A-25 / 2P 30A | U5-1B-25 / 2P 30A | 5-DaHall1-PDU-01-30-25 | 5-DaHall1-PDU-02-30-25 | 220 | 30 | 01 | 25 | 220 | 30 | 02 | 25 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 구글101
| 번호없음 |  |  | 1A-4-1 |  | U5-1A-42 / 2P 30A |  | 5-DaHall1-PDU-01-30-42 |  | 220 | 30 | 01 | 42 |  |  |  |  | U5-1A 4P 300A |  | LV-5A #01 3P 320A |  | TR-5A 1000KVA |  | 0 |  | 0 | 0 |  | 0
| 5F-O12 |  |  | 1A-4-2 | 1B-4-2 | U5-1A-44 / 2P 30A | U5-1B-44 / 2P 30A | 5-DaHall1-PDU-01-30-44 | 5-DaHall1-PDU-02-30-44 | 220 | 30 | 01 | 44 | 220 | 30 | 02 | 44 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0
G2203 | 5F-O-14 | LG U Plus | 2.2 | 1A-2-12 | 1B-2-12 | U5-1A-04 / 2P 30A | U5-1B-04 / 2P 30A | 5-DaHall1-PDU-01-30-4 | 5-DaHall1-PDU-02-30-4 | 220 | 30 | 01 | 4 | 220 | 30 | 02 | 4 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 구글202
G2204 | 5F-O-15 | LG U Plus | 2.2 | 1A-2-13 | 1B-2-13 | U5-1A-06 / 2P 30A | U5-1B-06 / 2P 30A | 5-DaHall1-PDU-01-30-6 | 5-DaHall1-PDU-02-30-6 | 220 | 30 | 01 | 6 | 220 | 30 | 02 | 6 | [6 empty] | 1.5294 | 1.252 | 2.7815 | 216.2 | 179.8 | 396 | 구글201
| 시스템박스 | LG U Plus |  | 1A-2-15 |  | U5-1A-10 / 2P 30A |  | 5-DaHall1-PDU-01-30-10 |  | 220 | 30 | 01 | 10 | [10 empty] | 0 |  | 0 | 0 |  | 0 | 구글
| 지문인식기 | LG U Plus |  |  | 1B-2-15 |  | U5-1B-10 / 2P 30A |  | 5-DaHall1-PDU-02-30-10 |  |  |  |  | 220 | 30 | 02 | 10 |  | U5-1B 4P 300A |  | LV-5B #01 3P 320A |  |  |  | 0 | 0 |  | 0 | 0 | 구글 |  | 0.7524
G3101 | 5F-M-04 | Vodafone Enterprise Global Limited | 2.2 | [22 empty] | 0 |  |  |  | 보다폰#3
G3102 | 5F-M-05 | Vodafone Enterprise Global Limited | 2.2 | - | - | U5-1A-50 / 2P 30A | U5-1B-50 / 2P 30A | 5-DaHall1-PDU-01-30-50 | 5-DaHall1-PDU-02-30-50 | 220 | 30 | 01 | 50 | 220 | 30 | 02 | 50 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0 | 보다폰#2 | 1A-4-5 | 1B-4-5
G3103 | 5F-M-06 | Vodafone Enterprise Global Limited | 2.2 | - | - | U5-1A-3P-02 / 3P 60A | U5-1B-3P-02 / 3P 60A | 5-DaHall1-PDU-01-60-2 | 5-DaHall1-PDU-02-60-2 | 380 | 60 | 01 | 2 | 380 | 60 | 02 | 2 | [6 empty] | 1.3337 | 1.4058 | 5.5836 | 32.8 | 32.7 | 65.5 | 보다폰 정류기
|  |  |  | - | - | U5-1A-48 / 2P 30A | U5-1B-48 / 2P 30A | 5-DaHall1-PDU-01-30-48 | 5-DaHall1-PDU-02-30-48 | 220 | 30 | 01 | 48 | 220 | 30 | 02 | 48 | [6 empty] | 1.7392 | 1.1049 |  | 269.7 | 173.8 | 443.5 | 보다폰#1 | 1A-4-4 | 1B-4-4
| 번호없음 |  |  | 2A-5-1 | 2B-5-1 | U5-2A-21 / 2P 30A | U5-2B-21 / 2P 30A | 5-DaHall1-PDU-03-30-21 | 5-DaHall1-PDU-04-30-21 | 220 | 30 | 03 | 21 | 220 | 30 | 04 | 21 | U5-2A 4P 300A | U5-2B 4P 300A | LV-5A #02 3P 320A | LV-5B #02 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0 | OFF
| 5F-N12 |  |  | 2A-5-2 | 2B-5-2 | U5-2A-23 / 2P 30A | U5-2B-23 / 2P 30A | 5-DaHall1-PDU-03-30-23 | 5-DaHall1-PDU-04-30-23 | 220 | 30 | 03 | 23 | 220 | 30 | 04 | 23 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-N13 |  |  | 2A-5-3 | 2B-5-3 | U5-2A-25 / 2P 30A | U5-2B-25 / 2P 30A | 5-DaHall1-PDU-03-30-25 | 5-DaHall1-PDU-04-30-25 | 220 | 30 | 03 | 25 | 220 | 30 | 04 | 25 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-N14 |  |  | 2A-5-4 | 2B-5-4 | U5-2A-27 / 2P 30A | U5-2B-27 / 2P 30A | 5-DaHall1-PDU-03-30-27 | 5-DaHall1-PDU-04-30-27 | 220 | 30 | 03 | 27 | 220 | 30 | 04 | 27 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-N15 |  |  | 2A-5-5 | 2B-5-5 | U5-2A-29 / 2P 30A | U5-2B-29 / 2P 30A | 5-DaHall1-PDU-03-30-29 | 5-DaHall1-PDU-04-30-29 | 220 | 30 | 03 | 29 | 220 | 30 | 04 | 29 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-N16 |  |  | 2A-5-6 | 2B-5-6 | U5-2A-31 / 2P 30A | U5-2B-31 / 2P 30A | 5-DaHall1-PDU-03-30-31 | 5-DaHall1-PDU-04-30-31 | 220 | 30 | 03 | 31 | 220 | 30 | 04 | 31 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-N17 |  |  | 2A-5-7 | 2B-5-7 | U5-2A-33 / 2P 30A | U5-2B-33 / 2P 30A | 5-DaHall1-PDU-03-30-33 | 5-DaHall1-PDU-04-30-33 | 220 | 30 | 03 | 33 | 220 | 30 | 04 | 33 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-O16 |  |  | 2A-4-6 | 2B-4-6 | U5-2A-01 / 2P 30A | U5-2B-01 / 2P 30A | 5-DaHall1-PDU-03-30-1 | 5-DaHall1-PDU-04-30-1 | 220 | 30 | 03 | 1 | 220 | 30 | 04 | 1 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-O17 |  |  | 2A-4-7 | 2B-4-7 | U5-2A-03 / 2P 30A | U5-2B-03 / 2P 30A | 5-DaHall1-PDU-03-30-3 | 5-DaHall1-PDU-04-30-3 | 220 | 30 | 03 | 3 | 220 | 30 | 04 | 3 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 번호없음 |  |  | 1A-3-1 | 1B-3-1 | U5-1A-12 / 2P 30A | U5-1B-12 / 2P 30A | 5-DaHall1-PDU-01-30-12 | 5-DaHall1-PDU-02-30-12 | 220 | 30 | 01 | 12 | 220 | 30 | 02 | 12 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0 | OFF
| 5F-P12 |  |  | 1A-3-2 | 1B-3-2 | U5-1A-14 / 2P 30A | U5-1B-14 / 2P 30A | 5-DaHall1-PDU-01-30-14 | 5-DaHall1-PDU-02-30-14 | 220 | 30 | 01 | 14 | 220 | 30 | 02 | 14 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-P13 |  |  | 1A-3-3 | 1B-3-3 | U5-1A-16 / 2P 30A | U5-1B-16 / 2P 30A | 5-DaHall1-PDU-01-30-16 | 5-DaHall1-PDU-02-30-16 | 220 | 30 | 01 | 16 | 220 | 30 | 02 | 16 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-P14 |  |  | 1A-3-4 | 1B-3-4 | U5-1A-18 / 2P 30A | U5-1B-18 / 2P 30A | 5-DaHall1-PDU-01-30-18 | 5-DaHall1-PDU-02-30-18 | 220 | 30 | 01 | 18 | 220 | 30 | 02 | 18 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-P15 |  |  | 1A-3-5 | 1B-3-5 | U5-1A-20 / 2P 30A | U5-1B-20 / 2P 30A | 5-DaHall1-PDU-01-30-20 | 5-DaHall1-PDU-02-30-20 | 220 | 30 | 01 | 20 | 220 | 30 | 02 | 20 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-P16 |  |  | 1A-3-6 | 1B-3-6 | U5-1A-22 / 2P 30A | U5-1B-22 / 2P 30A | 5-DaHall1-PDU-01-30-22 | 5-DaHall1-PDU-02-30-22 | 220 | 30 | 01 | 22 | 220 | 30 | 02 | 22 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-P17 |  |  | 1A-3-7 | 1B-3-7 | U5-1A-24 / 2P 30A | U5-1B-24 / 2P 30A | 5-DaHall1-PDU-01-30-24 | 5-DaHall1-PDU-02-30-24 | 220 | 30 | 01 | 24 | 220 | 30 | 02 | 24 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-P18 |  |  | 1A-3-8 | 1B-3-8 | U5-1A-26 / 2P 30A | U5-1B-26 / 2P 30A | 5-DaHall1-PDU-01-30-26 | 5-DaHall1-PDU-02-30-26 | 220 | 30 | 01 | 26 | 220 | 30 | 02 | 26 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-P19 |  |  | 1A-3-9 | 1B-3-9 | U5-1A-28 / 2P 30A | U5-1B-28 / 2P 30A | 5-DaHall1-PDU-01-30-28 | 5-DaHall1-PDU-02-30-28 | 220 | 30 | 01 | 28 | 220 | 30 | 02 | 28 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-P20 |  |  | 1A-3-10 | 1B-3-10 | U5-1A-30 / 2P 30A | U5-1B-30 / 2P 30A | 5-DaHall1-PDU-01-30-30 | 5-DaHall1-PDU-02-30-30 | 220 | 30 | 01 | 30 | 220 | 30 | 02 | 30 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-P21 |  |  | 1A-3-11 | 1B-3-11 | U5-1A-32 / 2P 30A | U5-1B-32 / 2P 30A | 5-DaHall1-PDU-01-30-32 | 5-DaHall1-PDU-02-30-32 | 220 | 30 | 01 | 32 | 220 | 30 | 02 | 32 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-P22 |  |  | 1A-3-12 | 1B-3-12 | U5-1A-34 / 2P 30A | U5-1B-34 / 2P 30A | 5-DaHall1-PDU-01-30-34 | 5-DaHall1-PDU-02-30-34 | 220 | 30 | 01 | 34 | 220 | 30 | 02 | 34 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-P23 |  |  | 1A-3-13 | 1B-3-13 | U5-1A-36 / 2P 30A | U5-1B-36 / 2P 30A | 5-DaHall1-PDU-01-30-36 | 5-DaHall1-PDU-02-30-36 | 220 | 30 | 01 | 36 | 220 | 30 | 02 | 36 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-P24 |  |  | 1A-3-14 | 1B-3-14 | U5-1A-38 / 2P 30A | U5-1B-38 / 2P 30A | 5-DaHall1-PDU-01-30-38 | 5-DaHall1-PDU-02-30-38 | 220 | 30 | 01 | 38 | 220 | 30 | 02 | 38 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 번호없음 |  |  |  | 1B-3-15 |  | U5-1B-40 / 2P 30A |  | 5-DaHall1-PDU-02-30-40 |  |  |  |  | 220 | 30 | 02 | 40 | [7 empty] | 0 | 0 |  | 0 | 0 | 미구축
| 5F-Q20 |  |  | 1A-2-10 | 1B-2-10 | U5-1A-49 / 2P 30A | U5-1B-49 / 2P 30A | 5-DaHall1-PDU-01-30-49 | 5-DaHall1-PDU-02-30-49 | 220 | 30 | 01 | 49 | 220 | 30 | 02 | 49 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0
| 5F-Q21 |  |  | 1A-2-11 | 1B-2-11 | U5-1A-02 / 2P 30A | U5-1B-02 / 2P 30A | 5-DaHall1-PDU-01-30-2 | 5-DaHall1-PDU-02-30-2 | 220 | 30 | 01 | 2 | 220 | 30 | 02 | 2 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-Q24 |  |  | 1A-2-14 | 1B-2-14 | U5-1A-08 / 2P 30A | U5-1B-08 / 2P 30A | 5-DaHall1-PDU-01-30-8 | 5-DaHall1-PDU-02-30-8 | 220 | 30 | 01 | 8 | 220 | 30 | 02 | 8 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5F-R24 |  |  | 1A-1-14 | 1B-1-14 | U5-1A-27 / 2P 30A | U5-1B-27 / 2P 30A | 5-DaHall1-PDU-01-30-27 | 5-DaHall1-PDU-02-30-27 | 220 | 30 | 01 | 27 | 220 | 30 | 02 | 27 | U5-1A 4P 300A | U5-1B 4P 300A | LV-5A #01 3P 320A | LV-5B #01 3P 320A | TR-5A 1000KVA | TR-5B 1000KVA | 0 | 0 | 0 | 0 | 0 | 0
| 번호없음 |  |  | 1A-1-15 | 1B-1-15 | U5-1A-29 / 2P 30A | U5-1B-29 / 2P 30A | 5-DaHall1-PDU-01-30-29 | 5-DaHall1-PDU-02-30-29 | 220 | 30 | 01 | 29 | 220 | 30 | 02 | 29 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | OFF
[7 empty] | PDU(B)-2-32 / 3P 20A |  | 5-DaHall1-PDU-14-20-32 |  |  |  |  | 220 | 20 | 14 | 32 |  | PDU(B)-2 4P 150A |  | UPS출력 배전반(B), #04 3P 150A |  | TR-5B 1000KVA |  | 0.00020998 | 0.00020998 |  | 0 | 0
| pacnet 내 분전반2식 | 싱텔 분전반(A) | 22 | - | - | - | - |  |  |  |  | - | - |  |  | - | - | PDU-08-A 4P 200A |  | UPS출력 배전반(A), #08 3P 200A |  | TR-5A 1000KVA |  | 26.6021 |  | 26.6021 |  |  |  | 싱텔 분전반 메인전류 계측값
|  | 싱텔 분전반(B) |  | - | - | - | - |  |  |  |  | - | - |  |  | - | - |  | PDU-08-B 4P 200A |  | UPS출력 배전반(B), #08 3P 200A |  | TR-5B 1000KVA |  | 20.7587 | 20.7587
| 싱텔 | 싱텔 SKB CWDM |  | 싱텔 SKB CWDM A전원 | 싱텔 SKB CWDM B전원 | PDU(A)-3-13 / 2P 30A | PDU(B)-3-13 / 2P 30A | 5-DaHall1-PDU-15-30-13 | 5-DaHall1-PDU-16-30-13 | 220 | 30 | 15 | 13 | 220 | 30 | 16 | 13 | PDU(A)-3 4P 300A | PDU(B)-3 4P 300A | UPS출력 배전반(A), #01 3P 300A | UPS출력 배전반(B), #01, 3P 300A | TR-5A 1000KVA | TR-5B 1000KVA | 0.65398 | 1.3404 | 1.9944 | 92.7 | 251.9 | 344.6
|  | single-2 |  | PUD(A)-2-21 |  | PDU(A)-3-23 / 2P 20A |  | 5-DaHall1-PDU-15-20-23 |  | 220 | 20 | 15 | 23 | [10 empty] | 2.246 |  | 2.246 | 350.8 |  | 350.8
|  | single-2 |  | PUD(A)-2-27 |  | PDU(A)-3-29 / 2P 20A |  | 5-DaHall1-PDU-15-20-29 |  | 220 | 20 | 15 | 29 | [10 empty] | 0.44294 |  | 0.44294 | 22.1 |  | 22.1
|  | KT Rack #2 (소형 임시정류기) |  |  | KT Rack #2 (소형 임시정류기) |  | PDU(B)-3-15 / 2P 20A |  | 5-DaHall1-PDU-16-20-15 |  |  |  |  | 220 | 20 | 16 | 15 |  | PDU(B)-3 4P 300A |  | UPS출력 배전반(B), #01 3P 300A |  | TR-5B 1000KVA |  | 2.3945 | 2.3945 |  | 379.3 | 379.3
|  | KT Rack #3 (소형 임시정류기) |  |  | KT Rack #3 (소형 임시정류기) |  | PDU(B)-3-17 / 2P 20A |  | 5-DaHall1-PDU-16-20-17 |  |  |  |  | 220 | 20 | 16 | 17 | [7 empty] | 1.5462 | 1.5462 |  | 241.4 | 241.4
|  | KT Rack #4 (소형 임시정류기) |  |  | KT Rack #4 (소형 임시정류기) |  | PDU(B)-3-19 / 2P 20A |  | 5-DaHall1-PDU-16-20-19 |  |  |  |  | 220 | 20 | 16 | 19 | [7 empty] | 4.52 | 4.52 |  | 0 | 0
|  | single-2 |  |  | DACOM EOS |  | PDU(B)-3-23 / 2P 20A |  | 5-DaHall1-PDU-16-20-23 |  |  |  |  | 220 | 20 | 16 | 23 | [7 empty] | 0 | 0 |  | 0 | 0
|  | single-2 |  |  |  |  | PDU(B)-3-25 / 2P 20A |  | 5-DaHall1-PDU-16-20-25 |  |  |  |  | 220 | 20 | 16 | 25 | [7 empty] | 0.46351 | 0.46351 |  | 57.3 | 57.3
|  | single-2 |  |  | SKB2.5G전용 PDU B3 27 |  | PDU(B)-3-27 / 2P 20A |  | 5-DaHall1-PDU-16-20-27 |  |  |  |  | 220 | 20 | 16 | 27 | [7 empty] | 1.4893 | 1.4893 |  | 224.4 | 224.4
|  | single-2 |  |  | 데이콤 AC전원 |  | PDU(B)-3-29 / 2P 20A |  | 5-DaHall1-PDU-16-20-29 |  |  |  |  | 220 | 20 | 16 | 29 | [7 empty] | 1.7927 | 1.7927 |  | 338.3 | 338.3
|  | single-2 |  |  | kt mspp 전원 |  | PDU(B)-3-24 / 2P 20A |  | 5-DaHall1-PDU-16-20-24 |  |  |  |  | 220 | 20 | 16 | 24 | [7 empty] | 1.4455 | 1.4455 |  | 215.8 | 215.8
|  | single-2 |  |  | TNSI A |  | PDU(B)-3-30 / 2P 20A |  | 5-DaHall1-PDU-16-20-30 |  |  |  |  | 220 | 20 | 16 | 30 | [7 empty] | 0.49895 | 0.49895 |  | 40.7 | 40.7 |  |  | 0.4656
| 텔스트라 | Telstra | 80 | C2C 정류기 B1 | C2C 정류기 A1 | - | - |  |  |  |  | - | - | 380 |  | - | - | - | - | UPS출력 배전반(A), #12 3P 100A | UPS출력 배전반(B), #12 3P 100A | TR-5A 1000KVA | TR-5B 1000KVA | 26 | 36.8 | 62.8 |  |  |  | 별도 측정 필요
|  | Telstra |  | C2C 정류기 B2 | C2C 정류기 A2 | - | - |  |  |  |  | - | - | 380 |  | - | - | - | - | UPS출력 배전반(A), #11 3P 100A | UPS출력 배전반(B), #11 3P 100A |  |  | 34.7 | 30.8 | 65.5 |  |  |  | 별도 측정 필요
|  | Telstra |  | AC PDU-3#A |  | PDU(A)-3-01(3상) / 3P 50A |  | 5-DaHall1-PDU-15-50-1 |  | 380 | 50 | 15 | 1 |  |  |  |  | PDU(A)-3 4P 300A |  | UPS출력 배전반(A), #01 3P 300A |  |  |  | 15.2537 |  | 23.2586 | 2154.5 |  | 2154.5
|  | Telstra |  | AC PDU(A)-3A |  | PDU(A)-3-02(3상) / 3P 50A |  | 5-DaHall1-PDU-15-50-2 |  | 380 | 50 | 15 | 2 | [10 empty] | 8.0049 |  |  | 1255.7 |  | 1255.7
|  | Telstra |  |  | AC PDU-3#B |  | PDU(B)-3-01(3상) / 3P 50A |  | 5-DaHall1-PDU-16-50-1 |  |  |  |  | 380 | 50 | 16 | 1 |  | PDU(B)-3 4P 300A |  | UPS출력 배전반(B), #01 3P 300A |  |  |  | 12.1488 | 20.0777 |  | 1630.1 | 1630.1
|  | Telstra |  |  | PDU(B)-3A |  | PDU(B)-3-02(3상) / 3P 50A |  | 5-DaHall1-PDU-16-50-2 |  |  |  |  | 380 | 50 | 16 | 2 | [7 empty] | 7.9289 |  |  | 1246.9 | 1246.9
|  | Telstra | [6 empty] | 5-DaHall1-PDU-16-20-21 |  |  |  |  | 220 | 20 | 16 | 21 | [7 empty] | 0.96691 | 0.96691 |  | 40 |  |  |  | 3.4102
| 신규 BMS(4F TPS실) Rack |  | 2.2 | [5 empty] | 5-DaHall1-PDU-16-50-20 | 220 |  |  |  | 220 | 50 | 16 | 20 | [7 empty] | 0.68925 | 0.68925 |  | 78.1 | 78.1
| 신규 BMS(5F TPS실) Rack |  | 2.2 | [5 empty] | 5-DaHall1-PDU-16-50-22 | 220 |  |  |  | 220 | 50 | 16 | 22 | [7 empty] | 0.84193 | 0.84193 |  | 77.7 | 77.7
[25 empty] | 합 계 | 865.3915 | #N/A | #N/A
[25 empty] | 오차 | #REF!

## 4층_랙별_계통 및_부하량
4층 랙별 전기공급계통
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | =AC5:AC233
열 구분 (부스바명) | DEKR No. | 고객명 | 계약용량 | 세종 관리 Name (IDC 관리명). | 차단기 정보 |  | DEK Naming Convention 적용 명칭(NEW) |  | DEK차단기 정보수정 | [7 empty] | 분전반 정보 |  | 배전반 정보 |  | TR 정보 |  | 월 평균 전류 |  |  | 월 유효전력량 |  | 월간 사용전력량[kWh] | 비 고
|  |  | kW |  | 상 | 하 | 상 | 하 | 상 |  |  |  | 하 |  |  |  | 상 | 하 | 상 | 하 | 상 | 하 | 상 | 하 | 합계 | 상 | 하 |  |  | 합계
정류기 | 4-Sejong-Rect-1 | Sejong Telecom Inc. | 4 | 정류기1호기 | KEN 1 #01 / 4P 100A |  | 4-DaHall 1-PDU-02-100-1 |  | 380 | 100 | 02 | 1 |  |  |  |  | KEN 1 4P 300A |  | LV-4B #01 (3P 320A) |  | TR-4B (1000kVA) |  | 2.6386 |  | 2.6386 | 259.5 |  | 259.5 |  | 2.3 | 0.3386 | -255.5 | -255.5
| 4-Sejong-Rect-2 | Sejong Telecom Inc. | 4 | 정류기2호기 |  | KEN 8 #01 / 4P 100A |  | 4-DaHall 1-PDU-01-100-1 |  |  |  |  | 380 | 100 | 01 | 1 |  | KEN 8 4P 300A |  | LV-4A #01 (3P 320A) |  | TR-4A (1000kVA) |  | 3.7415 | 3.7415 |  | 395.8 | 395.8 |  | 3.2 | 0.5415 | -391.8 | -391.8
항온항습기 |  | CRAC 4E-1호기(20RT) |  | CRAC 4E-1호기(20RT) | KEN 7 #02 / 4P 200A |  | 4-DaHall 1-PDU-10-200-2 |  | 380 | 200 | 10 | 2 |  |  |  |  | KEN 7 4P 300A |  | LV-4B #05 (3P 320A) |  | TR-4B (1000kVA) |  | 88.0199 |  | 88.0199 | 12636.4 |  | 12636.4 |  | 83.5 | 4.5199 | -12636.4 | -12636.4
|  | CRAC 4E-2호기(20RT) |  | CRAC 4E-2호기(20RT) | KEN 7 #03 / 4P 200A |  | 4-DaHall 1-PDU-10-200-3 |  | 380 | 200 | 10 | 3 | [10 empty] | 44.6424 |  | 44.6424 | 6598.3 |  | 6598.3 |  | 43.8 | 0.8424 | -6598.3 | -6598.3
101~111Bay /POP B열 | G4601-G4611 | Sejong Telecom Inc. | 17.6 | 세종인터넷 | KEN 1 #03 / 2P 100A | KEN 8 #03 / 2P 100A | 4-DaHall 1-PDU-02-100-3 | 4-DaHall 1-PDU-01-100-3 | 220 | 100 | 02 | 3 | 220 | 100 | 01 | 3 | KEN 1 4P 300A | KEN 8 4P 300A | LV-4B #01 (3P 320A) | LV-4A #01 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 32.4976 | 34.2678 | 66.7654 | 4940.3 | 5221.5 | 10161.8 | 세종 Core Room | 68.1 | -1.3346 | -10144.2 | -10144.2
201~211Bay /POP C열 | G4501-G4511 | Sejong Telecom Inc. | 17.6 | 세종인터넷 | KEN 1 #04 / 2P 100A | KEN 8 #04 / 2P 100A | 4-DaHall 1-PDU-02-100-4 | 4-DaHall 1-PDU-01-100-4 | 220 | 100 | 02 | 4 | 220 | 100 | 01 | 4 | [6 empty] | 36.0017 | 37.2639 | 73.2656 | 5372.7 | 5592.9 | 10965.6 |  | 74.1 | -0.83439 | -10948 | -10948
301~311Bay /POP D열 | G4401-G4411 | Sejong Telecom Inc. | 17.6 | 세종인터넷 | KEN 1 #05 / 2P 100A | KEN 8 #05 / 2P 100A | 4-DaHall 1-PDU-02-100-5 | 4-DaHall 1-PDU-01-100-5 | 220 | 100 | 02 | 5 | 220 | 100 | 01 | 5 | [6 empty] | 40.9562 | 41.4804 | 82.4365 | 6458.9 | 6510 | 12968.9 |  | 80.3 | 2.1365 | -12951.3 | -12951.3
401~411Bay /POP E열 | G4301-G4311 | Sejong Telecom Inc. | 17.6 | 세종인터넷 | KEN 1 #02 / 2P 100A | KEN 8 #02 / 2P 100A | 4-DaHall 1-PDU-02-100-2 | 4-DaHall 1-PDU-01-100-2 | 220 | 100 | 02 | 2 | 220 | 100 | 01 | 2 | [6 empty] | 35.2048 | 37.4998 | 72.7045 | 5349.7 | 5737.3 | 11087 |  | 73.6 | -0.89548 | -11069.4 | -11069.4
501~511Bay /POP F열 | G4201-G4211 | Sejong Telecom Inc. | 17.6 | 세종인터넷 | KEN 2 #02 / 2P 100A | KEN 9 #02 / 2P 100A | 4-DaHall 1-PDU-04-100-2 | 4-DaHall 1-PDU-03-100-2 | 220 | 100 | 04 | 2 | 220 | 100 | 03 | 2 | KEN 2 4P 300A | KEN 9 4P 300A | LV-4B #06 (3P 320A) | LV-4A #06 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 39.4635 | 32.2199 | 71.6834 | 6085.6 | 5018.1 | 11103.7 |  | 73.2 | -1.5166 | -11086.1 | -11086.1
601~611Bay /1구역 B열 | G4101-G4111 | Sejong Telecom Inc. | 17.6 | 세종인터넷 | KEN 2 #03 / 2P 100A | KEN 9 #03 / 2P 100A | 4-DaHall 1-PDU-04-100-3 | 4-DaHall 1-PDU-03-100-3 | 220 | 100 | 04 | 3 | 220 | 100 | 03 | 3 | [6 empty] | 28.2948 | 28.4408 | 56.7355 | 4413 | 4388 | 8801 |  | 57.5 | -0.76447 | -8783.4 | -8783.4
[29 empty] | 철거 ('21.10월) | 0 | 0 | 0
K 3-1 | G1101 | Media Player | 13.2 | 4F Cage2-R15 | KEN 6 #02 / 2P 100A | KEN 13 #02 / 2P 100A | 4-DaHall 1-PDU-08-100-2 | 4-DaHall 1-PDU-07-100-2 | 220 | 100 | 08 | 2 | 220 | 100 | 07 | 2 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 33.2791 | 33.5635 | 66.8426 | 5070.3 | 5139.6 | 10209.9 | 미디어꾼(구)윈텔) | 67.9 | -1.0574 | -10196.7 | -10196.7
| G1102 | Media Player |  | 4F Cage2-R16 | [25 empty] | 0 | 0 | 0
| G1103 | Media Player |  | 4F Cage2-R17 | [25 empty] | 0 | 0 | 0
| G1104 | Media Player |  | 4F Cage2-R18 | [25 empty] | 0 | 0 | 0
| G1105 | Media Player |  | 4F Cage2-R19 | [25 empty] | 0 | 0 | 0
| G1106 | Media Player |  | 4F Cage2-R20 | [25 empty] | 0 | 0 | 0
K 3-3 | G1201 | Media Player | 6.6 | 4F Cage2-R08 | KEN 6 #06 / 2P 100A | KEN 13 #06 / 2P 100A | 4-DaHall 1-PDU-08-100-6 | 4-DaHall 1-PDU-07-100-6 | 220 | 100 | 08 | 6 | 220 | 100 | 07 | 6 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 12.24 | 15.6783 | 27.9182 | 1671.9 | 2168.2 | 3840.1 | 미디어꾼(구)윈텔) | 28.2 | -0.28177 | -3833.5 | -3833.5
| G1202 | Media Player |  | 4F Cage2-R09 | [25 empty] | 0 | 0 | 0
| G1302 | Media Player |  | 4F Cage2-R02 | [25 empty] | 0 | 0 | 0
K 3-2 | G1203 | Media Player | 11 | 4F Cage2-R10 | KEN 6 #04 / 2P 100A | KEN 13 #04 / 2P 100A | 4-DaHall 1-PDU-08-100-4 | 4-DaHall 1-PDU-07-100-4 | 220 | 100 | 08 | 4 | 220 | 100 | 07 | 4 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 9.4718 | 10.3767 | 19.8485 | 1433.1 | 1512.3 | 2945.4 | 미디어꾼(구)윈텔) | 20.2 | -0.35148 | -2934.4 | -2934.4
| G1204 | Media Player |  | 4F Cage2-R11 | [25 empty] | 0 | 0 | 0
| G1205 | Media Player |  | 4F Cage2-R12 | [25 empty] | 0 | 0 | 0
| G1206 | Media Player |  | 4F Cage2-R13 | [25 empty] | 0 | 0 | 0
| G1207 | Media Player |  | 4F Cage2-R14 | [25 empty] | 0 | 0 | 0
K 3-4 | G1301 | Media Player | 13.2 | 4F Cage2-R01 | KEN 6 #08 / 2P 100A | KEN 13 #08 / 2P 100A | 4-DaHall 1-PDU-08-100-8 | 4-DaHall 1-PDU-07-100-8 | 220 | 100 | 08 | 8 | 220 | 100 | 07 | 8 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 27.0223 | 34.3054 | 61.3277 | 3914.5 | 5132.6 | 9047.1 | 미디어꾼(구)윈텔) | 61.3 | 0.027673 | -9033.9 | -9033.9
| G1303 | Media Player |  | 4F Cage2-R03 | [25 empty] | 0 | 0 | 0
| G1304 | Media Player |  | 4F Cage2-R04 | [25 empty] | 0 | 0 | 0
| G1305 | Media Player |  | 4F Cage2-R05 | [25 empty] | 0 | 0 | 0
| G1306 | Media Player |  | 4F Cage2-R06 | [25 empty] | 0 | 0 | 0
| G1307 | Media Player |  | 4F Cage2-R07 | [25 empty] | 0 | 0 | 0
K 2-4 | G2103 | Settle Bank Co., Ltd. | 8.8 | 4F Cage3-R16 | KEN 6 #07 / 2P 100A | KEN 13 #07 / 2P 100A | 4-DaHall 1-PDU-08-100-7 | 4-DaHall 1-PDU-07-100-7 | 220 | 100 | 08 | 7 | 220 | 100 | 07 | 7 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 13.0529 | 13.8234 | 26.8763 | 1749.5 | 1855.3 | 3604.8 | 세틀뱅크 | 27.4 | -0.52372 | -3596 | -3596
| G2104 | Settle Bank Co., Ltd. |  | 4F Cage3-R15 | [25 empty] | 0 | 0 | 0
| G2105 | Settle Bank Co., Ltd. |  | 4F Cage3-R14 | [25 empty] | 0 | 0 | 0
| G2106 | Settle Bank Co., Ltd. |  | 4F Cage3-R13 | [25 empty] | 0 | 0 | 0
K 2-2 | G2201 | Settle Bank Co., Ltd. | 6.6 | 4F Cage3-R12 | KEN 6 #03 / 2P 100A | KEN 13 #03 / 2P 100A | 4-DaHall 1-PDU-08-100-3 | 4-DaHall 1-PDU-07-100-3 | 220 | 100 | 08 | 3 | 220 | 100 | 07 | 3 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 5.4024 | 5.3006 | 10.703 | 798.7 | 776.2 | 1574.9 | 세틀뱅크 | 10.8 | -0.096979 | -1568.3 | -1568.3
| G2203 | Settle Bank Co., Ltd. |  | 4F Cage3-R10 | [25 empty] | 0 | 0 | 0
| G2205 | Settle Bank Co., Ltd. |  | 4F Cage3-R08 | [25 empty] | 0 | 0 | 0
K 2-3 | G2202 | Settle Bank Co., Ltd. | 6.6 | 4F Cage3-R11 | KEN 6 #05 / 2P 100A | KEN 13 #05 / 2P 100A | 4-DaHall 1-PDU-08-100-5 | 4-DaHall 1-PDU-07-100-5 | 220 | 100 | 08 | 5 | 220 | 100 | 07 | 5 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 7.4679 | 6.0186 | 13.4865 | 1102 | 864.2 | 1966.2 | 세틀뱅크 | 13.5 | -0.013458 | -1959.6 | -1959.6
| G2204 | Settle Bank Co., Ltd. |  | 4F Cage3-R09 | [25 empty] | 0 | 0 | 0
| G2206 | Settle Bank Co., Ltd. |  | 4F Cage3-R07 | [25 empty] | 0 | 0 | 0
K 2-1 | G2301 | Settle Bank Co., Ltd. | 13.2 | 4F Cage3-R06 | KEN 6 #01 / 2P 100A | KEN 13 #01 / 2P 100A | 4-DaHall 1-PDU-08-100-1 | 4-DaHall 1-PDU-07-100-1 | 220 | 100 | 08 | 1 | 220 | 100 | 07 | 1 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 22.6604 | 20.3838 | 43.0442 | 3423.9 | 3053.1 | 6477 | 세틀뱅크 | 44.2 | -1.1558 | -6463.8 | -6463.8
| G2302 | Settle Bank Co., Ltd. |  | 4F Cage3-R05 | [25 empty] | 0 | 0 | 0
| G2303 | Settle Bank Co., Ltd. |  | 4F Cage3-R04 | [25 empty] | 0 | 0 | 0
| G2304 | Settle Bank Co., Ltd. |  | 4F Cage3-R03 | [25 empty] | 0 | 0 | 0
| G2305 | Settle Bank Co., Ltd. |  | 4F Cage3-R02 | [25 empty] | 0 | 0 | 0
| G2306 | Settle Bank Co., Ltd. |  | 4F Cage3-R01 | [25 empty] | 0 | 0 | 0
K 1-2 |  |  |  |  | KEN 6 #10 / 2P 100A | KEN 13 #10 / 2P 100A | 4-DaHall 1-PDU-08-100-10 | 4-DaHall 1-PDU-07-100-10 | 220 | 100 | 08 | 10 | 220 | 100 | 07 | 10 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[30 empty] | 0 | 0 | 0
[30 empty] | 0 | 0 | 0
K 1-1 | G3201 |  |  |  | KEN 6 #09 / 2P 100A | KEN 13 #09 / 2P 100A | 4-DaHall 1-PDU-08-100-9 | 4-DaHall 1-PDU-07-100-9 | 220 | 100 | 08 | 9 | 220 | 100 | 07 | 9 | KEN 6 4P 300A | KEN 13 4P 300A | LV-4B #04 (3P 320A) | LV-4A #04 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 0 | 0 | 0 | 0 | 0 | 0 | Cage 1-1-02 & 03 (총 4회로) | 1.4 | -1.4 | 0 | 0
| G3202 | [27 empty] | Café 1-1-01 (2회로) | 0 | 0 | 0
[30 empty] | 0 | 0 | 0
[30 empty] | 0 | 0 | 0
[30 empty] | 0 | 0 | 0
[30 empty] | 0 | 0 | 0
[30 empty] | 0 | 0 | 0
[30 empty] | 0 | 0 | 0
3구역 S열 | B115 | Media Player | 20.9 | 4F-S20 | KEN 3 #10 / 2P 100A | KEN 10 #10 / 2P 100A | 4-DaHall 1-PDU-06-100-10 | 4-DaHall 1-PDU-05-100-10 | 220 | 100 | 06 | 10 | 220 | 100 | 05 | 10 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 39.6661 | 34.7027 | 74.3688 | 5991.4 | 5187.4 | 11178.8 |  | 70.2 | 4.1688 | -11157.9 | -11157.9
| B116 |  |  | 4F-S19 | [25 empty] | 0 | 0 | 0
| B117 | Suntech Solution |  | 4F-S18 | [25 empty] | 0 | 0 | 0
| B118 | Suntech Solution |  | 4F-S17 | [25 empty] | 0 | 0 | 0
| B119 | Suntech Solution |  | 4F-S16 | [25 empty] | 0 | 0 | 0
| B120 | Suntech Solution |  | 4F-S15 | [25 empty] | 0 | 0 | 0
| B121 | Suntech Solution |  | 4F-S14 | [25 empty] | 0 | 0 | 0
| B122 | Suntech Solution |  | 4F-S13 | [25 empty] | 0 | 0 | 0
| B123 | Suntech Solution |  | 4F-S12 | [25 empty] | 0 | 0 | 0
| B124 | Suntech Solution |  | 4F-S11 | [25 empty] | 0 | 0 | 0
3구역 R열 |  |  |  | 4F-R20 | KEN 3 #9 / 2P 100A | KEN 10 #9 / 2P 100A | 4-DaHall 1-PDU-06-100-9 | 4-DaHall 1-PDU-05-100-9 | 220 | 100 | 06 | 9 | 220 | 100 | 05 | 9 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  |  |  | 4F-R19 | [25 empty] | 0 | 0 | 0
|  |  |  | 4F-R18 | [25 empty] | 0 | 0 | 0
|  |  |  | 4F-R17 | [25 empty] | 0 | 0 | 0
|  |  |  | 4F-R16 | [25 empty] | 0 | 0 | 0
|  |  |  | 4F-R15 | [25 empty] | 0 | 0 | 0
|  |  |  | 4F-R14 | [25 empty] | 0 | 0 | 0
|  |  |  | 4F-R13 | [25 empty] | 0 | 0 | 0
|  |  |  | 4F-R12 | [25 empty] | 0 | 0 | 0
|  |  |  | 4F-R11 | [25 empty] | 0 | 0 | 0
3구역 Q열 | B315 |  | 15.4 | 4F-Q20 | KEN 3 #8 / 2P 100A | KEN 10 #8 / 2P 100A | 4-DaHall 1-PDU-06-100-8 | 4-DaHall 1-PDU-05-100-8 | 220 | 100 | 06 | 8 | 220 | 100 | 05 | 8 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 14.0982 | 11.8335 | 25.9316 | 2039.9 | 1704.6 | 3744.5 |  | 26 | -0.068369 | -3729.1 | -3729.1
| B316 | Suntech Solution |  | 4F-Q19 | [25 empty] | 0 | 0 | 0
| B317 | Suntech Solution |  | 4F-Q18 | [25 empty] | 0 | 0 | 0
| B318 |  |  | 4F-Q17 | [25 empty] | 0 | 0 | 0
| B319 |  |  | 4F-Q16 | [25 empty] | 0 | 0 | 0
| B320 |  |  | 4F-Q15 | [25 empty] | 0 | 0 | 0
| B321 | Sysone Co., Ltd. |  | 4F-Q14 | [25 empty] | 0 | 0 | 0
| B322 | Sysone Co., Ltd. |  | 4F-Q13 | [25 empty] | 0 | 0 | 0
| B323 | Sysone Co., Ltd. |  | 4F-Q12 | [25 empty] | 0 | 0 | 0
| B324 | Digital Edge Korea |  | 4F-Q11 | [25 empty] | 0 | 0 | 0
3구역 P열 | B415 |  | 7.2 | 4F-P20 | KEN 3 #7 / 2P 100A | KEN 10 #7 / 2P 100A | 4-DaHall 1-PDU-06-100-7 | 4-DaHall 1-PDU-05-100-7 | 220 | 100 | 06 | 7 | 220 | 100 | 05 | 7 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 8.3674 | 6.5082 | 14.8755 | 1189.4 | 900.5 | 2089.9 |  | 15.7 | -0.82446 | -2082.7 | -2082.7
| B416 |  |  | 4F-P19 | [25 empty] | 0 | 0 | 0
| B417 |  |  | 4F-P18 | [25 empty] | 0 | 0 | 0
| B418 | Sejong Telecom Inc. |  | 4F-P17 | [25 empty] | 0 | 0 | 0
| B419 | Sejong Telecom Inc. |  | 4F-P16 | [25 empty] | 0 | 0 | 0
| B420 | Digital Edge Korea |  | 4F-P15 | [25 empty] | 0 | 0 | 0
| B421 |  |  | 4F-P14 | [25 empty] | 0 | 0 | 0
| B422 | Digital Edge Korea |  | 4F-P13 | [25 empty] | 0 | 0 | 0
| B423 |  |  | 4F-P12 | [25 empty] | 0 | 0 | 0
| B424 |  |  | 4F-P11 | [25 empty] | 0 | 0 | 0
3구역 O열 |  |  | 11.6 |  | KEN 3 #6 / 2P 100A | KEN 10 #6 / 2P 100A | 4-DaHall 1-PDU-06-100-6 | 4-DaHall 1-PDU-05-100-6 | 220 | 100 | 06 | 6 | 220 | 100 | 05 | 6 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 0 | 12.8628 | 12.8628 | 0 | 1714 | 1714 | O #01 | 36.3 | -23.4372 | -1702.4 | -1702.4
[29 empty] | O #03 | 0 | 0 | 0
| B515 |  |  | 4F-O20 | [25 empty] | 0 | 0 | 0
| B516 | Ellis Information Technology Co., Ltd. |  | 4F-O19 | [25 empty] | 0 | 0 | 0
| B517 | SCG Lab |  | 4F-O18 | [25 empty] | 0 | 0 | 0
| B518 | Netoz Co., Ltd. |  | 4F-O17 | [25 empty] | 0 | 0 | 0
| B519 | Hi Auto Club Co., Ltd. |  | 4F-O16 | [25 empty] | 0 | 0 | 0
| B520 |  |  | 4F-O15 | [25 empty] | 0 | 0 | 0
| B521 |  |  | 4F-O14 | [25 empty] | 0 | 0 | 0
| B522 | Hi Auto Club Co., Ltd. |  | 4F-O13 | [25 empty] | 0 | 0 | 0
| B523 | Daerim I&T |  | 4F-O12 | [25 empty] | 0 | 0 | 0
| B524 | Oriental Moon Co., Ltd. |  | 4F-O11 | [25 empty] | 0 | 0 | 0
3구역 Z열 |  |  |  | 4F-Z11 | KEN 3 #5 / 2P 100A | KEN 10 #5 / 2P 100A | 4-DaHall 1-PDU-06-100-5 | 4-DaHall 1-PDU-05-100-5 | 220 | 100 | 06 | 5 | 220 | 100 | 05 | 5 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 0 | 0 | 0 | 0 | 0 | 0 | spare | 35.5 | -35.5 | 0 | 0
|  |  |  | 4F-Z12 | [24 empty] | spare | 0 | 0 | 0
|  |  |  | 4F-Z13 | [24 empty] | spare | 0 | 0 | 0
|  |  |  | 4F-Z14 | [24 empty] | spare | 0 | 0 | 0
[29 empty] | N #02 | 0 | 0 | 0
[29 empty] | N #04 & N #05 | 0 | 0 | 0
[29 empty] | N #01 & N #03 | 0 | 0 | 0
[29 empty] | N #06 | 0 | 0 | 0
2구역 M열 | C101 |  | 6.6 | 4F-N11 | KEN 3 #04 / 2P 100A | KEN 10 #04 / 2P 100A | 4-DaHall 1-PDU-06-100-4 | 4-DaHall 1-PDU-05-100-4 | 220 | 100 | 06 | 4 | 220 | 100 | 05 | 4 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 6.9284 | 7.2205 | 14.1489 | 997.4 | 1036.8 | 2034.2 | 미설치 | 14.5 | -0.35109 | -2027.6 | -2027.6
| C102 |  |  | 4F-N12 | [24 empty] | 미설치 | 0 | 0 | 0
| C103 |  |  | 4F-N13 | [24 empty] | 미설치 | 0 | 0 | 0
| C104 |  |  | 4F-N14 | [25 empty] | 0 | 0 | 0
| C105 |  |  | 4F-N15 | [25 empty] | 0 | 0 | 0
| C106 | Sysone Co., Ltd. |  | 4F-N16 | [25 empty] | 0 | 0 | 0
| C107 |  |  | 4F-N17 | [25 empty] | 0 | 0 | 0
| C108 | Sysone Co., Ltd. |  | 4F-N18 | [25 empty] | 0 | 0 | 0
| C109 | Sysone Co., Ltd. |  | 4F-N19 | [25 empty] | 0 | 0 | 0
| C110 |  |  | 4F-N20 | [24 empty] | 미설치 | 0 | 0 | 0
| C111 |  |  | 4F-N21 | [24 empty] | 미설치 | 0 | 0 | 0
2구역 L열 | C201 | Digital Edge Korea | 5.5 | 4F-M11 | KEN 3 #03 / 2P 100A | KEN 10 #03 / 2P 100A | 4-DaHall 1-PDU-06-100-3 | 4-DaHall 1-PDU-05-100-3 | 220 | 100 | 06 | 3 | 220 | 100 | 05 | 3 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 8.9534 | 7.7355 | 16.6889 | 1352.4 | 1114.9 | 2467.3 |  | 17.4 | -0.71114 | -2461.8 | -2461.8
| C202 |  |  | 4F-M12 | [25 empty] | 0 | 0 | 0
| C203 | Singapore Telecom Korea Limited |  | 4F-M13 | [25 empty] | 0 | 0 | 0
| C204 | Singapore Telecom Korea Limited |  | 4F-M14 | [25 empty] | 0 | 0 | 0
| C205 |  |  | 4F-M15 | [25 empty] | 0 | 0 | 0
| C206 | Singapore Telecom Korea Limited |  | 4F-M16 | [25 empty] | 0 | 0 | 0
| C207 |  |  | 4F-M17 | [25 empty] | 0 | 0 | 0
| C208 |  |  | 4F-M18 | [25 empty] | 0 | 0 | 0
| C209 |  |  | 4F-M19 | [25 empty] | 0 | 0 | 0
| C210 |  |  | 4F-M20 | [25 empty] | 0 | 0 | 0
| C211 |  |  | 4F-M21 | [25 empty] | 0 | 0 | 0
2구역 K열 | C301 |  |  | 4F-L11 | KEN 3 #02 / 2P 100A | KEN 10 #02 / 2P 100A | 4-DaHall 1-PDU-06-100-2 | 4-DaHall 1-PDU-05-100-2 | 220 | 100 | 06 | 2 | 220 | 100 | 05 | 2 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| C302 |  |  | 4F-L12 | [25 empty] | 0 | 0 | 0
| C303 |  |  | 4F-L13 | [25 empty] | 0 | 0 | 0
| C304 |  |  | 4F-L14 | [25 empty] | 0 | 0 | 0
| C305 |  |  | 4F-L15 | [25 empty] | 0 | 0 | 0
| C306 |  |  | 4F-L16 | [25 empty] | 0 | 0 | 0
| C307 |  |  | 4F-L17 | [25 empty] | 0 | 0 | 0
| C308 |  |  | 4F-L18 | [25 empty] | 0 | 0 | 0
| C309 |  |  | 4F-L19 | [25 empty] | 0 | 0 | 0
| C310 |  |  | 4F-L20 | [25 empty] | 0 | 0 | 0
2구역 J열 | C401 |  | 5 | 4F-K11 | KEN 3 #01 / 2P 100A | KEN 10 #01 / 2P 100A | 4-DaHall 1-PDU-06-100-1 | 4-DaHall 1-PDU-05-100-1 | 220 | 100 | 06 | 1 | 220 | 100 | 05 | 1 | KEN 3 4P 300A | KEN 10 4P 300A | LV-4B #03 (3P 320A) | LV-4A #03 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 10.6138 | 8.9695 | 19.5834 | 1605.2 | 1363.3 | 2968.5 |  | 20 | -0.41664 | -2963.5 | -2963.5
| C402 |  |  | 4F-K12 | [25 empty] | 0 | 0 | 0
| C403 |  |  | 4F-K13 | [25 empty] | 0 | 0 | 0
| C404 | CASTIS CO.,LTD. |  | 4F-K14 | [25 empty] | 0 | 0 | 0
| C405 | Sysone Co., Ltd. |  | 4F-K15 | [25 empty] | 0 | 0 | 0
| C406 |  |  | 4F-K16 | [25 empty] | 0 | 0 | 0
| C407 | TNC Technology |  | 4F-K17 | [25 empty] | 0 | 0 | 0
| C408 |  |  | 4F-K18 | [25 empty] | 0 | 0 | 0
| C409 |  |  | 4F-K19 | [25 empty] | 0 | 0 | 0
| C410 |  |  | 4F-K20 | [25 empty] | 0 | 0 | 0
2구역 I열 | C501 | Digital Edge Korea | 6.1 | 4F-J11 | KEN 1 #06 / 2P 100A | KEN 8 #06 | 4-DaHall 1-PDU-02-100-6 | 4-DaHall 1-PDU-01-100-6 | 220 | 100 | 02 | 6 | 220 | 100 | 01 | 6 | KEN 1 4P 300A | KEN 8 4P 300A | LV-4B #01 (3P 320A) | LV-4A #01 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 12.3198 | 23.5345 | 35.8543 | 1792.3 | 3450.2 | 5242.5 |  | 37.1 | -1.2457 | -5236.4 | -5236.4
| C502 |  |  | 4F-J12 | [25 empty] | 0 | 0 | 0
| C503 | Plus Eye Co., Ltd. |  | 4F-J13 | [25 empty] | 0 | 0 | 0
| C504 |  |  | 4F-J14 | [25 empty] | 0 | 0 | 0
| C505 |  |  | 4F-J15 | [25 empty] | 0 | 0 | 0
| C506 | Hecto Financial Co., Ltd. |  | 4F-J16 | [25 empty] | 0 | 0 | 0
| C507 | Hecto Financial Co., Ltd. |  | 4F-J17 | [25 empty] | 0 | 0 | 0
| C508 |  |  | 4F-J18 | [25 empty] | 0 | 0 | 0
| C509 | BS Printech |  | 4F-J19 | [25 empty] | 0 | 0 | 0
| C510 |  |  | 4F-J20 | [25 empty] | 0 | 0 | 0
1구역 H열 | C601 | Jongro Hakpyung | 18.7 | 4F-H11 | KEN 1 #07 / 2P 100A | KEN 8 #07 / 2P 100A | 4-DaHall 1-PDU-02-100-7 | 4-DaHall 1-PDU-01-100-7 | 220 | 100 | 02 | 7 | 220 | 100 | 01 | 7 | KEN 1 4P 300A | KEN 8 4P 300A | LV-4B #01 (3P 320A) | LV-4A #01 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 28.991 | 12.608 | 41.599 | 4320.9 | 1781.8 | 6102.7 |  | 40.7 | 0.89902 | -6084 | -6084
| C602 |  |  | 4F-H12 | [24 empty] | 22/05/01 해지 | 0 | 0 | 0
| C603 | Jongro Hakpyung |  | 4F-H13 | [25 empty] | 0 | 0 | 0
| C604 | JS Data Systems Korea |  | 4F-H14 | [25 empty] | 0 | 0 | 0
| C605 | Settle Bank Co., Ltd. |  | 4F-H15 | [25 empty] | 0 | 0 | 0
| C606 | Settle Bank Co., Ltd. |  | 4F-H16 | [25 empty] | 0 | 0 | 0
| C607 | JS Data Systems Korea |  | 4F-H17 | [25 empty] | 0 | 0 | 0
| C608 | Settle Bank Co., Ltd. |  | 4F-H18 | [25 empty] | 0 | 0 | 0
| C609 | Settle Bank Co., Ltd. |  | 4F-H19 | [25 empty] | 0 | 0 | 0
| C610 |  |  | 4F-H20 | [25 empty] | 0 | 0 | 0
| C611 | CoinNet |  | 4F-H21 | [25 empty] | 0 | 0 | 0
1구역 G열 | C701 | Winnet System Co., Ltd. | 13.8 | 4F-G11 | KEN 2 #08 / 2P 100A | KEN 9 #08 / 2P 100A | 4-DaHall 1-PDU-04-100-8 | 4-DaHall 1-PDU-03-100-8 | 220 | 100 | 04 | 8 | 220 | 100 | 03 | 8 | KEN 2 4P 300A | KEN 9 4P 300A | LV-4B #06 (3P 320A) | LV-4A #06 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 22.3842 | 18.5092 | 40.8934 | 3222.8 | 2609.3 | 5832.1 |  | 39 | 1.8934 | -5818.3 | -5818.3
| C702 |  |  | 4F-G12 | [25 empty] | 0 | 0 | 0
| C703 |  |  | 4F-G13 | [25 empty] | 0 | 0 | 0
| C704 | Sysone Co., Ltd. |  | 4F-G14 | [25 empty] | 0 | 0 | 0
| C705 | JS Data Systems Korea |  | 4F-G15 | [25 empty] | 0 | 0 | 0
| C706 | Digital Edge Korea |  | 4F-G16 | [25 empty] | 0 | 0 | 0
| C707 |  |  | 4F-G17 | [25 empty] | 0 | 0 | 0
| C708 | Sysone Co., Ltd. |  | 4F-G18 | [25 empty] | 0 | 0 | 0
| C709 | Settle Bank Co., Ltd. |  | 4F-G19 | [25 empty] | 0 | 0 | 0
| C710 | Settle Bank Co., Ltd. |  | 4F-G20 | [25 empty] | 0 | 0 | 0
| C711 | Settle Bank Co., Ltd. |  | 4F-G21 | [25 empty] | 0 | 0 | 0
| C712 |  |  | 4F-G22 | [25 empty] | 0 | 0 | 0
1구역 F열 | C801 | Digital Edge Korea | 17.6 | 4F-F11 | KEN 2 #07 / 2P 100A | KEN 9 #07 / 2P 100A | 4-DaHall 1-PDU-04-100-7 | 4-DaHall 1-PDU-03-100-7 | 220 | 100 | 04 | 7 | 220 | 100 | 03 | 7 | KEN 2 4P 300A | KEN 9 4P 300A | LV-4B #06 (3P 320A) | LV-4A #06 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 22.2232 | 28.4161 | 50.6393 | 3190.4 | 4199 | 7389.4 |  | 49.6 | 1.0393 | -7371.8 | -7371.8
| C802 | ANEXIA |  | 4F-F12 | [25 empty] | 0 | 0 | 0
| C803 |  |  | 4F-F13 | [25 empty] | 0 | 0 | 0
| C804 |  |  | 4F-F14 | [25 empty] | 0 | 0 | 0
| C805 |  |  | 4F-F15 | [25 empty] | 0 | 0 | 0
| C806 | Settle Bank Co., Ltd. |  | 4F-F16 | [25 empty] | 0 | 0 | 0
| C807 | Settle Bank Co., Ltd. |  | 4F-F17 | [25 empty] | 0 | 0 | 0
| C808 | Settle Bank Co., Ltd. |  | 4F-F18 | [25 empty] | 0 | 0 | 0
| C809 | Settle Bank Co., Ltd. |  | 4F-F19 | [25 empty] | 0 | 0 | 0
| C810 | Settle Bank Co., Ltd. |  | 4F-F20 | [25 empty] | 0 | 0 | 0
| C811 |  |  | 4F-F21 | [25 empty] | 0 | 0 | 0
| C812 | Shoot |  | 4F-F22 | [25 empty] | 0 | 0 | 0
1구역 E열 | C901 |  | 4.4 | 4F-E11 | KEN 2 #06 / 2P 100A | KEN 9 #06 / 2P 100A | 4-DaHall 1-PDU-04-100-6 | 4-DaHall 1-PDU-03-100-6 | 220 | 100 | 04 | 6 | 220 | 100 | 03 | 6 | KEN 2 4P 300A | KEN 9 4P 300A | LV-4B #06 (3P 320A) | LV-4A #06 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 14.5532 | 10.3842 | 24.9373 | 2230.9 | 1507.6 | 3738.5 |  | 25 | -0.062666 | -3734.1 | -3734.1
| C902 | MS Information Communication Co., Ltd. |  | 4F-E12 | [25 empty] | 0 | 0 | 0
| C903 |  |  | 4F-E13 | [25 empty] | 0 | 0 | 0
| C904 | Kyungdong Corporation |  | 4F-E14 | [25 empty] | 0 | 0 | 0
| C905 | Kyungdong Corporation |  | 4F-E15 | [25 empty] | 0 | 0 | 0
| C906 |  |  | 4F-E16 | [25 empty] | 0 | 0 | 0
| C907 |  |  | 4F-E17 | [25 empty] | 0 | 0 | 0
| C908 |  |  | 4F-E18 | [25 empty] | 0 | 0 | 0
| C909 |  |  | 4F-E19 | [25 empty] | 0 | 0 | 0
| C910 |  |  | 4F-E20 | [25 empty] | 0 | 0 | 0
| C911 |  |  | 4F-E21 | [25 empty] | 0 | 0 | 0
| C912 | Wiz Communication Co., Ltd. |  | 4F-E22 | [25 empty] | 0 | 0 | 0
1구역 D열 | C1001 | Spark & ​​Associates Co., Ltd. | 3.3 | 4F-D11 | KEN 2 #05 / 2P 100A | KEN 9 #05 / 2P 100A | 4-DaHall 1-PDU-04-100-5 | 4-DaHall 1-PDU-03-100-5 | 220 | 100 | 04 | 5 | 220 | 100 | 03 | 5 | KEN 2 4P 300A | KEN 9 4P 300A | LV-4B #06 (3P 320A) | LV-4A #06 (3P 320A) | TR-4B (1000kVA) | TR-4A (1000kVA) | 9.6382 | 6.3018 | 15.94 | 1447.4 | 964.3 | 2411.7 |  | 16.2 | -0.26005 | -2408.4 | -2408.4
| C1002 |  |  | 4F-D12 | [25 empty] | 0 | 0 | 0
| C1003 |  |  | 4F-D13 | [25 empty] | 0 | 0 | 0
| C1004 |  |  | 4F-D14 | [25 empty] | 0 | 0 | 0
| C1005 |  |  | 4F-D15 | [25 empty] | 0 | 0 | 0
| C1006 |  |  | 4F-D16 | [25 empty] | 0 | 0 | 0
| C1007 |  |  | 4F-D17 | [25 empty] | 0 | 0 | 0
| C1008 | Sejong Telecom Inc. |  | 4F-D18 | [25 empty] | 0 | 0 | 0
| C1009 |  |  | 4F-D19 | [25 empty] | 0 | 0 | 0
| C1010 |  |  | 4F-D20 | [25 empty] | 0 | 0 | 0
| C1011 |  |  | 4F-D21 | [25 empty] | 0 | 0 | 0
| C1012 |  |  | 4F-D22 | [25 empty] | 0 | 0 | 0
-56.6963
[25 empty] | 1088.3413 | 100.6587
[24 empty] | 오차 | #REF!
Note on A115: 이현상: 랙 배치도 참고하세요

## 4_7층_총_사용전력표
월간 사용전력량 | 개수: 1060 | =A2:A1062
259.5 | 4층
395.8
12636.4
6598.3
10161.8
10965.6
12968.9
11087
11103.7
8801
0
10209.9
0
0
0
0
0
3840.1
0
0
2945.4
0
0
0
0
9047.1
0
0
0
0
0
3604.8
0
0
0
1574.9
0
0
1966.2
0
0
6477
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
11178.8
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
3744.5
0
0
0
0
0
0
0
0
0
2089.9
0
0
0
0
0
0
0
0
0
1714
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
2034.2
0
0
0
0
0
0
0
0
0
0
2467.3
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
2968.5
0
0
0
0
0
0
0
0
0
5242.5
0
0
0
0
0
0
0
0
0
6102.7
0
0
0
0
0
0
0
0
0
0
5832.1
0
0
0
0
0
0
0
0
0
0
0
7389.4
0
0
0
0
0
0
0
0
0
0
0
3738.5
0
0
0
0
0
0
0
0
0
0
0
2411.7
0
0
0
0
0
0
0
0
0
0
0
0 | 5층
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0 | 6층
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0 | 7층
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## 각층분기별_유효전력량(전월)
Date : 2023-11-01 ~ 2023-11-30
4F | 포인트명 | kWh(전월유효전력량) | 5F | 포인트명 | kWh(전월유효전력량) | 6F | 포인트명 | kWh(전월유효전력량) | 7F | 포인트명 | kWh(전월유효전력량)
4-CRACRm-CEP-01 | 0119 [branch#01] [A] KWh last month | 0 | 5-CRACRm-CEP-01 | 0119 [branch#01] [A] KWh last month | 19.4 | 6-DaHall 1-CEP-05 | [branch#001] [A] kWh last month | 204.7 | 7-DaHall 1-PDU-01 | [branch#001] [A] kWh last month | 0
4-CRACRm-CEP-01 | 0279 [branch#02] [A] KWh last month | 13849.5 | 5-CRACRm-CEP-01 | 0279 [branch#02] [A] KWh last month | 13299.8 | 6-DaHall 1-CEP-05 | [branch#002] [A] kWh last month | 1.8 | 7-DaHall 1-PDU-01 | [branch#002] [A] kWh last month | 0
4-CRACRm-CEP-01 | 0439 [branch#03] [A] KWh last month | 11.9 | 5-CRACRm-CEP-01 | 0439 [branch#03] [A] KWh last month | 17.9 | 6-DaHall 1-CEP-05 | [branch#003] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#003] [A] kWh last month | 329.6
4-CRACRm-CEP-01 | 0599 [branch#04] [A] KWh last month | 7639.7 | 5-CRACRm-CEP-01 | 0599 [branch#04] [A] KWh last month | 13614.9 | 6-DaHall 1-CEP-05 | [branch#004] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#004] [A] kWh last month | 0
4-CRACRm-CEP-02 | 0119 [branch#01] [A] KWh last month | 15972.7 | 5-CRACRm-CEP-02 | 0119 [branch#01] [A] KWh last month | 4258.6 | 6-DaHall 1-CEP-05 | [branch#005] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#005] [A] kWh last month | 744.6
4-CRACRm-CEP-02 | 0279 [branch#02] [A] KWh last month | 18.9 | 5-CRACRm-CEP-02 | 0279 [branch#02] [A] KWh last month | 18.7 | 6-DaHall 1-CEP-05 | [branch#006] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#006] [A] kWh last month | 0
4-CRACRm-CEP-02 | 0439 [branch#03] [A] KWh last month | 13938.9 | 5-CRACRm-CEP-02 | 0439 [branch#03] [A] KWh last month | 25399.8 | 6-DaHall 1-CEP-05 | [branch#007] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#007] [A] kWh last month | 920.5
4-CRACRm-CEP-02 | 0599 [branch#04] [A] KWh last month | 16.3 | 5-CRACRm-CEP-02 | 0599 [branch#04] [A] KWh last month | 14.7 | 6-DaHall 1-CEP-05 | [branch#008] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#008] [A] kWh last month | 261.8
4-DaHall 1-CEP-05 | 0119 [branch#01] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#001] [A] kWh last month | 25.1 | 6-DaHall 1-CEP-05 | [branch#009] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#009] [A] kWh last month | 957.7
4-DaHall 1-CEP-05 | 0279 [branch#02] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#002] [A] kWh last month | 51.4 | 6-DaHall 1-CEP-05 | [branch#010] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#010] [A] kWh last month | 359.3
4-DaHall 1-CEP-05 | 0439 [branch#03] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#003] [A] kWh last month | 69.8 | 6-DaHall 1-CEP-05 | [branch#011] [A] kWh last month | 1777.9 | 7-DaHall 1-PDU-01 | [branch#011] [A] kWh last month | 963.8
4-DaHall 1-CEP-05 | 0599 [branch#04] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#004] [A] kWh last month | 8201.7 | 6-DaHall 1-CEP-05 | [branch#012] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#012] [A] kWh last month | 0
4-DaHall 1-CEP-05 | 0759 [branch#05] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#005] [A] kWh last month | 69.8 | 6-DaHall 1-CEP-05 | [branch#013] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#013] [A] kWh last month | 1006.3
4-DaHall 1-CEP-05 | 0919 [branch#06] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#006] [A] kWh last month | 8771.8 | 6-DaHall 1-CEP-05 | [branch#014] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#014] [A] kWh last month | 644.4
4-DaHall 1-CEP-05 | 1079 [branch#07] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#007] [A] kWh last month | 6667 | 6-DaHall 1-CEP-05 | [branch#015] [A] kWh last month | 1419 | 7-DaHall 1-PDU-01 | [branch#015] [A] kWh last month | 68.3
4-DaHall 1-CEP-05 | 1239 [branch#08] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#008] [A] kWh last month | 4809.7 | 6-DaHall 1-CEP-05 | [branch#016] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#016] [A] kWh last month | 320.2
4-DaHall 1-CEP-05 | 1399 [branch#09] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#009] [A] kWh last month | 69.4 | 6-DaHall 1-CEP-05 | [branch#017] [A] kWh last month | 881.5 | 7-DaHall 1-PDU-01 | [branch#017] [A] kWh last month | 426.6
4-DaHall 1-CEP-05 | 1559 [branch#10] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#010] [A] kWh last month | 69.9 | 6-DaHall 1-PDU-01 | [branch#001] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#018] [A] kWh last month | 265
4-DaHall 1-CEP-05 | 1719 [branch#11] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#011] [A] kWh last month | 69.3 | 6-DaHall 1-PDU-01 | [branch#002] [A] kWh last month | 236.8 | 7-DaHall 1-PDU-01 | [branch#019] [A] kWh last month | 580.6
4-DaHall 1-CEP-05 | 1879 [branch#12] [A] KWh last month | 0 | 5-DaHall 1-CEP-05 | [branch#012] [A] kWh last month | 33 | 6-DaHall 1-PDU-01 | [branch#003] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#020] [A] kWh last month | 280.7
4-DaHall 1-PDU-01 | [branch#001] [A] kWh last month | 395.8 | 5-DaHall 1-CEP-05 | [branch#013] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#004] [A] kWh last month | 508 | 7-DaHall 1-PDU-01 | [branch#021] [A] kWh last month | 601
4-DaHall 1-PDU-01 | [branch#002] [A] kWh last month | 5737.3 | 5-DaHall 1-CEP-05 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#005] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#022] [A] kWh last month | 258.6
4-DaHall 1-PDU-01 | [branch#003] [A] kWh last month | 5221.5 | 5-DaHall 1-CEP-05 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#006] [A] kWh last month | 403.2 | 7-DaHall 1-PDU-01 | [branch#023] [A] kWh last month | 282.5
4-DaHall 1-PDU-01 | [branch#004] [A] kWh last month | 5592.9 | 5-DaHall 1-CEP-05 | [branch#016] [A] kWh last month | 1879.3 | 6-DaHall 1-PDU-01 | [branch#007] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#024] [A] kWh last month | 408
4-DaHall 1-PDU-01 | [branch#005] [A] kWh last month | 6510 | 5-DaHall 1-CEP-05 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#008] [A] kWh last month | 698.1 | 7-DaHall 1-PDU-01 | [branch#025] [A] kWh last month | 304.5
4-DaHall 1-PDU-01 | [branch#006] [A] kWh last month | 3450.2 | 5-DaHall 1-CEP-05 | [branch#018] [A] kWh last month | 1403.3 | 6-DaHall 1-PDU-01 | [branch#009] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#026] [A] kWh last month | 502.1
4-DaHall 1-PDU-01 | [branch#007] [A] kWh last month | 1781.8 | 5-DaHall 1-CEP-06 | 0119 [branch#01] [A] KWh last month | 69.5 | 6-DaHall 1-PDU-01 | [branch#010] [A] kWh last month | 1222.8 | 7-DaHall 1-PDU-01 | [branch#027] [A] kWh last month | 514.6
4-DaHall 1-PDU-01 | [branch#008] [A] kWh last month | 0 | 5-DaHall 1-CEP-06 | 0279 [branch#02] [A] KWh last month | 69.6 | 6-DaHall 1-PDU-01 | [branch#011] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#028] [A] kWh last month | 811.8
4-DaHall 1-PDU-01 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-CEP-06 | 0439 [branch#03] [A] KWh last month | 66.5 | 6-DaHall 1-PDU-01 | [branch#012] [A] kWh last month | 1161.9 | 7-DaHall 1-PDU-01 | [branch#029] [A] kWh last month | 3.5
4-DaHall 1-PDU-02 | [branch#001] [A] kWh last month | 259.5 | 5-DaHall 1-CEP-06 | 0599 [branch#04] [A] KWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#013] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#030] [A] kWh last month | 40.3
4-DaHall 1-PDU-02 | [branch#002] [A] kWh last month | 5349.7 | 5-DaHall 1-PDU-01 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#014] [A] kWh last month | 821 | 7-DaHall 1-PDU-01 | [branch#031] [A] kWh last month | 661.9
4-DaHall 1-PDU-02 | [branch#003] [A] kWh last month | 4940.3 | 5-DaHall 1-PDU-01 | [branch#055] [A] kWh last month | 32.8 | 6-DaHall 1-PDU-01 | [branch#015] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#032] [A] kWh last month | 283.7
4-DaHall 1-PDU-02 | [branch#004] [A] kWh last month | 5372.7 | 5-DaHall 1-PDU-01 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#016] [A] kWh last month | 721.6 | 7-DaHall 1-PDU-01 | [branch#033] [A] kWh last month | 1331.7
4-DaHall 1-PDU-02 | [branch#005] [A] kWh last month | 6458.9 | 5-DaHall 1-PDU-01 | [branch#056] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#017] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#034] [A] kWh last month | 0
4-DaHall 1-PDU-02 | [branch#006] [A] kWh last month | 1792.3 | 5-DaHall 1-PDU-01 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#018] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#035] [A] kWh last month | 1040.6
4-DaHall 1-PDU-02 | [branch#007] [A] kWh last month | 4320.9 | 5-DaHall 1-PDU-01 | [branch#057] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#019] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#036] [A] kWh last month | 0
4-DaHall 1-PDU-02 | [branch#008] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#020] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#037] [A] kWh last month | 0
4-DaHall 1-PDU-02 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#058] [A] kWh last month | 216.2 | 6-DaHall 1-PDU-01 | [branch#021] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#038] [A] kWh last month | 380.7
4-DaHall 1-PDU-03 | [branch#001] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#022] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#039] [A] kWh last month | 135.4
4-DaHall 1-PDU-03 | [branch#002] [A] kWh last month | 5018.1 | 5-DaHall 1-PDU-01 | [branch#059] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#023] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#040] [A] kWh last month | 455.6
4-DaHall 1-PDU-03 | [branch#003] [A] kWh last month | 4388 | 5-DaHall 1-PDU-01 | [branch#006] [A] kWh last month | 2138 | 6-DaHall 1-PDU-01 | [branch#024] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#041] [A] kWh last month | 123.8
4-DaHall 1-PDU-03 | [branch#004] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#060] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#025] [A] kWh last month | 285.8 | 7-DaHall 1-PDU-01 | [branch#042] [A] kWh last month | 492.9
4-DaHall 1-PDU-03 | [branch#005] [A] kWh last month | 964.3 | 5-DaHall 1-PDU-01 | [branch#007] [A] kWh last month | 1693.2 | 6-DaHall 1-PDU-01 | [branch#026] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#043] [A] kWh last month | 0
4-DaHall 1-PDU-03 | [branch#006] [A] kWh last month | 1507.6 | 5-DaHall 1-PDU-01 | [branch#061] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#027] [A] kWh last month | 301.3 | 7-DaHall 1-PDU-01 | [branch#044] [A] kWh last month | 866.9
4-DaHall 1-PDU-03 | [branch#007] [A] kWh last month | 4199 | 5-DaHall 1-PDU-01 | [branch#008] [A] kWh last month | 2079.2 | 6-DaHall 1-PDU-01 | [branch#028] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#045] [A] kWh last month | 0
4-DaHall 1-PDU-03 | [branch#008] [A] kWh last month | 2609.3 | 5-DaHall 1-PDU-01 | [branch#062] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#029] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#046] [A] kWh last month | 0
4-DaHall 1-PDU-03 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#030] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#047] [A] kWh last month | 0
4-DaHall 1-PDU-04 | [branch#001] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#063] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#031] [A] kWh last month | 267.1 | 7-DaHall 1-PDU-01 | [branch#048] [A] kWh last month | 267.2
4-DaHall 1-PDU-04 | [branch#002] [A] kWh last month | 6085.6 | 5-DaHall 1-PDU-01 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#032] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#049] [A] kWh last month | 0
4-DaHall 1-PDU-04 | [branch#003] [A] kWh last month | 4413 | 5-DaHall 1-PDU-01 | [branch#064] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#033] [A] kWh last month | 240.4 | 7-DaHall 1-PDU-01 | [branch#050] [A] kWh last month | 0
4-DaHall 1-PDU-04 | [branch#004] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#011] [A] kWh last month | 123.4 | 6-DaHall 1-PDU-01 | [branch#034] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#051] [A] kWh last month | 0
4-DaHall 1-PDU-04 | [branch#005] [A] kWh last month | 1447.4 | 5-DaHall 1-PDU-01 | [branch#065] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#035] [A] kWh last month | 90.7 | 7-DaHall 1-PDU-01 | [branch#052] [A] kWh last month | 0
4-DaHall 1-PDU-04 | [branch#006] [A] kWh last month | 2230.9 | 5-DaHall 1-PDU-01 | [branch#012] [A] kWh last month | 186.7 | 6-DaHall 1-PDU-01 | [branch#036] [A] kWh last month | 145.3 | 7-DaHall 1-PDU-01 | [branch#053] [A] kWh last month | 0
4-DaHall 1-PDU-04 | [branch#007] [A] kWh last month | 3190.4 | 5-DaHall 1-PDU-01 | [branch#066] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#037] [A] kWh last month | 0 | 7-DaHall 1-PDU-01 | [branch#054] [A] kWh last month | 41.6
4-DaHall 1-PDU-04 | [branch#008] [A] kWh last month | 3222.8 | 5-DaHall 1-PDU-01 | [branch#013] [A] kWh last month | 226.1 | 6-DaHall 1-PDU-01 | [branch#038] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#001] [A] kWh last month | 0
4-DaHall 1-PDU-04 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#067] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#039] [A] kWh last month | 34.3 | 7-DaHall 1-PDU-02 | [branch#002] [A] kWh last month | 0
4-DaHall 1-PDU-05 | [branch#001] [A] kWh last month | 1363.3 | 5-DaHall 1-PDU-01 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#040] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#003] [A] kWh last month | 731.8
4-DaHall 1-PDU-05 | [branch#002] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#068] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#041] [A] kWh last month | 114.5 | 7-DaHall 1-PDU-02 | [branch#004] [A] kWh last month | 0
4-DaHall 1-PDU-05 | [branch#003] [A] kWh last month | 1114.9 | 5-DaHall 1-PDU-01 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#042] [A] kWh last month | 595 | 7-DaHall 1-PDU-02 | [branch#005] [A] kWh last month | 0
4-DaHall 1-PDU-05 | [branch#004] [A] kWh last month | 1036.8 | 5-DaHall 1-PDU-01 | [branch#069] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#043] [A] kWh last month | 593.7 | 7-DaHall 1-PDU-02 | [branch#006] [A] kWh last month | 0
4-DaHall 1-PDU-05 | [branch#005] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#044] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#007] [A] kWh last month | 880.2
4-DaHall 1-PDU-05 | [branch#006] [A] kWh last month | 1714 | 5-DaHall 1-PDU-01 | [branch#070] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#045] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#008] [A] kWh last month | 3
4-DaHall 1-PDU-05 | [branch#007] [A] kWh last month | 900.5 | 5-DaHall 1-PDU-01 | [branch#017] [A] kWh last month | 1747.7 | 6-DaHall 1-PDU-01 | [branch#046] [A] kWh last month | 75.1 | 7-DaHall 1-PDU-02 | [branch#009] [A] kWh last month | 870.9
4-DaHall 1-PDU-05 | [branch#008] [A] kWh last month | 1704.6 | 5-DaHall 1-PDU-01 | [branch#071] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#047] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#010] [A] kWh last month | 476.4
4-DaHall 1-PDU-05 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#018] [A] kWh last month | 1565.8 | 6-DaHall 1-PDU-01 | [branch#048] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#011] [A] kWh last month | 776.4
4-DaHall 1-PDU-05 | [branch#010] [A] kWh last month | 5187.4 | 5-DaHall 1-PDU-01 | [branch#072] [A] kWh last month | 0 | 6-DaHall 1-PDU-01 | [branch#049] [A] kWh last month | 958 | 7-DaHall 1-PDU-02 | [branch#012] [A] kWh last month | 0
4-DaHall 1-PDU-05 | [branch#011] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#019] [A] kWh last month | 1854.4 | 6-DaHall 1-PDU-01 | [branch#050] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#013] [A] kWh last month | 785.8
4-DaHall 1-PDU-05 | [branch#012] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#073] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#001] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#014] [A] kWh last month | 351.1
4-DaHall 1-PDU-06 | [branch#001] [A] kWh last month | 1605.2 | 5-DaHall 1-PDU-01 | [branch#020] [A] kWh last month | 1503.8 | 6-DaHall 1-PDU-02 | [branch#002] [A] kWh last month | 167.9 | 7-DaHall 1-PDU-02 | [branch#015] [A] kWh last month | 92.9
4-DaHall 1-PDU-06 | [branch#002] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#074] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#003] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#016] [A] kWh last month | 392.5
4-DaHall 1-PDU-06 | [branch#003] [A] kWh last month | 1352.4 | 5-DaHall 1-PDU-01 | [branch#021] [A] kWh last month | 1763.3 | 6-DaHall 1-PDU-02 | [branch#004] [A] kWh last month | 358.2 | 7-DaHall 1-PDU-02 | [branch#017] [A] kWh last month | 528.3
4-DaHall 1-PDU-06 | [branch#004] [A] kWh last month | 997.4 | 5-DaHall 1-PDU-01 | [branch#075] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#005] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#018] [A] kWh last month | 263
4-DaHall 1-PDU-06 | [branch#005] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#006] [A] kWh last month | 739.6 | 7-DaHall 1-PDU-02 | [branch#019] [A] kWh last month | 1311.5
4-DaHall 1-PDU-06 | [branch#006] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#076] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#007] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#020] [A] kWh last month | 301.1
4-DaHall 1-PDU-06 | [branch#007] [A] kWh last month | 1189.4 | 5-DaHall 1-PDU-01 | [branch#023] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#008] [A] kWh last month | 423.4 | 7-DaHall 1-PDU-02 | [branch#021] [A] kWh last month | 621.5
4-DaHall 1-PDU-06 | [branch#008] [A] kWh last month | 2039.9 | 5-DaHall 1-PDU-01 | [branch#077] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#009] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#022] [A] kWh last month | 296.8
4-DaHall 1-PDU-06 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#010] [A] kWh last month | 1180.2 | 7-DaHall 1-PDU-02 | [branch#023] [A] kWh last month | 395.8
4-DaHall 1-PDU-06 | [branch#010] [A] kWh last month | 5991.4 | 5-DaHall 1-PDU-01 | [branch#078] [A] kWh last month | 77.2 | 6-DaHall 1-PDU-02 | [branch#011] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#024] [A] kWh last month | 329.4
4-DaHall 1-PDU-06 | [branch#011] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#012] [A] kWh last month | 1497.4 | 7-DaHall 1-PDU-02 | [branch#025] [A] kWh last month | 334.6
4-DaHall 1-PDU-06 | [branch#012] [A] kWh last month | 0 | 5-DaHall 1-PDU-01 | [branch#079] [A] kWh last month | 269.7 | 6-DaHall 1-PDU-02 | [branch#013] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#026] [A] kWh last month | 537
4-DaHall 1-PDU-07 | [branch#001] [A] kWh last month | 3053.1 | 5-DaHall 1-PDU-01 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#014] [A] kWh last month | 1102.4 | 7-DaHall 1-PDU-02 | [branch#027] [A] kWh last month | 573.2
4-DaHall 1-PDU-07 | [branch#002] [A] kWh last month | 5139.6 | 5-DaHall 1-PDU-01 | [branch#080] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#015] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#028] [A] kWh last month | 855.5
4-DaHall 1-PDU-07 | [branch#003] [A] kWh last month | 776.2 | 5-DaHall 1-PDU-02 | [branch#055] [A] kWh last month | 32.7 | 6-DaHall 1-PDU-02 | [branch#016] [A] kWh last month | 744.1 | 7-DaHall 1-PDU-02 | [branch#029] [A] kWh last month | 272.8
4-DaHall 1-PDU-07 | [branch#004] [A] kWh last month | 1512.3 | 5-DaHall 1-PDU-02 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#017] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#030] [A] kWh last month | 55.3
4-DaHall 1-PDU-07 | [branch#005] [A] kWh last month | 864.2 | 5-DaHall 1-PDU-02 | [branch#056] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#018] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#031] [A] kWh last month | 506.7
4-DaHall 1-PDU-07 | [branch#006] [A] kWh last month | 2168.2 | 5-DaHall 1-PDU-02 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#019] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#032] [A] kWh last month | 236.8
4-DaHall 1-PDU-07 | [branch#007] [A] kWh last month | 1855.3 | 5-DaHall 1-PDU-02 | [branch#057] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#020] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#033] [A] kWh last month | 1295.8
4-DaHall 1-PDU-07 | [branch#008] [A] kWh last month | 5132.6 | 5-DaHall 1-PDU-02 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#021] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#034] [A] kWh last month | 0
4-DaHall 1-PDU-07 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#058] [A] kWh last month | 179.8 | 6-DaHall 1-PDU-02 | [branch#022] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#035] [A] kWh last month | 1007.9
4-DaHall 1-PDU-07 | [branch#010] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#023] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#036] [A] kWh last month | 0
4-DaHall 1-PDU-07 | [branch#011] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#059] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#024] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#037] [A] kWh last month | 0
4-DaHall 1-PDU-07 | [branch#012] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#025] [A] kWh last month | 335.9 | 7-DaHall 1-PDU-02 | [branch#038] [A] kWh last month | 529.7
4-DaHall 1-PDU-08 | [branch#001] [A] kWh last month | 3423.9 | 5-DaHall 1-PDU-02 | [branch#060] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#026] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#039] [A] kWh last month | 252.6
4-DaHall 1-PDU-08 | [branch#002] [A] kWh last month | 5070.3 | 5-DaHall 1-PDU-02 | [branch#006] [A] kWh last month | 1792.6 | 6-DaHall 1-PDU-02 | [branch#027] [A] kWh last month | 180.4 | 7-DaHall 1-PDU-02 | [branch#040] [A] kWh last month | 422
4-DaHall 1-PDU-08 | [branch#003] [A] kWh last month | 798.7 | 5-DaHall 1-PDU-02 | [branch#061] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#028] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#041] [A] kWh last month | 0
4-DaHall 1-PDU-08 | [branch#004] [A] kWh last month | 1433.1 | 5-DaHall 1-PDU-02 | [branch#007] [A] kWh last month | 1939.7 | 6-DaHall 1-PDU-02 | [branch#029] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#042] [A] kWh last month | 669.7
4-DaHall 1-PDU-08 | [branch#005] [A] kWh last month | 1102 | 5-DaHall 1-PDU-02 | [branch#062] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#030] [A] kWh last month | 949.9 | 7-DaHall 1-PDU-02 | [branch#043] [A] kWh last month | 0
4-DaHall 1-PDU-08 | [branch#006] [A] kWh last month | 1671.9 | 5-DaHall 1-PDU-02 | [branch#008] [A] kWh last month | 1716.3 | 6-DaHall 1-PDU-02 | [branch#031] [A] kWh last month | 257.5 | 7-DaHall 1-PDU-02 | [branch#044] [A] kWh last month | 223.6
4-DaHall 1-PDU-08 | [branch#007] [A] kWh last month | 1749.5 | 5-DaHall 1-PDU-02 | [branch#063] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#032] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#045] [A] kWh last month | 0
4-DaHall 1-PDU-08 | [branch#008] [A] kWh last month | 3914.5 | 5-DaHall 1-PDU-02 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#033] [A] kWh last month | 273.7 | 7-DaHall 1-PDU-02 | [branch#046] [A] kWh last month | 0
4-DaHall 1-PDU-08 | [branch#009] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#064] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#034] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#047] [A] kWh last month | 0
4-DaHall 1-PDU-08 | [branch#010] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#035] [A] kWh last month | 84.5 | 7-DaHall 1-PDU-02 | [branch#048] [A] kWh last month | 293.5
4-DaHall 1-PDU-08 | [branch#011] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#036] [A] kWh last month | 197 | 7-DaHall 1-PDU-02 | [branch#049] [A] kWh last month | 101.5
4-DaHall 1-PDU-08 | [branch#012] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#065] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#037] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#050] [A] kWh last month | 328.3
4-DaHall 1-PDU-09 | [branch#001] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#012] [A] kWh last month | 218.5 | 6-DaHall 1-PDU-02 | [branch#038] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#051] [A] kWh last month | 71.8
4-DaHall 1-PDU-09 | [branch#002] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#066] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#039] [A] kWh last month | 30.8 | 7-DaHall 1-PDU-02 | [branch#052] [A] kWh last month | 0
4-DaHall 1-PDU-09 | [branch#003] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#013] [A] kWh last month | 192.6 | 6-DaHall 1-PDU-02 | [branch#040] [A] kWh last month | 0 | 7-DaHall 1-PDU-02 | [branch#053] [A] kWh last month | 26.6
4-DaHall 1-PDU-10 | [branch#001] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#067] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#041] [A] kWh last month | 84.5 | 7-DaHall 1-PDU-02 | [branch#054] [A] kWh last month | 0
4-DaHall 1-PDU-10 | [branch#002] [A] kWh last month | 12636.4 | 5-DaHall 1-PDU-02 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#042] [A] kWh last month | 612.1 | 7-DaHall 1-PDU-03 | [branch#001] [A] kWh last month | 7905
4-DaHall 1-PDU-10 | [branch#003] [A] kWh last month | 6598.3 | 5-DaHall 1-PDU-02 | [branch#068] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#043] [A] kWh last month | 600.7 | 7-DaHall 1-PDU-03 | [branch#002] [A] kWh last month | 1745.9
4-EPS-CEP-06 | [branch#001] [A] kWh last month | 515.7 | 5-DaHall 1-PDU-02 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#044] [A] kWh last month | 0 | 7-DaHall 1-PDU-03 | [branch#003] [A] kWh last month | 2825.5
4-EPS-CEP-06 | [branch#002] [A] kWh last month | 4659.8 | 5-DaHall 1-PDU-02 | [branch#069] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#045] [A] kWh last month | 0 | 7-DaHall 1-PDU-03 | [branch#004] [A] kWh last month | 0
4-EPS-CEP-06 | [branch#003] [A] kWh last month | 407.9 | 5-DaHall 1-PDU-02 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#046] [A] kWh last month | 0 | 7-DaHall 1-PDU-03 | [branch#005] [A] kWh last month | 0
4-EPS-CEP-06 | [branch#004] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#070] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#047] [A] kWh last month | 0 | 7-DaHall 1-PDU-03 | [branch#006] [A] kWh last month | 22829.8
4-EPS-CEP-06 | [branch#005] [A] kWh last month | 75.8 | 5-DaHall 1-PDU-02 | [branch#017] [A] kWh last month | 1800.8 | 6-DaHall 1-PDU-02 | [branch#048] [A] kWh last month | 0 | 7-DaHall 1-PDU-03 | [branch#007] [A] kWh last month | 0
4-EPS-CEP-06 | [branch#006] [A] kWh last month | 0 | 5-DaHall 1-PDU-02 | [branch#071] [A] kWh last month | 0 | 6-DaHall 1-PDU-02 | [branch#049] [A] kWh last month | 0 | 7-DaHall 1-PDU-03 | [branch#008] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-02 | [branch#018] [A] kWh last month | 1829.4 | 6-DaHall 1-PDU-02 | [branch#050] [A] kWh last month | 0 | 7-DaHall 1-PDU-03 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-02 | [branch#072] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#001] [A] kWh last month | 730 | 7-DaHall 1-PDU-03 | [branch#010] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-02 | [branch#019] [A] kWh last month | 1541 | 6-DaHall 1-PDU-03 | [branch#002] [A] kWh last month | 0 | 7-DaHall 1-PDU-04 | [branch#001] [A] kWh last month | 20193.4
|  |  | 5-DaHall 1-PDU-02 | [branch#073] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#003] [A] kWh last month | 645.4 | 7-DaHall 1-PDU-04 | [branch#002] [A] kWh last month | 10523
|  |  | 5-DaHall 1-PDU-02 | [branch#020] [A] kWh last month | 1798.5 | 6-DaHall 1-PDU-03 | [branch#004] [A] kWh last month | 0 | 7-DaHall 1-PDU-04 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-02 | [branch#074] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#005] [A] kWh last month | 112.1 | 7-DaHall 1-PDU-04 | [branch#004] [A] kWh last month | 3276.8
|  |  | 5-DaHall 1-PDU-02 | [branch#021] [A] kWh last month | 1409.5 | 6-DaHall 1-PDU-03 | [branch#006] [A] kWh last month | 0 | 7-DaHall 1-PDU-04 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-02 | [branch#075] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#007] [A] kWh last month | 562.8 | 7-DaHall 1-PDU-04 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-02 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#008] [A] kWh last month | 0 | 7-DaHall 1-PDU-04 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-02 | [branch#076] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#009] [A] kWh last month | 562.4 | 7-DaHall 1-PDU-04 | [branch#008] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-02 | [branch#023] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#010] [A] kWh last month | 0 | 7-DaHall 1-PDU-04 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-02 | [branch#077] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#011] [A] kWh last month | 465.8 | 7-DaHall 1-PDU-04 | [branch#010] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-02 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#012] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-02 | [branch#078] [A] kWh last month | 86.5 | 6-DaHall 1-PDU-03 | [branch#013] [A] kWh last month | 799.8 | 7-DaHall 1-RPP-01 | [branch#002] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-02 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#014] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-02 | [branch#079] [A] kWh last month | 173.8 | 6-DaHall 1-PDU-03 | [branch#015] [A] kWh last month | 584.4 | 7-DaHall 1-RPP-01 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-02 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#016] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-02 | [branch#080] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#017] [A] kWh last month | 287.9 | 7-DaHall 1-RPP-01 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#018] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#055] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#019] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#008] [A] kWh last month | 319.5
|  |  | 5-DaHall 1-PDU-03 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#020] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#056] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#021] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#010] [A] kWh last month | 232.1
|  |  | 5-DaHall 1-PDU-03 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#022] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#011] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#057] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#023] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#012] [A] kWh last month | 571.8
|  |  | 5-DaHall 1-PDU-03 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#024] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#013] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#058] [A] kWh last month | 84.7 | 6-DaHall 1-PDU-03 | [branch#025] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#014] [A] kWh last month | 955.4
|  |  | 5-DaHall 1-PDU-03 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#026] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#015] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#059] [A] kWh last month | 214.1 | 6-DaHall 1-PDU-03 | [branch#027] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#016] [A] kWh last month | 223.2
|  |  | 5-DaHall 1-PDU-03 | [branch#006] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#028] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#017] [A] kWh last month | 68
|  |  | 5-DaHall 1-PDU-03 | [branch#060] [A] kWh last month | 545.4 | 6-DaHall 1-PDU-03 | [branch#029] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#018] [A] kWh last month | 198.3
|  |  | 5-DaHall 1-PDU-03 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#030] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#019] [A] kWh last month | 108.3
|  |  | 5-DaHall 1-PDU-03 | [branch#061] [A] kWh last month | 269.1 | 6-DaHall 1-PDU-03 | [branch#031] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#020] [A] kWh last month | 223.8
|  |  | 5-DaHall 1-PDU-03 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#032] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#062] [A] kWh last month | 44.5 | 6-DaHall 1-PDU-03 | [branch#033] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#034] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#023] [A] kWh last month | 184.2
|  |  | 5-DaHall 1-PDU-03 | [branch#063] [A] kWh last month | 608.9 | 6-DaHall 1-PDU-03 | [branch#035] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#036] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#025] [A] kWh last month | 233.4
|  |  | 5-DaHall 1-PDU-03 | [branch#064] [A] kWh last month | 730.3 | 6-DaHall 1-PDU-03 | [branch#037] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#026] [A] kWh last month | 198.3
|  |  | 5-DaHall 1-PDU-03 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#038] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#027] [A] kWh last month | 404.7
|  |  | 5-DaHall 1-PDU-03 | [branch#065] [A] kWh last month | 399.1 | 6-DaHall 1-PDU-03 | [branch#039] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#028] [A] kWh last month | 126.6
|  |  | 5-DaHall 1-PDU-03 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#040] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#029] [A] kWh last month | 475.8
|  |  | 5-DaHall 1-PDU-03 | [branch#066] [A] kWh last month | 461.9 | 6-DaHall 1-PDU-03 | [branch#041] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#030] [A] kWh last month | 503.7
|  |  | 5-DaHall 1-PDU-03 | [branch#013] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#042] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#031] [A] kWh last month | 570.1
|  |  | 5-DaHall 1-PDU-03 | [branch#067] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#043] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#044] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#068] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#045] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#046] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#035] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#069] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#047] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#036] [A] kWh last month | 518.2
|  |  | 5-DaHall 1-PDU-03 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#048] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#037] [A] kWh last month | 678.9
|  |  | 5-DaHall 1-PDU-03 | [branch#070] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#049] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#038] [A] kWh last month | 310.2
|  |  | 5-DaHall 1-PDU-03 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-03 | [branch#050] [A] kWh last month | 0 | 7-DaHall 1-RPP-01 | [branch#039] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#071] [A] kWh last month | 248.5 | 6-DaHall 1-PDU-04 | [branch#001] [A] kWh last month | 534 | 7-DaHall 1-RPP-01 | [branch#040] [A] kWh last month | 736.8
|  |  | 5-DaHall 1-PDU-03 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#002] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#072] [A] kWh last month | 214.9 | 6-DaHall 1-PDU-04 | [branch#003] [A] kWh last month | 699.6 | 7-DaHall 1-RPP-02 | [branch#002] [A] kWh last month | 287.3
|  |  | 5-DaHall 1-PDU-03 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#004] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#003] [A] kWh last month | 68.2
|  |  | 5-DaHall 1-PDU-03 | [branch#073] [A] kWh last month | 226 | 6-DaHall 1-PDU-04 | [branch#005] [A] kWh last month | 141.5 | 7-DaHall 1-RPP-02 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#020] [A] kWh last month | 481.2 | 6-DaHall 1-PDU-04 | [branch#006] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#074] [A] kWh last month | 264.8 | 6-DaHall 1-PDU-04 | [branch#007] [A] kWh last month | 604.9 | 7-DaHall 1-RPP-02 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#021] [A] kWh last month | 19.5 | 6-DaHall 1-PDU-04 | [branch#008] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#007] [A] kWh last month | 148.6
|  |  | 5-DaHall 1-PDU-03 | [branch#075] [A] kWh last month | 165.4 | 6-DaHall 1-PDU-04 | [branch#009] [A] kWh last month | 630.9 | 7-DaHall 1-RPP-02 | [branch#008] [A] kWh last month | 592
|  |  | 5-DaHall 1-PDU-03 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#010] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#009] [A] kWh last month | 173.6
|  |  | 5-DaHall 1-PDU-03 | [branch#076] [A] kWh last month | 209 | 6-DaHall 1-PDU-04 | [branch#011] [A] kWh last month | 710 | 7-DaHall 1-RPP-02 | [branch#010] [A] kWh last month | 73.3
|  |  | 5-DaHall 1-PDU-03 | [branch#023] [A] kWh last month | 362.5 | 6-DaHall 1-PDU-04 | [branch#012] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#011] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#077] [A] kWh last month | 440.3 | 6-DaHall 1-PDU-04 | [branch#013] [A] kWh last month | 434 | 7-DaHall 1-RPP-02 | [branch#012] [A] kWh last month | 619.2
|  |  | 5-DaHall 1-PDU-03 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#014] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#013] [A] kWh last month | 379.8
|  |  | 5-DaHall 1-PDU-03 | [branch#078] [A] kWh last month | 430.2 | 6-DaHall 1-PDU-04 | [branch#015] [A] kWh last month | 535.3 | 7-DaHall 1-RPP-02 | [branch#014] [A] kWh last month | 2175.5
|  |  | 5-DaHall 1-PDU-03 | [branch#025] [A] kWh last month | 596.6 | 6-DaHall 1-PDU-04 | [branch#016] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#015] [A] kWh last month | 261.9
|  |  | 5-DaHall 1-PDU-03 | [branch#079] [A] kWh last month | 565.6 | 6-DaHall 1-PDU-04 | [branch#017] [A] kWh last month | 253.8 | 7-DaHall 1-RPP-02 | [branch#016] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-03 | [branch#026] [A] kWh last month | 873.4 | 6-DaHall 1-PDU-04 | [branch#018] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#017] [A] kWh last month | 430.7
|  |  | 5-DaHall 1-PDU-03 | [branch#080] [A] kWh last month | 622.5 | 6-DaHall 1-PDU-04 | [branch#019] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-04 | [branch#055] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#020] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#019] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-04 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#021] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#020] [A] kWh last month | 323.7
|  |  | 5-DaHall 1-PDU-04 | [branch#056] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#022] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-04 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#023] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-04 | [branch#057] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#024] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-04 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#025] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#024] [A] kWh last month | 204.5
|  |  | 5-DaHall 1-PDU-04 | [branch#058] [A] kWh last month | 85.7 | 6-DaHall 1-PDU-04 | [branch#026] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#025] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-04 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#027] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#026] [A] kWh last month | 27.4
|  |  | 5-DaHall 1-PDU-04 | [branch#059] [A] kWh last month | 261 | 6-DaHall 1-PDU-04 | [branch#028] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#027] [A] kWh last month | 861.1
|  |  | 5-DaHall 1-PDU-04 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#029] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-04 | [branch#060] [A] kWh last month | 541.7 | 6-DaHall 1-PDU-04 | [branch#030] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#029] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-04 | [branch#006] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#031] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#030] [A] kWh last month | 273.2
|  |  | 5-DaHall 1-PDU-04 | [branch#061] [A] kWh last month | 274.1 | 6-DaHall 1-PDU-04 | [branch#032] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#031] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-04 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#033] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#032] [A] kWh last month | 530.1
|  |  | 5-DaHall 1-PDU-04 | [branch#062] [A] kWh last month | 92.4 | 6-DaHall 1-PDU-04 | [branch#034] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-04 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#035] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-04 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#036] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#035] [A] kWh last month | 292.1
|  |  | 5-DaHall 1-PDU-04 | [branch#063] [A] kWh last month | 608.7 | 6-DaHall 1-PDU-04 | [branch#037] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#036] [A] kWh last month | 1054.4
|  |  | 5-DaHall 1-PDU-04 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#038] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#037] [A] kWh last month | 670.8
|  |  | 5-DaHall 1-PDU-04 | [branch#064] [A] kWh last month | 705 | 6-DaHall 1-PDU-04 | [branch#039] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#038] [A] kWh last month | 745.2
|  |  | 5-DaHall 1-PDU-04 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#040] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#039] [A] kWh last month | 242.9
|  |  | 5-DaHall 1-PDU-04 | [branch#065] [A] kWh last month | 266.9 | 6-DaHall 1-PDU-04 | [branch#041] [A] kWh last month | 0 | 7-DaHall 1-RPP-02 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-04 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#042] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#001] [A] kWh last month | 163.5
|  |  | 5-DaHall 1-PDU-04 | [branch#066] [A] kWh last month | 661.4 | 6-DaHall 1-PDU-04 | [branch#043] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#002] [A] kWh last month | 137.8
|  |  | 5-DaHall 1-PDU-04 | [branch#013] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#044] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#003] [A] kWh last month | 377.8
|  |  | 5-DaHall 1-PDU-04 | [branch#067] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#045] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-04 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#046] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#005] [A] kWh last month | 490
|  |  | 5-DaHall 1-PDU-04 | [branch#068] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#047] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#006] [A] kWh last month | 242.6
|  |  | 5-DaHall 1-PDU-04 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#048] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#007] [A] kWh last month | 367.2
|  |  | 5-DaHall 1-PDU-04 | [branch#069] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#049] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#008] [A] kWh last month | 301.9
|  |  | 5-DaHall 1-PDU-04 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-04 | [branch#050] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#009] [A] kWh last month | 391.8
|  |  | 5-DaHall 1-PDU-04 | [branch#070] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#001] [A] kWh last month | 0 | 7-DaHall 1-RPP-03 | [branch#010] [A] kWh last month | 343.9
|  |  | 5-DaHall 1-PDU-04 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#002] [A] kWh last month | 1818.7 | 7-DaHall 1-RPP-04 | [branch#001] [A] kWh last month | 153
|  |  | 5-DaHall 1-PDU-04 | [branch#071] [A] kWh last month | 22.2 | 6-DaHall 1-PDU-05 | [branch#003] [A] kWh last month | 0 | 7-DaHall 1-RPP-04 | [branch#002] [A] kWh last month | 242.6
|  |  | 5-DaHall 1-PDU-04 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#004] [A] kWh last month | 745.1 | 7-DaHall 1-RPP-04 | [branch#003] [A] kWh last month | 486.8
|  |  | 5-DaHall 1-PDU-04 | [branch#072] [A] kWh last month | 15.6 | 6-DaHall 1-PDU-05 | [branch#005] [A] kWh last month | 0 | 7-DaHall 1-RPP-04 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-04 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#006] [A] kWh last month | 92.8 | 7-DaHall 1-RPP-04 | [branch#005] [A] kWh last month | 666.6
|  |  | 5-DaHall 1-PDU-04 | [branch#073] [A] kWh last month | 246.3 | 6-DaHall 1-PDU-05 | [branch#007] [A] kWh last month | 0 | 7-DaHall 1-RPP-04 | [branch#006] [A] kWh last month | 184.8
|  |  | 5-DaHall 1-PDU-04 | [branch#020] [A] kWh last month | 566.1 | 6-DaHall 1-PDU-05 | [branch#008] [A] kWh last month | 360.7 | 7-DaHall 1-RPP-04 | [branch#007] [A] kWh last month | 628.5
|  |  | 5-DaHall 1-PDU-04 | [branch#074] [A] kWh last month | 272.5 | 6-DaHall 1-PDU-05 | [branch#009] [A] kWh last month | 0 | 7-DaHall 1-RPP-04 | [branch#008] [A] kWh last month | 292.5
|  |  | 5-DaHall 1-PDU-04 | [branch#021] [A] kWh last month | 11 | 6-DaHall 1-PDU-05 | [branch#010] [A] kWh last month | 103.3 | 7-DaHall 1-RPP-04 | [branch#009] [A] kWh last month | 234.3
|  |  | 5-DaHall 1-PDU-04 | [branch#075] [A] kWh last month | 180.9 | 6-DaHall 1-PDU-05 | [branch#011] [A] kWh last month | 157.4 | 7-DaHall 1-RPP-04 | [branch#010] [A] kWh last month | 369.4
|  |  | 5-DaHall 1-PDU-04 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#012] [A] kWh last month | 203.2
|  |  | 5-DaHall 1-PDU-04 | [branch#076] [A] kWh last month | 177.2 | 6-DaHall 1-PDU-05 | [branch#013] [A] kWh last month | 205.1
|  |  | 5-DaHall 1-PDU-04 | [branch#023] [A] kWh last month | 377.3 | 6-DaHall 1-PDU-05 | [branch#014] [A] kWh last month | 740.1
|  |  | 5-DaHall 1-PDU-04 | [branch#077] [A] kWh last month | 326.7 | 6-DaHall 1-PDU-05 | [branch#015] [A] kWh last month | 481.3
|  |  | 5-DaHall 1-PDU-04 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#016] [A] kWh last month | 471.2
|  |  | 5-DaHall 1-PDU-04 | [branch#078] [A] kWh last month | 327 | 6-DaHall 1-PDU-05 | [branch#017] [A] kWh last month | 121.8
|  |  | 5-DaHall 1-PDU-04 | [branch#025] [A] kWh last month | 635.5 | 6-DaHall 1-PDU-05 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-04 | [branch#079] [A] kWh last month | 471.6 | 6-DaHall 1-PDU-05 | [branch#019] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-04 | [branch#026] [A] kWh last month | 828.1 | 6-DaHall 1-PDU-05 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-04 | [branch#080] [A] kWh last month | 604.6 | 6-DaHall 1-PDU-05 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#025] [A] kWh last month | 450.9
|  |  | 5-DaHall 1-PDU-05 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#006] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#027] [A] kWh last month | 519
|  |  | 5-DaHall 1-PDU-05 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#029] [A] kWh last month | 297.2
|  |  | 5-DaHall 1-PDU-05 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#031] [A] kWh last month | 241.5
|  |  | 5-DaHall 1-PDU-05 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#033] [A] kWh last month | 140.8
|  |  | 5-DaHall 1-PDU-05 | [branch#013] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#035] [A] kWh last month | 84.7
|  |  | 5-DaHall 1-PDU-05 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#037] [A] kWh last month | 544.6
|  |  | 5-DaHall 1-PDU-05 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#039] [A] kWh last month | 316
|  |  | 5-DaHall 1-PDU-05 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#020] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#041] [A] kWh last month | 249.4
|  |  | 5-DaHall 1-PDU-05 | [branch#021] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#043] [A] kWh last month | 838.9
|  |  | 5-DaHall 1-PDU-05 | [branch#023] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#045] [A] kWh last month | 684.6
|  |  | 5-DaHall 1-PDU-05 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#047] [A] kWh last month | 655.8
|  |  | 5-DaHall 1-PDU-05 | [branch#027] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#028] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#049] [A] kWh last month | 1205.7
|  |  | 5-DaHall 1-PDU-05 | [branch#029] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#030] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#051] [A] kWh last month | 624.3
|  |  | 5-DaHall 1-PDU-05 | [branch#031] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#052] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#032] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#053] [A] kWh last month | 881.4
|  |  | 5-DaHall 1-PDU-05 | [branch#033] [A] kWh last month | 0 | 6-DaHall 1-PDU-05 | [branch#054] [A] kWh last month | 592.4
|  |  | 5-DaHall 1-PDU-05 | [branch#034] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#035] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#002] [A] kWh last month | 1641
|  |  | 5-DaHall 1-PDU-05 | [branch#036] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#037] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#004] [A] kWh last month | 608.4
|  |  | 5-DaHall 1-PDU-05 | [branch#038] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#039] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#006] [A] kWh last month | 89.4
|  |  | 5-DaHall 1-PDU-05 | [branch#040] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#041] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#008] [A] kWh last month | 494.9
|  |  | 5-DaHall 1-PDU-05 | [branch#042] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#043] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#010] [A] kWh last month | 68.9
|  |  | 5-DaHall 1-PDU-05 | [branch#044] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#011] [A] kWh last month | 187.3
|  |  | 5-DaHall 1-PDU-05 | [branch#045] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#012] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#046] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#013] [A] kWh last month | 420.6
|  |  | 5-DaHall 1-PDU-05 | [branch#047] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#014] [A] kWh last month | 433
|  |  | 5-DaHall 1-PDU-05 | [branch#048] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#015] [A] kWh last month | 430.9
|  |  | 5-DaHall 1-PDU-05 | [branch#049] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#016] [A] kWh last month | 607.1
|  |  | 5-DaHall 1-PDU-05 | [branch#050] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#017] [A] kWh last month | 115.9
|  |  | 5-DaHall 1-PDU-05 | [branch#051] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#052] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#019] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#053] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-05 | [branch#054] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#025] [A] kWh last month | 386.4
|  |  | 5-DaHall 1-PDU-06 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#006] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#027] [A] kWh last month | 291.1
|  |  | 5-DaHall 1-PDU-06 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#029] [A] kWh last month | 155.9
|  |  | 5-DaHall 1-PDU-06 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#031] [A] kWh last month | 43.9
|  |  | 5-DaHall 1-PDU-06 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#033] [A] kWh last month | 140
|  |  | 5-DaHall 1-PDU-06 | [branch#013] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#035] [A] kWh last month | 43
|  |  | 5-DaHall 1-PDU-06 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#037] [A] kWh last month | 520.8
|  |  | 5-DaHall 1-PDU-06 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#039] [A] kWh last month | 283.7
|  |  | 5-DaHall 1-PDU-06 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#020] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#041] [A] kWh last month | 70.3
|  |  | 5-DaHall 1-PDU-06 | [branch#021] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#043] [A] kWh last month | 731.8
|  |  | 5-DaHall 1-PDU-06 | [branch#023] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#045] [A] kWh last month | 714.9
|  |  | 5-DaHall 1-PDU-06 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#047] [A] kWh last month | 606.3
|  |  | 5-DaHall 1-PDU-06 | [branch#027] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#028] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#049] [A] kWh last month | 187.5
|  |  | 5-DaHall 1-PDU-06 | [branch#029] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#030] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#051] [A] kWh last month | 721.9
|  |  | 5-DaHall 1-PDU-06 | [branch#031] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#052] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#032] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#053] [A] kWh last month | 91.3
|  |  | 5-DaHall 1-PDU-06 | [branch#033] [A] kWh last month | 0 | 6-DaHall 1-PDU-06 | [branch#054] [A] kWh last month | 352.1
|  |  | 5-DaHall 1-PDU-06 | [branch#034] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#035] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#002] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#036] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#037] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#038] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#039] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#040] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#041] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#008] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#042] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#043] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#010] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#044] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#011] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#045] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#012] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#046] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#013] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#047] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#014] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#048] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#015] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#049] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#016] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#050] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#017] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#051] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#052] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#019] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#053] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-06 | [branch#054] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#001] [A] kWh last month | 1196.9 | 6-DaHall 1-PDU-07 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#002] [A] kWh last month | 106.3 | 6-DaHall 1-PDU-07 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#003] [A] kWh last month | 101.4 | 6-DaHall 1-PDU-07 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#025] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#005] [A] kWh last month | 54.9 | 6-DaHall 1-PDU-07 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#006] [A] kWh last month | 58.1 | 6-DaHall 1-PDU-07 | [branch#027] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#029] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#031] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#013] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#035] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#037] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#039] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#020] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#041] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#021] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#043] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#023] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#045] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#047] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#027] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#028] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#049] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#029] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#030] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#051] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#031] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#052] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#032] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#053] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#033] [A] kWh last month | 0 | 6-DaHall 1-PDU-07 | [branch#054] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#034] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#035] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#002] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-07 | [branch#036] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#002] [A] kWh last month | 146.7 | 6-DaHall 1-PDU-08 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#003] [A] kWh last month | 120.2 | 6-DaHall 1-PDU-08 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#008] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#006] [A] kWh last month | 180.2 | 6-DaHall 1-PDU-08 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#007] [A] kWh last month | 776.2 | 6-DaHall 1-PDU-08 | [branch#010] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#011] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#012] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#013] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#014] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#015] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#013] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#016] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#017] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#019] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#020] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#021] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#025] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#023] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#027] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#029] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#027] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#028] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#031] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#029] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#030] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#031] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#032] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#035] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#033] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#034] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#037] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#035] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-08 | [branch#036] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#039] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#041] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#043] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#006] [A] kWh last month | 268 | 6-DaHall 1-PDU-08 | [branch#045] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#047] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#009] [A] kWh last month | 800.3 | 6-DaHall 1-PDU-08 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#049] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#051] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#013] [A] kWh last month | 293.7 | 6-DaHall 1-PDU-08 | [branch#052] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#053] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-08 | [branch#054] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#002] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#018] [A] kWh last month | 421.2 | 6-DaHall 1-PDU-09 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#020] [A] kWh last month | 323.6 | 6-DaHall 1-PDU-09 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#021] [A] kWh last month | 346.6 | 6-DaHall 1-PDU-09 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#023] [A] kWh last month | 741.6 | 6-DaHall 1-PDU-09 | [branch#008] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#010] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#026] [A] kWh last month | 841 | 6-DaHall 1-PDU-09 | [branch#011] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#027] [A] kWh last month | 376.3 | 6-DaHall 1-PDU-09 | [branch#012] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#028] [A] kWh last month | 842.7 | 6-DaHall 1-PDU-09 | [branch#013] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#029] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#014] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#030] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#015] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#031] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#016] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-11 | [branch#032] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#017] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#019] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#004] [A] kWh last month | 241.9 | 6-DaHall 1-PDU-09 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#006] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#025] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#009] [A] kWh last month | 441.3 | 6-DaHall 1-PDU-09 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#027] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#029] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#013] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#031] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#016] [A] kWh last month | 928.1 | 6-DaHall 1-PDU-09 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#018] [A] kWh last month | 462.8 | 6-DaHall 1-PDU-09 | [branch#035] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#019] [A] kWh last month | 373.7 | 6-DaHall 1-PDU-09 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#020] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#037] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#021] [A] kWh last month | 669.9 | 6-DaHall 1-PDU-09 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#039] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#023] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#024] [A] kWh last month | 549.5 | 6-DaHall 1-PDU-09 | [branch#041] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#025] [A] kWh last month | 483.3 | 6-DaHall 1-PDU-09 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#026] [A] kWh last month | 767.5 | 6-DaHall 1-PDU-09 | [branch#043] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#027] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#028] [A] kWh last month | 894 | 6-DaHall 1-PDU-09 | [branch#045] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#029] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#030] [A] kWh last month | 1005 | 6-DaHall 1-PDU-09 | [branch#047] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#031] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-12 | [branch#032] [A] kWh last month | 467.4 | 6-DaHall 1-PDU-09 | [branch#049] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-09 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#003] [A] kWh last month | 862.6 | 6-DaHall 1-PDU-10 | [branch#002] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#005] [A] kWh last month | 568.5 | 6-DaHall 1-PDU-10 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#006] [A] kWh last month | 888.8 | 6-DaHall 1-PDU-10 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#008] [A] kWh last month | 595.2 | 6-DaHall 1-PDU-10 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#008] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#010] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#011] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#013] [A] kWh last month | 68.3 | 6-DaHall 1-PDU-10 | [branch#012] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#014] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#013] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#014] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#016] [A] kWh last month | 610.6 | 6-DaHall 1-PDU-10 | [branch#015] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#016] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#017] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#019] [A] kWh last month | 868.8 | 6-DaHall 1-PDU-10 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#020] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#019] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#021] [A] kWh last month | 413.2 | 6-DaHall 1-PDU-10 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#023] [A] kWh last month | 1452.3 | 6-DaHall 1-PDU-10 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#025] [A] kWh last month | 371.8 | 6-DaHall 1-PDU-10 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#026] [A] kWh last month | 262.8 | 6-DaHall 1-PDU-10 | [branch#025] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#027] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#028] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#027] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#029] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#030] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#029] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#031] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-13 | [branch#032] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#031] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#001] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#002] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#003] [A] kWh last month | 457 | 6-DaHall 1-PDU-10 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#004] [A] kWh last month | 1046.5 | 6-DaHall 1-PDU-10 | [branch#035] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#006] [A] kWh last month | 411.3 | 6-DaHall 1-PDU-10 | [branch#037] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#007] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#008] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#039] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#009] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#010] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#041] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#012] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#043] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#013] [A] kWh last month | 234.9 | 6-DaHall 1-PDU-10 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#014] [A] kWh last month | 502.5 | 6-DaHall 1-PDU-10 | [branch#045] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#047] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#017] [A] kWh last month | 116.9 | 6-DaHall 1-PDU-10 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-10 | [branch#049] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#019] [A] kWh last month | 378.8 | 6-DaHall 1-PDU-10 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#020] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#021] [A] kWh last month | 536.2 | 6-DaHall 1-PDU-11 | [branch#002] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#023] [A] kWh last month | 391.7 | 6-DaHall 1-PDU-11 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#024] [A] kWh last month | 776.1 | 6-DaHall 1-PDU-11 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#027] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#008] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#028] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#029] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#010] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#030] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#011] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#031] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#012] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-14 | [branch#032] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#013] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#001] [A] kWh last month | 2154.5 | 6-DaHall 1-PDU-11 | [branch#014] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#002] [A] kWh last month | 1255.7 | 6-DaHall 1-PDU-11 | [branch#015] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#016] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#017] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#006] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#019] [A] kWh last month | 806
|  |  | 5-DaHall 1-PDU-15 | [branch#007] [A] kWh last month | 561.7 | 6-DaHall 1-PDU-11 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#008] [A] kWh last month | 600.6 | 6-DaHall 1-PDU-11 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#009] [A] kWh last month | 203.6 | 6-DaHall 1-PDU-11 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#010] [A] kWh last month | 1074.7 | 6-DaHall 1-PDU-11 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#011] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#012] [A] kWh last month | 293.6 | 6-DaHall 1-PDU-11 | [branch#025] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#013] [A] kWh last month | 92.7 | 6-DaHall 1-PDU-11 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#014] [A] kWh last month | 170.5 | 6-DaHall 1-PDU-11 | [branch#027] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#015] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#029] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#017] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#031] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#020] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#021] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#022] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#035] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#023] [A] kWh last month | 350.8 | 6-DaHall 1-PDU-11 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#024] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#037] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#025] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#039] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#027] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#028] [A] kWh last month | 75.7 | 6-DaHall 1-PDU-11 | [branch#041] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#029] [A] kWh last month | 22.1 | 6-DaHall 1-PDU-11 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-15 | [branch#030] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#043] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#001] [A] kWh last month | 1630.1 | 6-DaHall 1-PDU-11 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#002] [A] kWh last month | 1246.9 | 6-DaHall 1-PDU-11 | [branch#045] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#003] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#004] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#047] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#005] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#006] [A] kWh last month | 0 | 6-DaHall 1-PDU-11 | [branch#049] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#007] [A] kWh last month | 599.1 | 6-DaHall 1-PDU-11 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#008] [A] kWh last month | 676.2 | 6-DaHall 1-PDU-12 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#009] [A] kWh last month | 213.2 | 6-DaHall 1-PDU-12 | [branch#002] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#010] [A] kWh last month | 26.3 | 6-DaHall 1-PDU-12 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#011] [A] kWh last month | 0.1 | 6-DaHall 1-PDU-12 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#012] [A] kWh last month | 306.8 | 6-DaHall 1-PDU-12 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#013] [A] kWh last month | 251.9 | 6-DaHall 1-PDU-12 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#014] [A] kWh last month | 197.9 | 6-DaHall 1-PDU-12 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#015] [A] kWh last month | 379.3 | 6-DaHall 1-PDU-12 | [branch#008] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#016] [A] kWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#017] [A] kWh last month | 241.4 | 6-DaHall 1-PDU-12 | [branch#010] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#018] [A] kWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#011] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#019] [A] kWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#012] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#020] [A] kWh last month | 78.1 | 6-DaHall 1-PDU-12 | [branch#013] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#021] [A] kWh last month | 40 | 6-DaHall 1-PDU-12 | [branch#014] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#022] [A] kWh last month | 77.7 | 6-DaHall 1-PDU-12 | [branch#015] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#023] [A] kWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#016] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#024] [A] kWh last month | 215.8 | 6-DaHall 1-PDU-12 | [branch#017] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#025] [A] kWh last month | 57.3 | 6-DaHall 1-PDU-12 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#026] [A] kWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#019] [A] kWh last month | 802.3
|  |  | 5-DaHall 1-PDU-16 | [branch#027] [A] kWh last month | 224.4 | 6-DaHall 1-PDU-12 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#028] [A] kWh last month | 20.8 | 6-DaHall 1-PDU-12 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#029] [A] kWh last month | 338.3 | 6-DaHall 1-PDU-12 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-16 | [branch#030] [A] kWh last month | 40.7 | 6-DaHall 1-PDU-12 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 0119 [branch#01] [A] KWh last month | 86 | 6-DaHall 1-PDU-12 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 0279 [branch#02] [A] KWh last month | 113.5 | 6-DaHall 1-PDU-12 | [branch#025] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 0439 [branch#03] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 0599 [branch#04] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#027] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 0759 [branch#05] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 0919 [branch#06] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#029] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 1079 [branch#07] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 1239 [branch#08] [A] KWh last month | 319.9 | 6-DaHall 1-PDU-12 | [branch#031] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 1399 [branch#09] [A] KWh last month | 1115.4 | 6-DaHall 1-PDU-12 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 1559 [branch#10] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 1719 [branch#11] [A] KWh last month | 69.2 | 6-DaHall 1-PDU-12 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 1879 [branch#12] [A] KWh last month | 160 | 6-DaHall 1-PDU-12 | [branch#035] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 2039 [branch#13] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 2199 [branch#14] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#037] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 2359 [branch#15] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 2519 [branch#16] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#039] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 2679 [branch#17] [A] KWh last month | 78.4 | 6-DaHall 1-PDU-12 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 2839 [branch#18] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#041] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 2999 [branch#19] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 3159 [branch#20] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#043] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 3319 [branch#21] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 3479 [branch#22] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#045] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 3639 [branch#23] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 3799 [branch#24] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#047] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 3959 [branch#25] [A] KWh last month | 244.5 | 6-DaHall 1-PDU-12 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 4119 [branch#26] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#049] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 4279 [branch#27] [A] KWh last month | 0 | 6-DaHall 1-PDU-12 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 4439 [branch#28] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 4599 [branch#29] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#002] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 4759 [branch#30] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 4919 [branch#31] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 5079 [branch#32] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 5239 [branch#33] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-17 | 5399 [branch#34] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 0119 [branch#01] [A] KWh last month | 102 | 6-DaHall 1-PDU-13 | [branch#008] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 0279 [branch#02] [A] KWh last month | 106.1 | 6-DaHall 1-PDU-13 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 0439 [branch#03] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#010] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 0599 [branch#04] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#011] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 0759 [branch#05] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#012] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 0919 [branch#06] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#013] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 1079 [branch#07] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#014] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 1239 [branch#08] [A] KWh last month | 309.8 | 6-DaHall 1-PDU-13 | [branch#015] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 1399 [branch#09] [A] KWh last month | 746.1 | 6-DaHall 1-PDU-13 | [branch#016] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 1559 [branch#10] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#017] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 1719 [branch#11] [A] KWh last month | 50.9 | 6-DaHall 1-PDU-13 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 1879 [branch#12] [A] KWh last month | 141.5 | 6-DaHall 1-PDU-13 | [branch#019] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 2039 [branch#13] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 2199 [branch#14] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 2359 [branch#15] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 2519 [branch#16] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 2679 [branch#17] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 2839 [branch#18] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#025] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 2999 [branch#19] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 3159 [branch#20] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#027] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 3319 [branch#21] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 3479 [branch#22] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#029] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 3639 [branch#23] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 3799 [branch#24] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#031] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 3959 [branch#25] [A] KWh last month | 72.5 | 6-DaHall 1-PDU-13 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 4119 [branch#26] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 4279 [branch#27] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 4439 [branch#28] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#035] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 4599 [branch#29] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 4759 [branch#30] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#037] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 4919 [branch#31] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 5079 [branch#32] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#039] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 5239 [branch#33] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-18 | 5399 [branch#34] [A] KWh last month | 0 | 6-DaHall 1-PDU-13 | [branch#041] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 0119 [branch#01] [A] KWh last month | 683.5 | 6-DaHall 1-PDU-13 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 0279 [branch#02] [A] KWh last month | 509.5 | 6-DaHall 1-PDU-13 | [branch#043] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 0439 [branch#03] [A] KWh last month | 671.8 | 6-DaHall 1-PDU-13 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 0599 [branch#04] [A] KWh last month | 431.7 | 6-DaHall 1-PDU-13 | [branch#045] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 0759 [branch#05] [A] KWh last month | 550.6 | 6-DaHall 1-PDU-13 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 0919 [branch#06] [A] KWh last month | 495.4 | 6-DaHall 1-PDU-13 | [branch#047] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 1079 [branch#07] [A] KWh last month | 917.5 | 6-DaHall 1-PDU-13 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 1239 [branch#08] [A] KWh last month | 811.8 | 6-DaHall 1-PDU-13 | [branch#049] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 1399 [branch#09] [A] KWh last month | 568.9 | 6-DaHall 1-PDU-13 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 1559 [branch#10] [A] KWh last month | 808.6 | 6-DaHall 1-PDU-13 | [branch#051] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 1719 [branch#11] [A] KWh last month | 490.7 | 6-DaHall 1-PDU-13 | [branch#052] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 1879 [branch#12] [A] KWh last month | 543.6 | 6-DaHall 1-PDU-13 | [branch#053] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 2039 [branch#13] [A] KWh last month | 614.5 | 6-DaHall 1-PDU-13 | [branch#054] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 2199 [branch#14] [A] KWh last month | 226.8 | 6-DaHall 1-PDU-14 | [branch#001] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 2359 [branch#15] [A] KWh last month | 938.7 | 6-DaHall 1-PDU-14 | [branch#002] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 2519 [branch#16] [A] KWh last month | 1093 | 6-DaHall 1-PDU-14 | [branch#003] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 2679 [branch#17] [A] KWh last month | 562.6 | 6-DaHall 1-PDU-14 | [branch#004] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 2839 [branch#18] [A] KWh last month | 901.8 | 6-DaHall 1-PDU-14 | [branch#005] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 2999 [branch#19] [A] KWh last month | 577.6 | 6-DaHall 1-PDU-14 | [branch#006] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 3159 [branch#20] [A] KWh last month | 1102 | 6-DaHall 1-PDU-14 | [branch#007] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 3319 [branch#21] [A] KWh last month | 0 | 6-DaHall 1-PDU-14 | [branch#008] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 3479 [branch#22] [A] KWh last month | 1365.1 | 6-DaHall 1-PDU-14 | [branch#009] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 3639 [branch#23] [A] KWh last month | 0 | 6-DaHall 1-PDU-14 | [branch#010] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-19 | 3799 [branch#24] [A] KWh last month | 0 | 6-DaHall 1-PDU-14 | [branch#011] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 0119 [branch#01] [A] KWh last month | 690 | 6-DaHall 1-PDU-14 | [branch#012] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 0279 [branch#02] [A] KWh last month | 641.9 | 6-DaHall 1-PDU-14 | [branch#013] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 0439 [branch#03] [A] KWh last month | 644.5 | 6-DaHall 1-PDU-14 | [branch#014] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 0599 [branch#04] [A] KWh last month | 418.7 | 6-DaHall 1-PDU-14 | [branch#015] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 0759 [branch#05] [A] KWh last month | 547.2 | 6-DaHall 1-PDU-14 | [branch#016] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 0919 [branch#06] [A] KWh last month | 312.1 | 6-DaHall 1-PDU-14 | [branch#017] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 1079 [branch#07] [A] KWh last month | 929 | 6-DaHall 1-PDU-14 | [branch#018] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 1239 [branch#08] [A] KWh last month | 840.2 | 6-DaHall 1-PDU-14 | [branch#019] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 1399 [branch#09] [A] KWh last month | 554.6 | 6-DaHall 1-PDU-14 | [branch#020] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 1559 [branch#10] [A] KWh last month | 788.5 | 6-DaHall 1-PDU-14 | [branch#021] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 1719 [branch#11] [A] KWh last month | 373.6 | 6-DaHall 1-PDU-14 | [branch#022] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 1879 [branch#12] [A] KWh last month | 522.4 | 6-DaHall 1-PDU-14 | [branch#023] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 2039 [branch#13] [A] KWh last month | 566.3 | 6-DaHall 1-PDU-14 | [branch#024] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 2199 [branch#14] [A] KWh last month | 208.6 | 6-DaHall 1-PDU-14 | [branch#025] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 2359 [branch#15] [A] KWh last month | 1029.1 | 6-DaHall 1-PDU-14 | [branch#026] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 2519 [branch#16] [A] KWh last month | 1111.2 | 6-DaHall 1-PDU-14 | [branch#027] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 2679 [branch#17] [A] KWh last month | 619.5 | 6-DaHall 1-PDU-14 | [branch#028] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 2839 [branch#18] [A] KWh last month | 867.6 | 6-DaHall 1-PDU-14 | [branch#029] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 2999 [branch#19] [A] KWh last month | 596 | 6-DaHall 1-PDU-14 | [branch#030] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 3159 [branch#20] [A] KWh last month | 190.1 | 6-DaHall 1-PDU-14 | [branch#031] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 3319 [branch#21] [A] KWh last month | 0 | 6-DaHall 1-PDU-14 | [branch#032] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 3479 [branch#22] [A] KWh last month | 443.1 | 6-DaHall 1-PDU-14 | [branch#033] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 3639 [branch#23] [A] KWh last month | 0 | 6-DaHall 1-PDU-14 | [branch#034] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-20 | 3799 [branch#24] [A] KWh last month | 0 | 6-DaHall 1-PDU-14 | [branch#035] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 0119 [branch#01] [A] KWh last month | 540.9 | 6-DaHall 1-PDU-14 | [branch#036] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 0279 [branch#02] [A] KWh last month | 422.3 | 6-DaHall 1-PDU-14 | [branch#037] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 0439 [branch#03] [A] KWh last month | 662.3 | 6-DaHall 1-PDU-14 | [branch#038] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 0599 [branch#04] [A] KWh last month | 396.8 | 6-DaHall 1-PDU-14 | [branch#039] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 0759 [branch#05] [A] KWh last month | 977.1 | 6-DaHall 1-PDU-14 | [branch#040] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 0919 [branch#06] [A] KWh last month | 695.9 | 6-DaHall 1-PDU-14 | [branch#041] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 1079 [branch#07] [A] KWh last month | 533.4 | 6-DaHall 1-PDU-14 | [branch#042] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 1239 [branch#08] [A] KWh last month | 918 | 6-DaHall 1-PDU-14 | [branch#043] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 1399 [branch#09] [A] KWh last month | 709.8 | 6-DaHall 1-PDU-14 | [branch#044] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 1559 [branch#10] [A] KWh last month | 1115.7 | 6-DaHall 1-PDU-14 | [branch#045] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 1719 [branch#11] [A] KWh last month | 504 | 6-DaHall 1-PDU-14 | [branch#046] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 1879 [branch#12] [A] KWh last month | 257.8 | 6-DaHall 1-PDU-14 | [branch#047] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 2039 [branch#13] [A] KWh last month | 813.2 | 6-DaHall 1-PDU-14 | [branch#048] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 2199 [branch#14] [A] KWh last month | 329.8 | 6-DaHall 1-PDU-14 | [branch#049] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 2359 [branch#15] [A] KWh last month | 529.4 | 6-DaHall 1-PDU-14 | [branch#050] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 2519 [branch#16] [A] KWh last month | 1403.5 | 6-DaHall 1-PDU-14 | [branch#051] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 2679 [branch#17] [A] KWh last month | 675.9 | 6-DaHall 1-PDU-14 | [branch#052] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 2839 [branch#18] [A] KWh last month | 826.5 | 6-DaHall 1-PDU-14 | [branch#053] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 2999 [branch#19] [A] KWh last month | 589.4 | 6-DaHall 1-PDU-14 | [branch#054] [A] kWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 3159 [branch#20] [A] KWh last month | 1198.5
|  |  | 5-DaHall 1-PDU-21 | 3319 [branch#21] [A] KWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 3479 [branch#22] [A] KWh last month | 1193.5
|  |  | 5-DaHall 1-PDU-21 | 3639 [branch#23] [A] KWh last month | 0
|  |  | 5-DaHall 1-PDU-21 | 3799 [branch#24] [A] KWh last month | 0
|  |  | 5-DaHall 1-PDU-22 | 0119 [branch#01] [A] KWh last month | 593.5
|  |  | 5-DaHall 1-PDU-22 | 0279 [branch#02] [A] KWh last month | 405.7
|  |  | 5-DaHall 1-PDU-22 | 0439 [branch#03] [A] KWh last month | 674
|  |  | 5-DaHall 1-PDU-22 | 0599 [branch#04] [A] KWh last month | 342.5
|  |  | 5-DaHall 1-PDU-22 | 0759 [branch#05] [A] KWh last month | 892.5
|  |  | 5-DaHall 1-PDU-22 | 0919 [branch#06] [A] KWh last month | 385.8
|  |  | 5-DaHall 1-PDU-22 | 1079 [branch#07] [A] KWh last month | 518.8
|  |  | 5-DaHall 1-PDU-22 | 1239 [branch#08] [A] KWh last month | 979.2
|  |  | 5-DaHall 1-PDU-22 | 1399 [branch#09] [A] KWh last month | 694.9
|  |  | 5-DaHall 1-PDU-22 | 1559 [branch#10] [A] KWh last month | 1135.6
|  |  | 5-DaHall 1-PDU-22 | 1719 [branch#11] [A] KWh last month | 535.2
|  |  | 5-DaHall 1-PDU-22 | 1879 [branch#12] [A] KWh last month | 260.2
|  |  | 5-DaHall 1-PDU-22 | 2039 [branch#13] [A] KWh last month | 765
|  |  | 5-DaHall 1-PDU-22 | 2199 [branch#14] [A] KWh last month | 340.8
|  |  | 5-DaHall 1-PDU-22 | 2359 [branch#15] [A] KWh last month | 641
|  |  | 5-DaHall 1-PDU-22 | 2519 [branch#16] [A] KWh last month | 1457.3
|  |  | 5-DaHall 1-PDU-22 | 2679 [branch#17] [A] KWh last month | 586.2
|  |  | 5-DaHall 1-PDU-22 | 2839 [branch#18] [A] KWh last month | 782.8
|  |  | 5-DaHall 1-PDU-22 | 2999 [branch#19] [A] KWh last month | 568.5
|  |  | 5-DaHall 1-PDU-22 | 3159 [branch#20] [A] KWh last month | 242.6
|  |  | 5-DaHall 1-PDU-22 | 3319 [branch#21] [A] KWh last month | 0
|  |  | 5-DaHall 1-PDU-22 | 3479 [branch#22] [A] KWh last month | 596.4
|  |  | 5-DaHall 1-PDU-22 | 3639 [branch#23] [A] KWh last month | 0
|  |  | 5-DaHall 1-PDU-22 | 3799 [branch#24] [A] KWh last month | 0

## 8층 사무실 분전반 (hidden)
2023 년 9 월 25 일
Main CB 4P 100A
8층 사무실 창고 : UPS 출력(From:7F 창고)
[10 empty] | MAIN 계측값 : | 3.1 | 2.7 | 7.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
DEK LOC #01 | O | ON | 1.5 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 1.6 |  |  |  | O | ON | SECURITY #02
DEK LOC #03 | O | ON |  | 1.2 |  |  | 2P 30A | #03 | #04 | 2P 30A |  |  |  |  | O | OFF | KIOSK #04
DEK LOC #05 | O | ON |  |  | 2.2 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 3 |  | O | ON | RACK #06
| X | OFF |  |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | ON | 통합경보반 #08
| X | OFF |  |  |  |  | 2P 30A | #09 | #10 | 2P 30A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 2P 30A | #11 | #12 | 2P 30A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 2P 30A | #13 | #14 | 2P 30A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 2P 30A | #15 | #16 | 2P 30A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 2P 30A | #17 | #18 | 2P 30A |  |  |  |  | X | OFF | SELABLE #18
SJT 모니터 #19 | O | ON | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A |  |  |  |  | X | OFF | SELABLE #20
STJ 사무실 # 21 | O | ON |  | 1.7 |  |  | 2P 30A | #21 | #22 | 2P 30A |  |  |  |  | X | OFF | SELABLE #22
SJT (SERVER) # 23 | O | ON |  |  | 2.6 |  | 2P 30A | #21 | #22 | 2P 30A |  |  |  |  | X | OFF | SELABLE #24
[10 empty] | 총합: | 3.1 | 2.9 | 7.8
Main CB 4P 100A
8층 복도 : 에어컨 분전함 (From:6층 보조항온항습기 분전반)
[10 empty] | MAIN 계측값 : | 2.3 | 2.2 | 7.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
사무실, 회의실 실외기 | O | ON | 0.3 | 0.3 | 0.3 | 0.1 | 3P 50A | #01 | #02 | 3P 50A | 2.6 | 2.6 | 2.7 | 0.1 | O | ON | 임대오피스 실외기
사무실 외의실 실내기 | O | ON | 0.2 |  |  |  | 2P 30A | #03 | #04 | 2P 30A |  |  |  |  | X | OFF
실외기실 동파방지열선 | O | ON |  | 0 |  |  | 2P 30A | #05 | #06 | 2P 30A |  | 0.3 |  |  | O | ON | 임대오피스 실내기
| X | OFF |  |  |  |  | 2P 30A | #07 | #08 | 2P 30A |  |  | 5.4 |  | O | ON | SJT 에어컨
[10 empty] | 총합: | 3.1 | 3.2 | 8.4

## 7층_부하량(월간_MIN)
Date : 2023-11-01 ~ 2023-11-30
7-DaHall 1-RPP-01 |  |  | PDU : 7-DaHall 1-RPP-01 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 26 | 14 | 21.8 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
W-DCS 8000 | O | ON | 0 |  |  |  | 2P 20A | #01 | 전송 |  | #02 | 2P 30A | 0 |  |  |  | O | ON | TO 8F 보안실 UPS항온 항습기 모니터용PC
?? | O | ON |  | 0 |  |  | 2P 20A | #03 | 전송 | 넷피플 | #04 | 2P 30A |  | 0 |  |  | O | ON | E-4-B
?? | O | ON |  |  | 0 |  | 2P 20A | #05 | 전송 | 넷피플 | #06 | 2P 30A |  |  | 0 |  | O | OFF | E-3-B
517 BAY | O | ON | 0 |  |  |  | 2P 20A | #07 | 전송 | 전송 | #08 | 2P 30A | 0 |  |  |  | O | ON | 406BAY 405BAY DCN-1B
Voice사업팀 MMS용-B | X | OFF |  | 0 |  |  | 2P 20A | #09 | IDC | 전송 | #10 | 2P 30A |  | 0.99 |  |  | O | ON | 407BAY 406BAY DCN-2B
Voice사업팀 D-7 RACK | O | ON |  |  | 0 |  | 2P 20A | #11 | 니즈텔레콤 | 전송 | #12 | 2P 30A |  |  | 1.45 |  | O | ON | 408BAY 407BAY DCN-3B
ONS1064 SERVER | O | ON | 0 |  |  |  | 2P 20A | #13 | 전송 | 엑사넷 | #14 | 2P 30A | 3.11 |  |  |  | O | ON | E-8-B
NTT 하-1 | X | ON |  | 0 |  |  | 2P 20A | #15 | IDC | 델피콤 | #16 | 2P 30A |  | 2.5 |  |  | O | ON | F-5-B
8층 보안실 CCTV 모니터 | O | ON |  |  | 0 |  | 2P 20A | #17 | 공통 | CARANG ('23.09.19) | #18 | 2P 30A |  |  | 0 |  | O | ON | C604 / F-7-A
G-10-A | O | ON | 0.99 |  |  |  | 2P 20A | #19 | 신한금융투자 | IDC | #20 | 2P 30A | 0 |  |  |  | O | ON | 인터넷운영팀MAN RACK#2 전원A
NTT 하-3 | X | OFF |  | 0 |  |  | 2P 20A | #21 |  | NTT | #22 | 2P 30A |  | 0 |  |  | O | ON | G-4-B
C-7-A-Q1 | O | ON |  |  | 0 |  | 2P 20A | #23 | NTT | NTT | #24 | 2P 30A |  |  | 0 |  | O | ON | G-6-B
인터넷운영팀MAN RACK#2 전원B | O | ON | 1.5 |  |  |  | 2P 20A | #25 | IDC | 교환라우터(총무팀 ??) | #26 | 2P 30A | 0 |  |  |  | O | ON | F-3-B
NMS B-15 | O | ON |  | 2.96 |  |  | 2P 20A | #27 | 전송 | 공통 | #28 | 2P 30A |  | 0.87 |  |  | O | ON | 운용실콘센트
NMS B-16 | O | ON |  |  | 1.29 |  | 2P 20A | #29 | 전송 | 공통 | #30 | 2P 30A |  |  | 1.5 |  | O | ON | 운용실콘센트 창가1열
?? | O | ON | 0 |  |  |  | 2P 20A | #31 | 전송 | 전송 | #32 | 2P 30A | 0 |  |  |  | O | ON | 전산랙 410BAY(B)
G-5-B | O | ON |  | 0 |  |  | 2P 20A | #33 | NTT | 니즈텔레콤 | #34 | 2P 30A |  | 0 |  |  | O | OFF | D-6-B
G-1-B | O | ON |  |  | 0 |  | 2P 20A | #35 |  | 르네트 | #36 | 2P 30A |  |  | 0 |  | O | ON | E-9-B
C-7-B-Q1 | O | ON | 0 |  |  |  | 2P 20A | #37 | NTT | 니즈텔레콤 | #38 | 2P 30A | 0 |  |  |  | O | ON | D-7-B
G-2-B | O | ON |  | 0 |  |  | 2P 20A | #39 |  | IDC | #40 | 2P 30A |  | 0 |  |  | O | ON | 341BAY / IDC MAN POP AC전원(B)
[12 empty] | 총합: | 5.6 | 7.32 | 4.24
7-DaHall 1-PDU-02 |  |  | PDU : 7-DaHall 1-PDU-02 | [5 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 30.2 | 45.2 | 46.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
G-3-B (NTT#8-B) | O | ON |  | 0 |  |  | 2P 30A | #01 | NTT | 쿼드마이너 | #02 | 2P 30A |  | 0 |  |  | O | ON | C503 | 쿼드마이너 예약상면
7B-342BAY | O | ON |  |  | 0 |  | 2P 30A | #03 | 인터넷 IP 랙 |  | #04 | 2P 30A |  |  | 0 |  | O | ON | U3-7B-D1
| X | OFF | 0 |  |  |  | 2P 30A | #05 |  | NTT | #06 | 2P 30A | 0 |  |  |  | O | ON | U3-7B-D5 B
241BAY-B | O | ON |  | 5.24 |  |  | 2P 30A | #07 |  | 전송 | #08 | 2P 30A |  | 0 |  |  | O | ON | U3-7B-337
242BAY-B | O | ON |  |  | 3.26 |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  |  | 2.82 |  | O | ON | 7F-C-6-NTT#3-B
209Bay - B | O | ON | 4 |  |  |  | 2P 30A | #11 |  | NTT | #12 | 2P 30A | 0 |  |  |  | O | ON | U3-7B G-3-B
210Bay - B | O | ON |  | 2.33 |  |  | 2P 30A | #13 |  | DEKR Network Rack | #14 | 2P 30A |  | 2.97 |  |  | O | ON | 218Bay - A전원 ('22.01.12 투입)
TATA#1/B | O | ON |  |  | 1.08 |  | 2P 30A | #15 | TATA | DEKR Network Rack | #16 | 2P 30A |  |  | 2.38 |  | O | ON | 217Bay - A전원 ('22.01.12 투입)
208BAY-B | O | ON | 3.26 |  |  |  | 2P 30A | #17 |  | 318Bay - DEK Network Rack | #18 | 2P 30A | 1.74 |  |  |  | O | ON | 318BAY-B U3-7B-18
207BAY-B | O | ON |  | 0 |  |  | 2P 30A | #19 |  | 317Bay - DEK Network Rack | #20 | 2P 30A |  | 1.84 |  |  | O | ON | 317BAY-B U3-7B-20
206BAY-B | O | ON |  |  | 0 |  | 2P 30A | #21 |  | 316Bay - DEK Network Rack | #22 | 2P 30A |  |  | 0 |  | O | ON | 316BAY-B U3-7B-22
205BAY-B | O | ON | 0 |  |  |  | 2P 30A | #23 |  | 315Bay - DEK Network Rack | #24 | 2P 30A | 0 |  |  |  | O | ON | 315BAY-B U3-7B-24
204BAY-B | O | ON |  | 0.89 |  |  | 2P 30A | #25 |  | 314Bay - DEK Network Rack | #26 | 2P 30A |  | 0.56 |  |  | O | ON | 314BAY-B U3-7B-26
208BAY-B(2) | O | ON |  |  | 0.23 |  | 2P 30A | #27 |  | 313Bay - DEK Network Rack | #28 | 2P 30A |  |  | 0 |  | O | ON | 313BAY-B U3-7B-28
C604 / F-7-B | O | ON | 0 |  |  |  | 2P 30A | #29 | CARANG ('23.09.19) | 드림라인 | #30 | 2P 30A | 0 |  |  |  | O | ON | 301BAY U3-7B-30
U3-7B-31 B-6-B | O | ON |  | 0 |  |  | 2P 30A | #31 | 세종 인터넷(클라우드이음) | 203Bay - 세종-아톤AWS | #32 | 2P 30A |  | 1.89 |  |  | O | ON | 203Bay-B ('22.07.14 투입) U3-7B-32
B-7-B | O | ON |  |  | 0 |  | 2P 30A | #33 | 세종 인터넷(클라우드이음) | C909 (舊 C-02) / TATA#02 | #34 | 2P 30A |  |  | 0 |  | O | ON | C-02(C909-B) U3-7B-34
B-8-B | O | ON | 2.92 |  |  |  | 2P 30A | #35 | 세종 인터넷(클라우드이음) |  | #36 | 2P 30A | 0 |  |  |  | O | ON | B424(310BAY-B)
Test Bed #2 U3-7B-37 | O | ON |  | 0 |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  | 1.91 |  |  | O | ON | B423(311BAY-B)
7-1-B2-30-39 | O | ON |  |  | 1.83 |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  |  | 2.82 |  | O | ON | B422(312BAY-B)
7B-30-41(C409) | O | ON | 0 |  |  |  | 2P 30A | #41 | C409 |  | #42 | 2P 30A | 0.52 |  |  |  | O | ON | 7-1-B2-30-42
| X | OFF |  | 0 |  |  | 2P 30A | #43 |  | 쿼드마이너 | #44 | 2P 30A |  | 0 |  |  | O | ON | C502 | 2023/04/10 랙 반입 예정
| X | OFF |  |  | 0 |  | 2P 30A | #45 |  | 쿼드마이너 | #46 | 2P 30A |  |  | 0 |  | O | ON | C504 | 쿼드마이너 예약상면
| X | OFF | 0 |  |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A | 1.9 |  |  |  | X | OFF
신규BMS(20F TPS실) Rack | O | ON |  | 0.88 |  |  | 2P 30A | #49 | 20F BMS |  | #50 | 2P 30A |  | 0 |  |  | O | ON | 7층 출입카드
신규BMS(7F TPS실) Rack | O | ON |  |  | 0.55 |  | 2P 30A | #51 | 7F BMS |  | #52 | 2P 30A |  |  | 0 |  | O | ON | 20F MAIN (FMS)
7B-D5-#1 | O | ON | 0 |  |  |  | 2P 30A | #53 | NTT |  | #54 | 2P 30A | 0 |  |  |  | O | ON | 7F MAIN (FMS)
[12 empty] | 총합: | 14.34 | 18.51 | 14.97 | 0
7-DaHall 1-PDU-01 |  |  | PDU : 7-DaHall 1-PDU-01 | [5 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 33.4 | 43.4 | 40.1 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
G-3-A (NTT#8-A) | O | ON |  | 0 |  |  | 2P 30A | #01 | NTT | 쿼드마이너 | #02 | 2P 30A |  | 0 |  |  | O | ON | G-8-A (C503) | 쿼드마이너 예약상면
F-5-A | O | ON |  |  | 2.07 |  | 2P 30A | #03 | 텔피콤 |  | #04 | 2P 30A |  |  | 0 |  | O | ON | D-1-A
7A-342BAY | O | ON | 4.88 |  |  |  | 2P 30A | #05 | 인터넷 IP 랙 | NTT | #06 | 2P 30A | 0 |  |  |  | O | ON | D-5-A
241BAY-A | O | ON |  | 5.95 |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  | 0.79 |  |  | O | ON | 405BAY / U3-7A-405BAY(A)
242BAY-A | O | ON |  |  | 2.78 |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  |  | 2.08 |  | O | ON | C-6-A
209Bay - A | O | ON | 4.15 |  |  |  | 2P 30A | #11 | 인터넷 IP 랙 | NTT | #12 | 2P 30A | 0 |  |  |  | O | ON | U3-7A G-3-A
210Bay - A | O | ON |  | 2.02 |  |  | 2P 30A | #13 | 인터넷 IP 랙 | DEKR Network Rack | #14 | 2P 30A |  | 3.2 |  |  | O | ON | 218Bay - A전원 ('22.01.12 투입)
TATA#1/A | O | ON |  |  | 0 |  | 2P 30A | #15 | TATA | DEKR Network Rack | #16 | 2P 30A |  |  | 1.65 |  | O | ON | 217Bay - A전원 ('22.01.12 투입)
208BYA-A | O | ON | 2.76 |  |  |  | 2P 30A | #17 | 인터넷 IP 랙 | 318Bay - DEK Network Rack | #18 | 2P 30A | 1.75 |  |  |  | O | ON | 318BAY-A U3-7A-18
207BYA-A | O | ON |  | 0 |  |  | 2P 30A | #19 | 인터넷 IP 랙 | 317Bay - DEK Network Rack | #20 | 2P 30A |  | 0.9 |  |  | O | ON | 317BAY-A U3-7A-20
206BYA-A | O | ON |  |  | 1.06 |  | 2P 30A | #21 | 인터넷 IP 랙 | 316Bay - DEK Network Rack | #22 | 2P 30A |  |  | 0 |  | O | ON | 316BAY-A U3-7A-22
205BYA-A | O | ON | 0 |  |  |  | 2P 30A | #23 | 인터넷 IP 랙 | 315Bay - DEK Network Rack | #24 | 2P 30A | 0 |  |  |  | O | ON | 315BAY-A U3-7A-24
204BYA-A | O | ON |  | 0 |  |  | 2P 30A | #25 | 인터넷 IP 랙 | 314Bay - DEK Network Rack | #26 | 2P 30A |  | 0 |  |  | O | ON | 314BAY-A U3-7A-26
208BAY 207BAY - A(2) | O | ON |  |  | 0 |  | 2P 30A | #27 | 인터넷 IP 랙 | 313Bay - DEK Network Rack | #28 | 2P 30A |  |  | 0 |  | O | ON | 313BAY-A U3-7A-28
322BAY 331BAY | O | ON | 0 |  |  |  | 2P 30A | #29 | 김종원M 요구회로 | 드림라인 | #30 | 2P 30A | 0 |  |  |  | O | ON | 301BAY U3-7A-30
U3-7A-31 B-6-A | O | ON |  | 1.54 |  |  | 2P 30A | #31 | 세종 인터넷(클라우드이음) | 203Bay - 세종-아톤AWS | #32 | 2P 30A |  | 2.1 |  |  | O | ON | 203Bay-A ('22.07.14 투입) U3-7A-32
B-7-A | O | ON |  |  | 0 |  | 2P 30A | #33 | 세종 인터넷(클라우드이음) | C909 (舊 C-02) / TATA#02 | #34 | 2P 30A |  |  | 0 |  | O | ON | C-02(C909-A) U3-7A-34
B-8-A | O | ON | 2.27 |  |  |  | 2P 30A | #35 | 세종 인터넷(클라우드이음) |  | #36 | 2P 30A | 0 |  |  |  | O | ON | B424(310BAY-A)
Test Bed #1 U3-7A-37 | O | ON |  | 0 |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  | 1.71 |  |  | O | ON | B423(311BAY-A)
7-1-A2-30-39 | O | ON |  |  | 1.03 |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  |  | 3.16 |  | O | ON | B422(312BAY-A)
7A-30-41(C409) | O | ON | 1.05 |  |  |  | 2P 30A | #41 | C409 |  | #42 | 2P 30A | 0.35 |  |  |  | O | ON | 7-1-A2-30-42
| X | OFF |  | 0 |  |  | 2P 30A | #43 |  | 쿼드마이너 | #44 | 2P 30A |  | 0 |  |  | O | ON | C502 | 2023/04/10 랙 반입 예정
| X | OFF |  |  | 0 |  | 2P 30A | #45 |  | 쿼드마이너 | #46 | 2P 30A |  |  | 0 |  | O | ON | C504 | 쿼드마이너 예약상면
| X | OFF | 0 |  |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A | 1.71 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #51 |  |  | #52 | 2P 30A |  |  | 0 |  | O | ON | 7F NTT CCTV 전원
| X | OFF | 0 |  |  |  | 2P 30A | #53 |  | NTT | #54 | 2P 30A | 0.34 |  |  |  | O | ON | 7A-D5-#1
[12 empty] | 총합: | 19.26 | 18.21 | 13.83 | 0
7-DaHall 1-RPP-02 |  |  | PDU : 7-DaHall 1-RPP-02 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 39 | 12.5 | 20.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO | NO. | NO. | NO | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
강남방향 창가열 콘센트 | O | ON | 0 |  |  |  | 2P 20A | #01 | 공통 | 공통 | #02 | 2P 30A | 0.54 |  |  |  | O | ON | 정면창가 콘센트
?? | O | ON |  | 0 |  |  | 2P 20A | #03 | 공통 |  | #04 | 2P 30A |  | 0 |  |  | X | OFF | NTT 상-1
301 BAY | O | OFF |  |  | 0 |  | 2P 20A | #05 | 전송 | 전송 | #06 | 2P 30A |  |  | 0 |  | O | ON | GAINS
C2C DWDM EMS RACK | O | ON | 1.11 |  |  |  | 2P 20A | #07 | 전송 | NTT | #08 | 2P 30A | 1.76 |  |  |  | O | ON | C-8-A
405BAY / U3-7A-405BAY(A) | O | ON |  | 0.84 |  |  | 2P 20A | #09 | 전송 | 신한금융투자 | #10 | 2P 30A |  | 0 |  |  | O | ON | G-10-B
ONS1064 SERVER | O | ON |  |  | 0 |  | 2P 20A | #11 | 전송 | NTT | #12 | 2P 30A |  |  | 0 |  | O | ON | C-8-B
406BAY 405 BAY (DCN-1A) | O | ON | 0 |  |  |  | 2P 20A | #13 | 전송 | 유엔시스 | #14 | 2P 30A | 5.68 |  |  |  | O | ON | D-3-A
407BAY 406 BAY (DCN-2A) | O | ON |  | 0 |  |  | 2P 20A | #15 | 전송 | NTT | #16 | 2P 30A |  | 0 |  |  | O | ON | G-4-A (NTT#7)
408BAY 407 BAY (DCN-3A) | O | ON |  |  | 0 |  | 2P 20A | #17 | 전송 | NTT | #18 | 2P 30A |  |  | 0 |  | O | ON | G-6-A
E-2-A | O | ON | 0 |  |  |  | 2P 20A | #19 |  | 교환라우터(총무팀 ??) | #20 | 2P 30A | 0 |  |  |  | O | ON | F-3-A
E-5-A | X | OFF |  | 0 |  |  | 2P 20A | #21 | 니즈텔레콤 | 공통 | #22 | 2P 30A |  | 0 |  |  | O | ON | 운용실 바닥콘센트
E-6-A | O | ON |  |  | 0 |  | 2P 20A | #23 |  | 공통 | #24 | 2P 30A |  |  | 1.44 |  | O | ON | 운용실 콘센트 창가1열
E-7-A | O | ON | 0 |  |  |  | 2P 20A | #25 |  | 전송 | #26 | 2P 30A | 0.3 |  |  |  | O | ON | 전산랙 410 BAY-A
E-8-A | O | ON |  | 5.63 |  |  | 2P 20A | #27 | 엑사넷 | 니즈텔레콤 | #28 | 2P 30A |  | 0 |  |  | O | OFF | D-6-A
G-5-A | O | ON |  |  | 0 |  | 2P 20A | #29 | NTT | 르네트 | #30 | 2P 30A |  |  | 0 |  | O | ON | E-9-A
Voice사업팀 NMS용-A | X | OFF | 0 |  |  |  | 2P 20A | #31 | IDC | 니즈텔레콤 | #32 | 2P 30A | 1.48 |  |  |  | O | ON | D-7-A
NTT 상-3 | X | OFF |  | 0 |  |  | 2P 20A | #33 | IDC |  | #34 | 2P 30A |  | 0 |  |  | O | ON | F-8-A
7F NMS A-18 | O | ON |  |  | 1.72 |  | 2P 20A | #35 | 전송 | 델피콤 | #36 | 2P 30A |  |  | 3.37 |  | O | ON | F-6-A
7F NMS A-19 | O | ON | 0 |  |  |  | 2P 20A | #37 | 전송 | IDC | #38 | 2P 30A | 4.88 |  |  |  | O | ON | 341BAY / IDC MAN POP
7F NMS A-20 | O | ON |  | 2.43 |  |  | 2P 20A | #39 | 전송 |  | #40 | 2P 30A |  | 0 |  |  | O | ON | F-9-A
[12 empty] | 총합: | 15.75 | 8.9 | 6.53
7-DaHall 1-RPP-03 |  |  | PDU : 7-DaHall 1-RPP-03 | [5 empty] | Main CB 4P 225A
[12 empty] | MAIN 계측값 : | 6.8 | 8 | 5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A-1-A [A2-7-1] | O | ON | 1.17 |  |  |  | 2P 50A | #01 | CJ HELLOVISION | NTT | #02 | 2P 50A | 0.94 |  |  |  | O | ON | D-4-A [D3-A]
A-2-A [A2-7-2] | O | ON |  | 2.75 |  |  | 2P 50A | #03 | CJ HELLOVISION | NTT | #04 | 2P 50A |  | 0 |  |  | X | OFF | G-7-A
A-3-A [A2-7-3] | O | ON |  |  | 2.73 |  | 2P 50A | #05 | CJ HELLOVISION | CJ HELLOVISION | #06 | 2P 50A |  |  | 0.94 |  | O | ON | A-7-A [A2-7-7]
A-4-A [A2-7-4] | O | ON | 0 |  |  |  | 2P 50A | #07 | CJ HELLOVISION | CJ HELLOVISION | #08 | 2P 50A | 1.66 |  |  |  | O | ON | A-8-A [A2-7-8]
A-5-A [A2-7-5] | O | ON |  | 2.05 |  |  | 2P 50A | #09 | CJ HELLOVISION | CJ HELLOVISION | #10 | 2P 50A |  | 2.57 |  |  | O | ON | A-6-A [A2-7-6]
[12 empty] | 총합: | 3.77 | 7.37 | 3.67
7-DaHall 1-RPP-04 |  |  | PDU : 7-DaHall 1-RPP-04
[7 empty] | [A] |  | Main CB 4P 225A |  |  | MAIN 계측값 : | 8.6 | 7.6 | 5.7 | <- 실측값
A-1-B [B2-7-1] | O | ON | 1.17 |  |  |  | 2P 50A | #01 | CJ HELLOVISION | NTT | #02 | 2P 50A | 1.47 |  |  |  | O | ON | D-4-B [D3-B]
A-2-B [B2-7-2] | O | ON |  | 3.33 |  |  | 2P 50A | #03 | CJ HELLOVISION | NTT | #04 | 2P 50A |  | 0 |  |  | X | OFF | G-7-B
A-3-B [B2-7-3] | O | ON |  |  | 1.61 |  | 2P 50A | #05 | CJ HELLOVISION | CJ HELLOVISION | #06 | 2P 50A |  |  | 1.2 |  | O | ON | A-7-B [B2-7-7]
A-4-B [B2-7-4] | O | ON | 0 |  |  |  | 2P 50A | #07 | CJ HELLOVISION | CJ HELLOVISION | #08 | 2P 50A | 1.29 |  |  |  | O | ON | A-8-B [B2-7-8]
A-5-B [B2-7-5] | O | ON |  | 1.61 |  |  | 2P 50A | #09 | CJ HELLOVISION | CJ HELLOVISION | #10 | 2P 50A |  | 2.79 |  |  | O | ON | A-6-B [B2-7-6]
[12 empty] | 총합: | 3.93 | 7.73 | 2.81
7-DaHall 1-PDU-03 |  |  | PDU : 7-DaHall 1-PDU-03 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 82.2 | 71.2 | 81.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
7-DaHall 1-RPP-01 | O | ON | 23.68 | 12.05 | 17.05 |  | 4P 225A | #01 | . |  | #02 | 4P 225A | 2.37 | 1.8 | 5.06 |  | O | ON | 8층 Office 분전반(창고)
7-DaHall 1-RPP-03 | O | ON | 0 | 0 | 0 |  | 4P 225A | #03 | . |  | #04 | 4P 225A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #05 |  |  | #06 | 4P 225A | 2.41 | 1.92 | 6.64 |  | O | ON | 정류기시스템#1
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #07 |  |  | #08 | 4P 225A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #09 |  |  | #10 | 4P 225A | 0 | 0 | 0 |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #11 |  |  | #12 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #13 |  |  | #14 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #15 |  |  | #16 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #17 |  |  | #18 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 4P 100A | #19 |  |  | #20 | 4P 100A |  |  |  |  | X | OFF
[12 empty] | 총합: | 28.46 | 15.77 | 28.75
7-DaHall 1-PDU-04 |  |  | PDU : 7-DaHall 1-PDU-04 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 88.3 | 66 | 69.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
정류기시스템#2 | O | ON | 39.61 | 40.33 | 42.89 |  | 3P 150A | #01 |  | . | #02 | 3P 150A | 0 | 0 | 0 |  | O | ON | 7-DaHall 1-RPP-02
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #03 | . | . | #04 | 3P 150A | 0 | 0 | 0 |  | O | ON | 7-DaHall 1-RPP-04
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #05 | . |  | #06 | 3P 150A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #07 |  |  | #08 | 3P 150A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #09 |  |  | #10 | 3P 150A | 0 | 0 | 0 |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #11 |  |  | #12 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #13 |  |  | #14 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #15 |  |  | #16 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #17 |  |  | #18 | 3P 100A |  |  |  |  | X | OFF
| O | OFF |  |  |  |  | 4P 50A | #19 |  |  | #20 | 4P 50A |  |  |  |  | O | OFF
[12 empty] | 총합: | 39.61 | 40.33 | 42.89
|  |  | 사용량 | 층 배분
DEK | IDC | IDC상면 | 95.2 | 29.77% | [7 empty] | 7-1-A1 | 5.6 | 7.32 | 4.24
| 세종 | 인터넷 | 62.77 | 19.63% | [7 empty] | 7-1-B1 | 15.75 | 8.9 | 6.53
| 전송 | 전송 | 14.42 | 4.509% | [7 empty] | 7-1-A3 | 3.77 | 7.37 | 3.67
| 전송 | 정류기 | 133.8 | 41.84% | [7 empty] | 7-1-B3 | 3.93 | 7.73 | 2.81
| 전송/인터넷 | NOC | 4.35 | 1.36% | [7 empty] | 7-1-A2 | 19.26 | 18.21 | 13.83
| 8F Office |  | 9.23 | 2.886% | [7 empty] | 7-1-B2 | 14.34 | 18.51 | 14.97
|  | 총 합 | 319.77 | 100% | [7 empty] | 세종 정류기 | 42.02 | 42.25 | 49.53
[12 empty] | 8F Office | 2.37 | 1.8 | 5.06
[12 empty] | 총계 | 319.77
70.3494
Note on K18: 이현상: 변익준M에게 확인 요구 (2021.03.05)
Note on T21: 이현상: 기존부하명 : 전산랙 440BAY(B)
Note on A36: 이현상: 기존부하명 : 409BAY-B
Note on A37: 이현상: 기존부하명 : 410BAY-B 전원
Note on A68: 이현상: 기존부하명 : 409BAY-A
Note on A69: 이현상: 기존부하명 : 410BAY-A 전원
Note on A76: 이현상: 부하명은 207BAY-A(2)이지만, 실사용은 208BAY임

## 7층_부하량(월간_MAX)
Date : 2023-11-01 ~ 2023-11-30
7-DaHall 1-RPP-01 |  |  | PDU : 7-DaHall 1-RPP-01 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 26 | 14 | 21.8 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
W-DCS 8000 | O | ON | 0 |  |  |  | 2P 20A | #01 | 전송 |  | #02 | 2P 30A | 0 |  |  |  | O | ON | TO 8F 보안실 UPS항온 항습기 모니터용PC
?? | O | ON |  | 0 |  |  | 2P 20A | #03 | 전송 | 넷피플 | #04 | 2P 30A |  | 0 |  |  | O | ON | E-4-B
?? | O | ON |  |  | 0 |  | 2P 20A | #05 | 전송 | 넷피플 | #06 | 2P 30A |  |  | 0 |  | O | OFF | E-3-B
517 BAY | O | ON | 0 |  |  |  | 2P 20A | #07 | 전송 | 전송 | #08 | 2P 30A | 2.51 |  |  |  | O | ON | 406BAY 405BAY DCN-1B
Voice사업팀 MMS용-B | X | OFF |  | 2.68 |  |  | 2P 20A | #09 | IDC | 전송 | #10 | 2P 30A |  | 1.69 |  |  | O | ON | 407BAY 406BAY DCN-2B
Voice사업팀 D-7 RACK | O | ON |  |  | 0 |  | 2P 20A | #11 | 니즈텔레콤 | 전송 | #12 | 2P 30A |  |  | 5.48 |  | O | ON | 408BAY 407BAY DCN-3B
ONS1064 SERVER | O | ON | 1.53 |  |  |  | 2P 20A | #13 | 전송 | 엑사넷 | #14 | 2P 30A | 7.19 |  |  |  | O | ON | E-8-B
NTT 하-1 | X | ON |  | 4.81 |  |  | 2P 20A | #15 | IDC | 델피콤 | #16 | 2P 30A |  | 6.38 |  |  | O | ON | F-5-B
8층 보안실 CCTV 모니터 | O | ON |  |  | 0 |  | 2P 20A | #17 | 공통 | CARANG ('23.09.19) | #18 | 2P 30A |  |  | 2.18 |  | O | ON | C604 / F-7-A
G-10-A | O | ON | 5.38 |  |  |  | 2P 20A | #19 | 신한금융투자 | IDC | #20 | 2P 30A | 1.52 |  |  |  | O | ON | 인터넷운영팀MAN RACK#2 전원A
NTT 하-3 | X | OFF |  | 0 |  |  | 2P 20A | #21 |  | NTT | #22 | 2P 30A |  | 0 |  |  | O | ON | G-4-B
C-7-A-Q1 | O | ON |  |  | 1.5 |  | 2P 20A | #23 | NTT | NTT | #24 | 2P 30A |  |  | 2.29 |  | O | ON | G-6-B
인터넷운영팀MAN RACK#2 전원B | O | ON | 1.69 |  |  |  | 2P 20A | #25 | IDC | 교환라우터(총무팀 ??) | #26 | 2P 30A | 5.08 |  |  |  | O | ON | F-3-B
NMS B-15 | O | ON |  | 7.12 |  |  | 2P 20A | #27 | 전송 | 공통 | #28 | 2P 30A |  | 4.48 |  |  | O | ON | 운용실콘센트
NMS B-16 | O | ON |  |  | 4.81 |  | 2P 20A | #29 | 전송 | 공통 | #30 | 2P 30A |  |  | 5.98 |  | O | ON | 운용실콘센트 창가1열
?? | O | ON | 6.45 |  |  |  | 2P 20A | #31 | 전송 | 전송 | #32 | 2P 30A | 0 |  |  |  | O | ON | 전산랙 410BAY(B)
G-5-B | O | ON |  | 0 |  |  | 2P 20A | #33 | NTT | 니즈텔레콤 | #34 | 2P 30A |  | 4.2 |  |  | O | OFF | D-6-B
G-1-B | O | ON |  |  | 9.68 |  | 2P 20A | #35 |  | 르네트 | #36 | 2P 30A |  |  | 4.25 |  | O | ON | E-9-B
C-7-B-Q1 | O | ON | 5.39 |  |  |  | 2P 20A | #37 | NTT | 니즈텔레콤 | #38 | 2P 30A | 3.99 |  |  |  | O | ON | D-7-B
G-2-B | O | ON |  | 2.31 |  |  | 2P 20A | #39 |  | IDC | #40 | 2P 30A |  | 4.99 |  |  | O | ON | 341BAY / IDC MAN POP AC전원(B)
[12 empty] | 총합: | 40.73 | 38.66 | 36.17
7-DaHall 1-PDU-02 |  |  | PDU : 7-DaHall 1-PDU-02 | [5 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 30.2 | 45.2 | 46.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
G-3-B (NTT#8-B) | O | ON |  | 0 |  |  | 2P 30A | #01 | NTT | 쿼드마이너 | #02 | 2P 30A |  | 5.89 |  |  | O | ON | C503 | 쿼드마이너 예약상면
7B-342BAY | O | ON |  |  | 6.13 |  | 2P 30A | #03 | 인터넷 IP 랙 |  | #04 | 2P 30A |  |  | 5.78 |  | O | ON | U3-7B-D1
| X | OFF | 6.05 |  |  |  | 2P 30A | #05 |  | NTT | #06 | 2P 30A | 5.72 |  |  |  | O | ON | U3-7B-D5 B
241BAY-B | O | ON |  | 5.78 |  |  | 2P 30A | #07 |  | 전송 | #08 | 2P 30A |  | 1.09 |  |  | O | ON | U3-7B-337
242BAY-B | O | ON |  |  | 6.04 |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  |  | 9.39 |  | O | ON | 7F-C-6-NTT#3-B
209Bay - B | O | ON | 5.71 |  |  |  | 2P 30A | #11 |  | NTT | #12 | 2P 30A | 3.22 |  |  |  | O | ON | U3-7B G-3-B
210Bay - B | O | ON |  | 5.26 |  |  | 2P 30A | #13 |  | DEKR Network Rack | #14 | 2P 30A |  | 4.19 |  |  | O | ON | 218Bay - A전원 ('22.01.12 투입)
TATA#1/B | O | ON |  |  | 2.49 |  | 2P 30A | #15 | TATA | DEKR Network Rack | #16 | 2P 30A |  |  | 3.77 |  | O | ON | 217Bay - A전원 ('22.01.12 투입)
208BAY-B | O | ON | 8.53 |  |  |  | 2P 30A | #17 |  | 318Bay - DEK Network Rack | #18 | 2P 30A | 6.82 |  |  |  | O | ON | 318BAY-B U3-7B-18
207BAY-B | O | ON |  | 9.22 |  |  | 2P 30A | #19 |  | 317Bay - DEK Network Rack | #20 | 2P 30A |  | 3.06 |  |  | O | ON | 317BAY-B U3-7B-20
206BAY-B | O | ON |  |  | 4.65 |  | 2P 30A | #21 |  | 316Bay - DEK Network Rack | #22 | 2P 30A |  |  | 1.99 |  | O | ON | 316BAY-B U3-7B-22
205BAY-B | O | ON | 3.7 |  |  |  | 2P 30A | #23 |  | 315Bay - DEK Network Rack | #24 | 2P 30A | 2.41 |  |  |  | O | ON | 315BAY-B U3-7B-24
204BAY-B | O | ON |  | 2.35 |  |  | 2P 30A | #25 |  | 314Bay - DEK Network Rack | #26 | 2P 30A |  | 3.65 |  |  | O | ON | 314BAY-B U3-7B-26
208BAY-B(2) | O | ON |  |  | 4.23 |  | 2P 30A | #27 |  | 313Bay - DEK Network Rack | #28 | 2P 30A |  |  | 5.87 |  | O | ON | 313BAY-B U3-7B-28
C604 / F-7-B | O | ON | 2.49 |  |  |  | 2P 30A | #29 | CARANG ('23.09.19) | 드림라인 | #30 | 2P 30A | 0.68 |  |  |  | O | ON | 301BAY U3-7B-30
U3-7B-31 B-6-B | O | ON |  | 3.76 |  |  | 2P 30A | #31 | 세종 인터넷(클라우드이음) | 203Bay - 세종-아톤AWS | #32 | 2P 30A |  | 3.54 |  |  | O | ON | 203Bay-B ('22.07.14 투입) U3-7B-32
B-7-B | O | ON |  |  | 8.58 |  | 2P 30A | #33 | 세종 인터넷(클라우드이음) | C909 (舊 C-02) / TATA#02 | #34 | 2P 30A |  |  | 3.22 |  | O | ON | C-02(C909-B) U3-7B-34
B-8-B | O | ON | 6.81 |  |  |  | 2P 30A | #35 | 세종 인터넷(클라우드이음) |  | #36 | 2P 30A | 1.77 |  |  |  | O | ON | B424(310BAY-B)
Test Bed #2 U3-7B-37 | O | ON |  | 3.04 |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  | 4.11 |  |  | O | ON | B423(311BAY-B)
7-1-B2-30-39 | O | ON |  |  | 2.4 |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  |  | 3.65 |  | O | ON | B422(312BAY-B)
7B-30-41(C409) | O | ON | 5.87 |  |  |  | 2P 30A | #41 | C409 |  | #42 | 2P 30A | 5.21 |  |  |  | O | ON | 7-1-B2-30-42
| X | OFF |  | 1.91 |  |  | 2P 30A | #43 |  | 쿼드마이너 | #44 | 2P 30A |  | 3.32 |  |  | O | ON | C502 | 2023/04/10 랙 반입 예정
| X | OFF |  |  | 0 |  | 2P 30A | #45 |  | 쿼드마이너 | #46 | 2P 30A |  |  | 4.03 |  | O | ON | C504 | 쿼드마이너 예약상면
| X | OFF | 3.25 |  |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A | 5.27 |  |  |  | X | OFF
신규BMS(20F TPS실) Rack | O | ON |  | 3.26 |  |  | 2P 30A | #49 | 20F BMS |  | #50 | 2P 30A |  | 4.01 |  |  | O | ON | 7층 출입카드
신규BMS(7F TPS실) Rack | O | ON |  |  | 1.94 |  | 2P 30A | #51 | 7F BMS |  | #52 | 2P 30A |  |  | 3.8 |  | O | ON | 20F MAIN (FMS)
7B-D5-#1 | O | ON | 0.24 |  |  |  | 2P 30A | #53 | NTT |  | #54 | 2P 30A | 0 |  |  |  | O | ON | 7F MAIN (FMS)
[12 empty] | 총합: | 73.75 | 67.44 | 77.96 | 0
7-DaHall 1-PDU-01 |  |  | PDU : 7-DaHall 1-PDU-01 | [5 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 33.4 | 43.4 | 40.1 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
G-3-A (NTT#8-A) | O | ON |  | 0 |  |  | 2P 30A | #01 | NTT | 쿼드마이너 | #02 | 2P 30A |  | 2.53 |  |  | O | ON | G-8-A (C503) | 쿼드마이너 예약상면
F-5-A | O | ON |  |  | 5.08 |  | 2P 30A | #03 | 텔피콤 |  | #04 | 2P 30A |  |  | 6.02 |  | O | ON | D-1-A
7A-342BAY | O | ON | 7.44 |  |  |  | 2P 30A | #05 | 인터넷 IP 랙 | NTT | #06 | 2P 30A | 6.86 |  |  |  | O | ON | D-5-A
241BAY-A | O | ON |  | 6.67 |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  | 2.28 |  |  | O | ON | 405BAY / U3-7A-405BAY(A)
242BAY-A | O | ON |  |  | 7.46 |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  |  | 4.11 |  | O | ON | C-6-A
209Bay - A | O | ON | 6.88 |  |  |  | 2P 30A | #11 | 인터넷 IP 랙 | NTT | #12 | 2P 30A | 2.47 |  |  |  | O | ON | U3-7A G-3-A
210Bay - A | O | ON |  | 6.69 |  |  | 2P 30A | #13 | 인터넷 IP 랙 | DEKR Network Rack | #14 | 2P 30A |  | 4.57 |  |  | O | ON | 218Bay - A전원 ('22.01.12 투입)
TATA#1/A | O | ON |  |  | 0.79 |  | 2P 30A | #15 | TATA | DEKR Network Rack | #16 | 2P 30A |  |  | 4.58 |  | O | ON | 217Bay - A전원 ('22.01.12 투입)
208BYA-A | O | ON | 8.94 |  |  |  | 2P 30A | #17 | 인터넷 IP 랙 | 318Bay - DEK Network Rack | #18 | 2P 30A | 7.17 |  |  |  | O | ON | 318BAY-A U3-7A-18
207BYA-A | O | ON |  | 4.17 |  |  | 2P 30A | #19 | 인터넷 IP 랙 | 317Bay - DEK Network Rack | #20 | 2P 30A |  | 1.89 |  |  | O | ON | 317BAY-A U3-7A-20
206BYA-A | O | ON |  |  | 4.44 |  | 2P 30A | #21 | 인터넷 IP 랙 | 316Bay - DEK Network Rack | #22 | 2P 30A |  |  | 1.77 |  | O | ON | 316BAY-A U3-7A-22
205BYA-A | O | ON | 2.43 |  |  |  | 2P 30A | #23 | 인터넷 IP 랙 | 315Bay - DEK Network Rack | #24 | 2P 30A | 2.83 |  |  |  | O | ON | 315BAY-A U3-7A-24
204BYA-A | O | ON |  | 2.24 |  |  | 2P 30A | #25 | 인터넷 IP 랙 | 314Bay - DEK Network Rack | #26 | 2P 30A |  | 3.85 |  |  | O | ON | 314BAY-A U3-7A-26
208BAY 207BAY - A(2) | O | ON |  |  | 3.49 |  | 2P 30A | #27 | 인터넷 IP 랙 | 313Bay - DEK Network Rack | #28 | 2P 30A |  |  | 6.38 |  | O | ON | 313BAY-A U3-7A-28
322BAY 331BAY | O | ON | 0.38 |  |  |  | 2P 30A | #29 | 김종원M 요구회로 | 드림라인 | #30 | 2P 30A | 0.35 |  |  |  | O | ON | 301BAY U3-7A-30
U3-7A-31 B-6-A | O | ON |  | 4.59 |  |  | 2P 30A | #31 | 세종 인터넷(클라우드이음) | 203Bay - 세종-아톤AWS | #32 | 2P 30A |  | 2.85 |  |  | O | ON | 203Bay-A ('22.07.14 투입) U3-7A-32
B-7-A | O | ON |  |  | 8.88 |  | 2P 30A | #33 | 세종 인터넷(클라우드이음) | C909 (舊 C-02) / TATA#02 | #34 | 2P 30A |  |  | 4.58 |  | O | ON | C-02(C909-A) U3-7A-34
B-8-A | O | ON | 7.16 |  |  |  | 2P 30A | #35 | 세종 인터넷(클라우드이음) |  | #36 | 2P 30A | 1.78 |  |  |  | O | ON | B424(310BAY-A)
Test Bed #1 U3-7A-37 | O | ON |  | 1.89 |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  | 3.05 |  |  | O | ON | B423(311BAY-A)
7-1-A2-30-39 | O | ON |  |  | 2.78 |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  |  | 3.56 |  | O | ON | B422(312BAY-A)
7A-30-41(C409) | O | ON | 5.61 |  |  |  | 2P 30A | #41 | C409 |  | #42 | 2P 30A | 3.64 |  |  |  | O | ON | 7-1-A2-30-42
| X | OFF |  | 2.18 |  |  | 2P 30A | #43 |  | 쿼드마이너 | #44 | 2P 30A |  | 6.82 |  |  | O | ON | C502 | 2023/04/10 랙 반입 예정
| X | OFF |  |  | 0 |  | 2P 30A | #45 |  | 쿼드마이너 | #46 | 2P 30A |  |  | 2.95 |  | O | ON | C504 | 쿼드마이너 예약상면
| X | OFF | 3.45 |  |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A | 3.63 |  |  |  | X | OFF
| X | OFF |  | 6.66 |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 1.74 |  | 2P 30A | #51 |  |  | #52 | 2P 30A |  |  | 4.06 |  | O | ON | 7F NTT CCTV 전원
| X | OFF | 0 |  |  |  | 2P 30A | #53 |  | NTT | #54 | 2P 30A | 0.35 |  |  |  | O | ON | 7A-D5-#1
[12 empty] | 총합: | 71.37 | 62.93 | 72.67 | 0
7-DaHall 1-RPP-02 |  |  | PDU : 7-DaHall 1-RPP-02 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 39 | 12.5 | 20.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO | NO. | NO. | NO | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
강남방향 창가열 콘센트 | O | ON | 0 |  |  |  | 2P 20A | #01 | 공통 | 공통 | #02 | 2P 30A | 3.02 |  |  |  | O | ON | 정면창가 콘센트
?? | O | ON |  | 0.56 |  |  | 2P 20A | #03 | 공통 |  | #04 | 2P 30A |  | 1.13 |  |  | X | OFF | NTT 상-1
301 BAY | O | OFF |  |  | 1.84 |  | 2P 20A | #05 | 전송 | 전송 | #06 | 2P 30A |  |  | 0 |  | O | ON | GAINS
C2C DWDM EMS RACK | O | ON | 2.86 |  |  |  | 2P 20A | #07 | 전송 | NTT | #08 | 2P 30A | 4.75 |  |  |  | O | ON | C-8-A
405BAY / U3-7A-405BAY(A) | O | ON |  | 4.5 |  |  | 2P 20A | #09 | 전송 | 신한금융투자 | #10 | 2P 30A |  | 0.72 |  |  | O | ON | G-10-B
ONS1064 SERVER | O | ON |  |  | 0 |  | 2P 20A | #11 | 전송 | NTT | #12 | 2P 30A |  |  | 4.72 |  | O | ON | C-8-B
406BAY 405 BAY (DCN-1A) | O | ON | 2.86 |  |  |  | 2P 20A | #13 | 전송 | 유엔시스 | #14 | 2P 30A | 15.79 |  |  |  | O | ON | D-3-A
407BAY 406 BAY (DCN-2A) | O | ON |  | 1.78 |  |  | 2P 20A | #15 | 전송 | NTT | #16 | 2P 30A |  | 0 |  |  | O | ON | G-4-A (NTT#7)
408BAY 407 BAY (DCN-3A) | O | ON |  |  | 4.52 |  | 2P 20A | #17 | 전송 | NTT | #18 | 2P 30A |  |  | 2.91 |  | O | ON | G-6-A
E-2-A | O | ON | 6.61 |  |  |  | 2P 20A | #19 |  | 교환라우터(총무팀 ??) | #20 | 2P 30A | 8.08 |  |  |  | O | ON | F-3-A
E-5-A | X | OFF |  | 2.45 |  |  | 2P 20A | #21 | 니즈텔레콤 | 공통 | #22 | 2P 30A |  | 0 |  |  | O | ON | 운용실 바닥콘센트
E-6-A | O | ON |  |  | 0 |  | 2P 20A | #23 |  | 공통 | #24 | 2P 30A |  |  | 4.78 |  | O | ON | 운용실 콘센트 창가1열
E-7-A | O | ON | 0.72 |  |  |  | 2P 20A | #25 |  | 전송 | #26 | 2P 30A | 6.8 |  |  |  | O | ON | 전산랙 410 BAY-A
E-8-A | O | ON |  | 15.17 |  |  | 2P 20A | #27 | 엑사넷 | 니즈텔레콤 | #28 | 2P 30A |  | 0 |  |  | O | OFF | D-6-A
G-5-A | O | ON |  |  | 0 |  | 2P 20A | #29 | NTT | 르네트 | #30 | 2P 30A |  |  | 2.67 |  | O | ON | E-9-A
Voice사업팀 NMS용-A | X | OFF | 0 |  |  |  | 2P 20A | #31 | IDC | 니즈텔레콤 | #32 | 2P 30A | 4.18 |  |  |  | O | ON | D-7-A
NTT 상-3 | X | OFF |  | 0.48 |  |  | 2P 20A | #33 | IDC |  | #34 | 2P 30A |  | 0 |  |  | O | ON | F-8-A
7F NMS A-18 | O | ON |  |  | 3 |  | 2P 20A | #35 | 전송 | 델피콤 | #36 | 2P 30A |  |  | 8.03 |  | O | ON | F-6-A
7F NMS A-19 | O | ON | 6.77 |  |  |  | 2P 20A | #37 | 전송 | IDC | #38 | 2P 30A | 7.94 |  |  |  | O | ON | 341BAY / IDC MAN POP
7F NMS A-20 | O | ON |  | 8.07 |  |  | 2P 20A | #39 | 전송 |  | #40 | 2P 30A |  | 0 |  |  | O | ON | F-9-A
[12 empty] | 총합: | 70.38 | 34.86 | 32.47
7-DaHall 1-RPP-03 |  |  | PDU : 7-DaHall 1-RPP-03 | [5 empty] | Main CB 4P 225A
[12 empty] | MAIN 계측값 : | 6.8 | 8 | 5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A-1-A [A2-7-1] | O | ON | 1.2 |  |  |  | 2P 50A | #01 | CJ HELLOVISION | NTT | #02 | 2P 50A | 2.88 |  |  |  | O | ON | D-4-A [D3-A]
A-2-A [A2-7-2] | O | ON |  | 3.49 |  |  | 2P 50A | #03 | CJ HELLOVISION | NTT | #04 | 2P 50A |  | 2.63 |  |  | X | OFF | G-7-A
A-3-A [A2-7-3] | O | ON |  |  | 3.5 |  | 2P 50A | #05 | CJ HELLOVISION | CJ HELLOVISION | #06 | 2P 50A |  |  | 1.77 |  | O | ON | A-7-A [A2-7-7]
A-4-A [A2-7-4] | O | ON | 2.64 |  |  |  | 2P 50A | #07 | CJ HELLOVISION | CJ HELLOVISION | #08 | 2P 50A | 2.16 |  |  |  | O | ON | A-8-A [A2-7-8]
A-5-A [A2-7-5] | O | ON |  | 2.99 |  |  | 2P 50A | #09 | CJ HELLOVISION | CJ HELLOVISION | #10 | 2P 50A |  | 2.79 |  |  | O | ON | A-6-A [A2-7-6]
[12 empty] | 총합: | 8.88 | 11.9 | 5.27
7-DaHall 1-RPP-04 |  |  | PDU : 7-DaHall 1-RPP-04
[7 empty] | [A] |  | Main CB 4P 225A |  |  | MAIN 계측값 : | 8.6 | 7.6 | 5.7 | <- 실측값
A-1-B [B2-7-1] | O | ON | 1.19 |  |  |  | 2P 50A | #01 | CJ HELLOVISION | NTT | #02 | 2P 50A | 3.39 |  |  |  | O | ON | D-4-B [D3-B]
A-2-B [B2-7-2] | O | ON |  | 4.54 |  |  | 2P 50A | #03 | CJ HELLOVISION | NTT | #04 | 2P 50A |  | 5.55 |  |  | X | OFF | G-7-B
A-3-B [B2-7-3] | O | ON |  |  | 4.56 |  | 2P 50A | #05 | CJ HELLOVISION | CJ HELLOVISION | #06 | 2P 50A |  |  | 1.84 |  | O | ON | A-7-B [B2-7-7]
A-4-B [B2-7-4] | O | ON | 5.52 |  |  |  | 2P 50A | #07 | CJ HELLOVISION | CJ HELLOVISION | #08 | 2P 50A | 2.16 |  |  |  | O | ON | A-8-B [B2-7-8]
A-5-B [B2-7-5] | O | ON |  | 2.16 |  |  | 2P 50A | #09 | CJ HELLOVISION | CJ HELLOVISION | #10 | 2P 50A |  | 3.01 |  |  | O | ON | A-6-B [B2-7-6]
[12 empty] | 총합: | 12.26 | 15.26 | 6.4
7-DaHall 1-PDU-03 |  |  | PDU : 7-DaHall 1-PDU-03 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 82.2 | 71.2 | 81.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
7-DaHall 1-RPP-01 | O | ON | 27.41 | 15.7 | 28.82 |  | 4P 225A | #01 | . |  | #02 | 4P 225A | 7.09 | 8.25 | 9.83 |  | O | ON | 8층 Office 분전반(창고)
7-DaHall 1-RPP-03 | O | ON | 7.1 | 8.29 | 5.19 |  | 4P 225A | #03 | . |  | #04 | 4P 225A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #05 |  |  | #06 | 4P 225A | 59.06 | 59.71 | 62.09 |  | O | ON | 정류기시스템#1
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #07 |  |  | #08 | 4P 225A | 51.81 | 52.37 | 54.75 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #09 |  |  | #10 | 4P 225A | 0 | 0 | 0 |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #11 |  |  | #12 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #13 |  |  | #14 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #15 |  |  | #16 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #17 |  |  | #18 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 4P 100A | #19 |  |  | #20 | 4P 100A |  |  |  |  | X | OFF
[12 empty] | 총합: | 152.47 | 144.32 | 160.68
7-DaHall 1-PDU-04 |  |  | PDU : 7-DaHall 1-PDU-04 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 88.3 | 66 | 69.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
정류기시스템#2 | O | ON | 47.16 | 47.56 | 50.14 |  | 3P 150A | #01 |  | . | #02 | 3P 150A | 43.78 | 17.88 | 24.36 |  | O | ON | 7-DaHall 1-RPP-02
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #03 | . | . | #04 | 3P 150A | 10.47 | 7.93 | 5.85 |  | O | ON | 7-DaHall 1-RPP-04
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #05 | . |  | #06 | 3P 150A | 38.99 | 17.76 | 23.97 |  | X | OFF
| X | OFF | 10.51 | 7.83 | 5.84 |  | 3P 150A | #07 |  |  | #08 | 3P 150A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #09 |  |  | #10 | 3P 150A | 0 | 0 | 0 |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #11 |  |  | #12 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #13 |  |  | #14 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #15 |  |  | #16 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #17 |  |  | #18 | 3P 100A |  |  |  |  | X | OFF
| O | OFF |  |  |  |  | 4P 50A | #19 |  |  | #20 | 4P 50A |  |  |  |  | O | OFF
[12 empty] | 총합: | 150.91 | 98.96 | 110.16
|  |  | 사용량 | 층 배분
DEK | IDC | IDC상면 | 447.12 | 41.01% | [7 empty] | 7-1-A1 | 40.73 | 38.66 | 36.17
| 세종 | 인터넷 | 189.94 | 17.42% | [7 empty] | 7-1-B1 | 70.38 | 34.86 | 32.47
| 전송 | 전송 | 83.48 | 7.657% | [7 empty] | 7-1-A3 | 8.88 | 11.9 | 5.27
| 전송 | 정류기 | 325.72 | 29.88% | [7 empty] | 7-1-B3 | 12.26 | 15.26 | 6.4
| 전송/인터넷 | NOC | 18.82 | 1.726% | [7 empty] | 7-1-A2 | 71.37 | 62.93 | 72.67
| 8F Office |  | 25.17 | 2.309% | [7 empty] | 7-1-B2 | 73.75 | 67.44 | 77.96
|  | 총 합 | 1090.25 | 100% | [7 empty] | 세종 정류기 | 106.22 | 107.27 | 112.23
[12 empty] | 8F Office | 7.09 | 8.25 | 9.83
[12 empty] | 총계 | 1090.25
239.855
Note on K18: 이현상: 변익준M에게 확인 요구 (2021.03.05)
Note on T21: 이현상: 기존부하명 : 전산랙 440BAY(B)
Note on A36: 이현상: 기존부하명 : 409BAY-B
Note on A37: 이현상: 기존부하명 : 410BAY-B 전원
Note on A68: 이현상: 기존부하명 : 409BAY-A
Note on A69: 이현상: 기존부하명 : 410BAY-A 전원
Note on A76: 이현상: 부하명은 207BAY-A(2)이지만, 실사용은 208BAY임

## 7층_부하량(월간_AVG)
Date : 2023-11-01 ~ 2023-11-30
7-DaHall 1-RPP-01 |  |  | PDU : 7-DaHall 1-RPP-01 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 26 | 14 | 21.8 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
W-DCS 8000 | O | ON | 0 |  |  |  | 2P 20A | #01 | 전송 |  | #02 | 2P 30A | 0 |  |  |  | O | ON | TO 8F 보안실 UPS항온 항습기 모니터용PC
?? | O | ON |  | 0 |  |  | 2P 20A | #03 | 전송 | 넷피플 | #04 | 2P 30A |  | 0 |  |  | O | ON | E-4-B
?? | O | ON |  |  | 0 |  | 2P 20A | #05 | 전송 | 넷피플 | #06 | 2P 30A |  |  | 0 |  | O | OFF | E-3-B
517 BAY | O | ON | 0 |  |  |  | 2P 20A | #07 | 전송 | 전송 | #08 | 2P 30A | 2.295 |  |  |  | O | ON | 406BAY 405BAY DCN-1B
Voice사업팀 MMS용-B | X | OFF |  | 2.4182 |  |  | 2P 20A | #09 | IDC | 전송 | #10 | 2P 30A |  | 1.5543 |  |  | O | ON | 407BAY 406BAY DCN-2B
Voice사업팀 D-7 RACK | O | ON |  |  | 0 |  | 2P 20A | #11 | 니즈텔레콤 | 전송 | #12 | 2P 30A |  |  | 3.5739 |  | O | ON | 408BAY 407BAY DCN-3B
ONS1064 SERVER | O | ON | 1.4136 |  |  |  | 2P 20A | #13 | 전송 | 엑사넷 | #14 | 2P 30A | 5.8455 |  |  |  | O | ON | E-8-B
NTT 하-1 | X | ON |  | 4.0936 |  |  | 2P 20A | #15 | IDC | 델피콤 | #16 | 2P 30A |  | 3.2014 |  |  | O | ON | F-5-B
8층 보안실 CCTV 모니터 | O | ON |  |  | 0 |  | 2P 20A | #17 | 공통 | CARANG ('23.09.19) | #18 | 2P 30A |  |  | 1.4665 |  | O | ON | C604 / F-7-A
G-10-A | O | ON | 1.7132 |  |  |  | 2P 20A | #19 | 신한금융투자 | IDC | #20 | 2P 30A | 1.4647 |  |  |  | O | ON | 인터넷운영팀MAN RACK#2 전원A
NTT 하-3 | X | OFF |  | 0 |  |  | 2P 20A | #21 |  | NTT | #22 | 2P 30A |  | 0 |  |  | O | ON | G-4-B
C-7-A-Q1 | O | ON |  |  | 1.4198 |  | 2P 20A | #23 | NTT | NTT | #24 | 2P 30A |  |  | 2.1344 |  | O | ON | G-6-B
인터넷운영팀MAN RACK#2 전원B | O | ON | 1.5435 |  |  |  | 2P 20A | #25 | IDC | 교환라우터(총무팀 ??) | #26 | 2P 30A | 2.137 |  |  |  | O | ON | F-3-B
NMS B-15 | O | ON |  | 3.8387 |  |  | 2P 20A | #27 | 전송 | 공통 | #28 | 2P 30A |  | 1.8009 |  |  | O | ON | 운용실콘센트
NMS B-16 | O | ON |  |  | 3.7843 |  | 2P 20A | #29 | 전송 | 공통 | #30 | 2P 30A |  |  | 3.8632 |  | O | ON | 운용실콘센트 창가1열
?? | O | ON | 5.6071 |  |  |  | 2P 20A | #31 | 전송 | 전송 | #32 | 2P 30A | 0 |  |  |  | O | ON | 전산랙 410BAY(B)
G-5-B | O | ON |  | 0 |  |  | 2P 20A | #33 | NTT | 니즈텔레콤 | #34 | 2P 30A |  | 1.4248 |  |  | O | OFF | D-6-B
G-1-B | O | ON |  |  | 4.0589 |  | 2P 20A | #35 |  | 르네트 | #36 | 2P 30A |  |  | 3.4252 |  | O | ON | E-9-B
C-7-B-Q1 | O | ON | 4.639 |  |  |  | 2P 20A | #37 | NTT | 니즈텔레콤 | #38 | 2P 30A | 2.4542 |  |  |  | O | ON | D-7-B
G-2-B | O | ON |  | 2.0833 |  |  | 2P 20A | #39 |  | IDC | #40 | 2P 30A |  | 4.8317 |  |  | O | ON | 341BAY / IDC MAN POP AC전원(B)
[12 empty] | 총합: | 29.1128 | 25.2469 | 23.7262
7-DaHall 1-PDU-02 |  |  | PDU : 7-DaHall 1-PDU-02 | [5 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 30.2 | 45.2 | 46.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
G-3-B (NTT#8-B) | O | ON |  | 0 |  |  | 2P 30A | #01 | NTT | 쿼드마이너 | #02 | 2P 30A |  | 5.4828 |  |  | O | ON | C503 | 쿼드마이너 예약상면
7B-342BAY | O | ON |  |  | 5.5322 |  | 2P 30A | #03 | 인터넷 IP 랙 |  | #04 | 2P 30A |  |  | 5.3789 |  | O | ON | U3-7B-D1
| X | OFF | 5.5401 |  |  |  | 2P 30A | #05 |  | NTT | #06 | 2P 30A | 5.3234 |  |  |  | O | ON | U3-7B-D5 B
241BAY-B | O | ON |  | 5.6451 |  |  | 2P 30A | #07 |  | 전송 | #08 | 2P 30A |  | 1.011 |  |  | O | ON | U3-7B-337
242BAY-B | O | ON |  |  | 5.1452 |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  |  | 4.3618 |  | O | ON | 7F-C-6-NTT#3-B
209Bay - B | O | ON | 5.4275 |  |  |  | 2P 30A | #11 |  | NTT | #12 | 2P 30A | 2.6773 |  |  |  | O | ON | U3-7B G-3-B
210Bay - B | O | ON |  | 4.6923 |  |  | 2P 30A | #13 |  | DEKR Network Rack | #14 | 2P 30A |  | 3.2196 |  |  | O | ON | 218Bay - A전원 ('22.01.12 투입)
TATA#1/B | O | ON |  |  | 1.1919 |  | 2P 30A | #15 | TATA | DEKR Network Rack | #16 | 2P 30A |  |  | 3.0965 |  | O | ON | 217Bay - A전원 ('22.01.12 투입)
208BAY-B | O | ON | 4.2887 |  |  |  | 2P 30A | #17 |  | 318Bay - DEK Network Rack | #18 | 2P 30A | 2.6467 |  |  |  | O | ON | 318BAY-B U3-7B-18
207BAY-B | O | ON |  | 8.6048 |  |  | 2P 30A | #19 |  | 317Bay - DEK Network Rack | #20 | 2P 30A |  | 1.9609 |  |  | O | ON | 317BAY-B U3-7B-20
206BAY-B | O | ON |  |  | 4.0313 |  | 2P 30A | #21 |  | 316Bay - DEK Network Rack | #22 | 2P 30A |  |  | 1.9178 |  | O | ON | 316BAY-B U3-7B-22
205BAY-B | O | ON | 2.6238 |  |  |  | 2P 30A | #23 |  | 315Bay - DEK Network Rack | #24 | 2P 30A | 2.2107 |  |  |  | O | ON | 315BAY-B U3-7B-24
204BAY-B | O | ON |  | 2.064 |  |  | 2P 30A | #25 |  | 314Bay - DEK Network Rack | #26 | 2P 30A |  | 3.0434 |  |  | O | ON | 314BAY-B U3-7B-26
208BAY-B(2) | O | ON |  |  | 3.1066 |  | 2P 30A | #27 |  | 313Bay - DEK Network Rack | #28 | 2P 30A |  |  | 5.6621 |  | O | ON | 313BAY-B U3-7B-28
C604 / F-7-B | O | ON | 1.8172 |  |  |  | 2P 30A | #29 | CARANG ('23.09.19) | 드림라인 | #30 | 2P 30A | 0.5586 |  |  |  | O | ON | 301BAY U3-7B-30
U3-7B-31 B-6-B | O | ON |  | 3.2471 |  |  | 2P 30A | #31 | 세종 인터넷(클라우드이음) | 203Bay - 세종-아톤AWS | #32 | 2P 30A |  | 2.1671 |  |  | O | ON | 203Bay-B ('22.07.14 투입) U3-7B-32
B-7-B | O | ON |  |  | 8.1425 |  | 2P 30A | #33 | 세종 인터넷(클라우드이음) | C909 (舊 C-02) / TATA#02 | #34 | 2P 30A |  |  | 2.8911 |  | O | ON | C-02(C909-B) U3-7B-34
B-8-B | O | ON | 5.8439 |  |  |  | 2P 30A | #35 | 세종 인터넷(클라우드이음) |  | #36 | 2P 30A | 1.6451 |  |  |  | O | ON | B424(310BAY-B)
Test Bed #2 U3-7B-37 | O | ON |  | 1.2372 |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  | 3.5214 |  |  | O | ON | B423(311BAY-B)
7-1-B2-30-39 | O | ON |  |  | 1.9337 |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  |  | 3.0971 |  | O | ON | B422(312BAY-B)
7B-30-41(C409) | O | ON | 5.4582 |  |  |  | 2P 30A | #41 | C409 |  | #42 | 2P 30A | 3.9346 |  |  |  | O | ON | 7-1-B2-30-42
| X | OFF |  | 1.7774 |  |  | 2P 30A | #43 |  | 쿼드마이너 | #44 | 2P 30A |  | 1.8154 |  |  | O | ON | C502 | 2023/04/10 랙 반입 예정
| X | OFF |  |  | 0 |  | 2P 30A | #45 |  | 쿼드마이너 | #46 | 2P 30A |  |  | 3.6165 |  | O | ON | C504 | 쿼드마이너 예약상면
| X | OFF | 2.7992 |  |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A | 2.4513 |  |  |  | X | OFF
신규BMS(20F TPS실) Rack | O | ON |  | 1.081 |  |  | 2P 30A | #49 | 20F BMS |  | #50 | 2P 30A |  | 3.4265 |  |  | O | ON | 7층 출입카드
신규BMS(7F TPS실) Rack | O | ON |  |  | 0.81052 |  | 2P 30A | #51 | 7F BMS |  | #52 | 2P 30A |  |  | 3.2826 |  | O | ON | 20F MAIN (FMS)
7B-D5-#1 | O | ON | 0.22466 |  |  |  | 2P 30A | #53 | NTT |  | #54 | 2P 30A | 0 |  |  |  | O | ON | 7F MAIN (FMS)
[12 empty] | 총합: | 55.471 | 53.9967 | 63.1981 | 0
7-DaHall 1-PDU-01 |  |  | PDU : 7-DaHall 1-PDU-01 | [5 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 33.4 | 43.4 | 40.1 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
G-3-A (NTT#8-A) | O | ON |  | 0 |  |  | 2P 30A | #01 | NTT | 쿼드마이너 | #02 | 2P 30A |  | 2.2574 |  |  | O | ON | G-8-A (C503) | 쿼드마이너 예약상면
F-5-A | O | ON |  |  | 2.954 |  | 2P 30A | #03 | 텔피콤 |  | #04 | 2P 30A |  |  | 5.6083 |  | O | ON | D-1-A
7A-342BAY | O | ON | 5.2297 |  |  |  | 2P 30A | #05 | 인터넷 IP 랙 | NTT | #06 | 2P 30A | 6.3779 |  |  |  | O | ON | D-5-A
241BAY-A | O | ON |  | 6.0984 |  |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  | 1.6519 |  |  | O | ON | 405BAY / U3-7A-405BAY(A)
242BAY-A | O | ON |  |  | 5.6284 |  | 2P 30A | #09 |  |  | #10 | 2P 30A |  |  | 2.8402 |  | O | ON | C-6-A
209Bay - A | O | ON | 6.3336 |  |  |  | 2P 30A | #11 | 인터넷 IP 랙 | NTT | #12 | 2P 30A | 2.0299 |  |  |  | O | ON | U3-7A G-3-A
210Bay - A | O | ON |  | 5.7529 |  |  | 2P 30A | #13 | 인터넷 IP 랙 | DEKR Network Rack | #14 | 2P 30A |  | 4.0892 |  |  | O | ON | 218Bay - A전원 ('22.01.12 투입)
TATA#1/A | O | ON |  |  | 0.7122 |  | 2P 30A | #15 | TATA | DEKR Network Rack | #16 | 2P 30A |  |  | 2.7079 |  | O | ON | 217Bay - A전원 ('22.01.12 투입)
208BYA-A | O | ON | 3.9791 |  |  |  | 2P 30A | #17 | 인터넷 IP 랙 | 318Bay - DEK Network Rack | #18 | 2P 30A | 2.7001 |  |  |  | O | ON | 318BAY-A U3-7A-18
207BYA-A | O | ON |  | 3.8195 |  |  | 2P 30A | #19 | 인터넷 IP 랙 | 317Bay - DEK Network Rack | #20 | 2P 30A |  | 1.7184 |  |  | O | ON | 317BAY-A U3-7A-20
206BYA-A | O | ON |  |  | 3.462 |  | 2P 30A | #21 | 인터넷 IP 랙 | 316Bay - DEK Network Rack | #22 | 2P 30A |  |  | 1.6897 |  | O | ON | 316BAY-A U3-7A-22
205BYA-A | O | ON | 1.8628 |  |  |  | 2P 30A | #23 | 인터넷 IP 랙 | 315Bay - DEK Network Rack | #24 | 2P 30A | 2.65 |  |  |  | O | ON | 315BAY-A U3-7A-24
204BYA-A | O | ON |  | 1.9762 |  |  | 2P 30A | #25 | 인터넷 IP 랙 | 314Bay - DEK Network Rack | #26 | 2P 30A |  | 3.3292 |  |  | O | ON | 314BAY-A U3-7A-26
208BAY 207BAY - A(2) | O | ON |  |  | 3.2123 |  | 2P 30A | #27 | 인터넷 IP 랙 | 313Bay - DEK Network Rack | #28 | 2P 30A |  |  | 5.4264 |  | O | ON | 313BAY-A U3-7A-28
322BAY 331BAY | O | ON | 0.12754 |  |  |  | 2P 30A | #29 | 김종원M 요구회로 | 드림라인 | #30 | 2P 30A | 0.34146 |  |  |  | O | ON | 301BAY U3-7A-30
U3-7A-31 B-6-A | O | ON |  | 3.983 |  |  | 2P 30A | #31 | 세종 인터넷(클라우드이음) | 203Bay - 세종-아톤AWS | #32 | 2P 30A |  | 2.205 |  |  | O | ON | 203Bay-A ('22.07.14 투입) U3-7A-32
B-7-A | O | ON |  |  | 8.4039 |  | 2P 30A | #33 | 세종 인터넷(클라우드이음) | C909 (舊 C-02) / TATA#02 | #34 | 2P 30A |  |  | 4.0287 |  | O | ON | C-02(C909-A) U3-7A-34
B-8-A | O | ON | 5.9127 |  |  |  | 2P 30A | #35 | 세종 인터넷(클라우드이음) |  | #36 | 2P 30A | 1.6549 |  |  |  | O | ON | B424(310BAY-A)
Test Bed #1 U3-7A-37 | O | ON |  | 1.7538 |  |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  | 2.6066 |  |  | O | ON | B423(311BAY-A)
7-1-A2-30-39 | O | ON |  |  | 1.3576 |  | 2P 30A | #39 |  |  | #40 | 2P 30A |  |  | 3.3337 |  | O | ON | B422(312BAY-A)
7A-30-41(C409) | O | ON | 1.9029 |  |  |  | 2P 30A | #41 | C409 |  | #42 | 2P 30A | 2.8907 |  |  |  | O | ON | 7-1-A2-30-42
| X | OFF |  | 1.9771 |  |  | 2P 30A | #43 |  | 쿼드마이너 | #44 | 2P 30A |  | 5.6326 |  |  | O | ON | C502 | 2023/04/10 랙 반입 예정
| X | OFF |  |  | 0 |  | 2P 30A | #45 |  | 쿼드마이너 | #46 | 2P 30A |  |  | 2.6241 |  | O | ON | C504 | 쿼드마이너 예약상면
| X | OFF | 3.1056 |  |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A | 2.0633 |  |  |  | X | OFF
| X | OFF |  | 5.4363 |  |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 1.6246 |  | 2P 30A | #51 |  |  | #52 | 2P 30A |  |  | 0.0086132 |  | O | ON | 7F NTT CCTV 전원
| X | OFF | 0 |  |  |  | 2P 30A | #53 |  | NTT | #54 | 2P 30A | 0.34024 |  |  |  | O | ON | 7A-D5-#1
[12 empty] | 총합: | 49.5024 | 54.2876 | 55.6226 | 0
7-DaHall 1-RPP-02 |  |  | PDU : 7-DaHall 1-RPP-02 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 39 | 12.5 | 20.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO | NO. | NO. | NO | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
강남방향 창가열 콘센트 | O | ON | 0 |  |  |  | 2P 20A | #01 | 공통 | 공통 | #02 | 2P 30A | 1.6103 |  |  |  | O | ON | 정면창가 콘센트
?? | O | ON |  | 0.5364 |  |  | 2P 20A | #03 | 공통 |  | #04 | 2P 30A |  | 1.0467 |  |  | X | OFF | NTT 상-1
301 BAY | O | OFF |  |  | 1.1637 |  | 2P 20A | #05 | 전송 | 전송 | #06 | 2P 30A |  |  | 0 |  | O | ON | GAINS
C2C DWDM EMS RACK | O | ON | 1.4434 |  |  |  | 2P 20A | #07 | 전송 | NTT | #08 | 2P 30A | 3.7722 |  |  |  | O | ON | C-8-A
405BAY / U3-7A-405BAY(A) | O | ON |  | 1.4678 |  |  | 2P 20A | #09 | 전송 | 신한금융투자 | #10 | 2P 30A |  | 0.65395 |  |  | O | ON | G-10-B
ONS1064 SERVER | O | ON |  |  | 0 |  | 2P 20A | #11 | 전송 | NTT | #12 | 2P 30A |  |  | 4.3444 |  | O | ON | C-8-B
406BAY 405 BAY (DCN-1A) | O | ON | 2.7752 |  |  |  | 2P 20A | #13 | 전송 | 유엔시스 | #14 | 2P 30A | 12.9108 |  |  |  | O | ON | D-3-A
407BAY 406 BAY (DCN-2A) | O | ON |  | 1.7234 |  |  | 2P 20A | #15 | 전송 | NTT | #16 | 2P 30A |  | 0 |  |  | O | ON | G-4-A (NTT#7)
408BAY 407 BAY (DCN-3A) | O | ON |  |  | 3.1283 |  | 2P 20A | #17 | 전송 | NTT | #18 | 2P 30A |  |  | 2.4131 |  | O | ON | G-6-A
E-2-A | O | ON | 5.5701 |  |  |  | 2P 20A | #19 |  | 교환라우터(총무팀 ??) | #20 | 2P 30A | 2.7515 |  |  |  | O | ON | F-3-A
E-5-A | X | OFF |  | 1.5628 |  |  | 2P 20A | #21 | 니즈텔레콤 | 공통 | #22 | 2P 30A |  | 0 |  |  | O | ON | 운용실 바닥콘센트
E-6-A | O | ON |  |  | 0 |  | 2P 20A | #23 |  | 공통 | #24 | 2P 30A |  |  | 2.5932 |  | O | ON | 운용실 콘센트 창가1열
E-7-A | O | ON | 0.62625 |  |  |  | 2P 20A | #25 |  | 전송 | #26 | 2P 30A | 1.2034 |  |  |  | O | ON | 전산랙 410 BAY-A
E-8-A | O | ON |  | 7.3389 |  |  | 2P 20A | #27 | 엑사넷 | 니즈텔레콤 | #28 | 2P 30A |  | 0 |  |  | O | OFF | D-6-A
G-5-A | O | ON |  |  | 0 |  | 2P 20A | #29 | NTT | 르네트 | #30 | 2P 30A |  |  | 1.8933 |  | O | ON | E-9-A
Voice사업팀 NMS용-A | X | OFF | 0 |  |  |  | 2P 20A | #31 | IDC | 니즈텔레콤 | #32 | 2P 30A | 3.2696 |  |  |  | O | ON | D-7-A
NTT 상-3 | X | OFF |  | 0.43786 |  |  | 2P 20A | #33 | IDC |  | #34 | 2P 30A |  | 0 |  |  | O | ON | F-8-A
7F NMS A-18 | O | ON |  |  | 2.4571 |  | 2P 20A | #35 | 전송 | 델피콤 | #36 | 2P 30A |  |  | 6.6171 |  | O | ON | F-6-A
7F NMS A-19 | O | ON | 5.8717 |  |  |  | 2P 20A | #37 | 전송 | IDC | #38 | 2P 30A | 5.3995 |  |  |  | O | ON | 341BAY / IDC MAN POP
7F NMS A-20 | O | ON |  | 3.1211 |  |  | 2P 20A | #39 | 전송 |  | #40 | 2P 30A |  | 0 |  |  | O | ON | F-9-A
[12 empty] | 총합: | 47.204 | 17.8888 | 24.6103
7-DaHall 1-RPP-03 |  |  | PDU : 7-DaHall 1-RPP-03 | [5 empty] | Main CB 4P 225A
[12 empty] | MAIN 계측값 : | 6.8 | 8 | 5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A-1-A [A2-7-1] | O | ON | 1.179 |  |  |  | 2P 50A | #01 | CJ HELLOVISION | NTT | #02 | 2P 50A | 1.3236 |  |  |  | O | ON | D-4-A [D3-A]
A-2-A [A2-7-2] | O | ON |  | 2.9106 |  |  | 2P 50A | #03 | CJ HELLOVISION | NTT | #04 | 2P 50A |  | 1.9266 |  |  | X | OFF | G-7-A
A-3-A [A2-7-3] | O | ON |  |  | 3.3004 |  | 2P 50A | #05 | CJ HELLOVISION | CJ HELLOVISION | #06 | 2P 50A |  |  | 1.5083 |  | O | ON | A-7-A [A2-7-7]
A-4-A [A2-7-4] | O | ON | 2.437 |  |  |  | 2P 50A | #07 | CJ HELLOVISION | CJ HELLOVISION | #08 | 2P 50A | 1.9608 |  |  |  | O | ON | A-8-A [A2-7-8]
A-5-A [A2-7-5] | O | ON |  | 2.6297 |  |  | 2P 50A | #09 | CJ HELLOVISION | CJ HELLOVISION | #10 | 2P 50A |  | 2.6178 |  |  | O | ON | A-6-A [A2-7-6]
[12 empty] | 총합: | 6.9005 | 10.0847 | 4.8087
7-DaHall 1-RPP-04 |  |  | PDU : 7-DaHall 1-RPP-04
[7 empty] | [A] |  | Main CB 4P 225A |  |  | MAIN 계측값 : | 8.6 | 7.6 | 5.7 | <- 실측값
A-1-B [B2-7-1] | O | ON | 1.1786 |  |  |  | 2P 50A | #01 | CJ HELLOVISION | NTT | #02 | 2P 50A | 2.0054 |  |  |  | O | ON | D-4-B [D3-B]
A-2-B [B2-7-2] | O | ON |  | 3.5632 |  |  | 2P 50A | #03 | CJ HELLOVISION | NTT | #04 | 2P 50A |  | 4.3943 |  |  | X | OFF | G-7-B
A-3-B [B2-7-3] | O | ON |  |  | 3.9282 |  | 2P 50A | #05 | CJ HELLOVISION | CJ HELLOVISION | #06 | 2P 50A |  |  | 1.3512 |  | O | ON | A-7-B [B2-7-7]
A-4-B [B2-7-4] | O | ON | 4.0821 |  |  |  | 2P 50A | #07 | CJ HELLOVISION | CJ HELLOVISION | #08 | 2P 50A | 1.859 |  |  |  | O | ON | A-8-B [B2-7-8]
A-5-B [B2-7-5] | O | ON |  | 1.7102 |  |  | 2P 50A | #09 | CJ HELLOVISION | CJ HELLOVISION | #10 | 2P 50A |  | 2.8469 |  |  | O | ON | A-6-B [B2-7-6]
[12 empty] | 총합: | 9.125 | 12.5146 | 5.2793
7-DaHall 1-PDU-03 |  |  | PDU : 7-DaHall 1-PDU-03 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 82.2 | 71.2 | 81.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
7-DaHall 1-RPP-01 | O | ON | 25.3735 | 12.9936 | 19.0699 |  | 4P 225A | #01 | . |  | #02 | 4P 225A | 3.5731 | 3.5363 | 7.6977 |  | O | ON | 8층 Office 분전반(창고)
7-DaHall 1-RPP-03 | O | ON | 6.4377 | 7.8114 | 4.8932 |  | 4P 225A | #03 | . |  | #04 | 4P 225A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #05 |  |  | #06 | 4P 225A | 42.4126 | 42.8076 | 45.9105 |  | O | ON | 정류기시스템#1
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #07 |  |  | #08 | 4P 225A | 48.1898 | 48.7565 | 50.9272 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 225A | #09 |  |  | #10 | 4P 225A | 0 | 0 | 0 |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #11 |  |  | #12 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #13 |  |  | #14 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #15 |  |  | #16 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #17 |  |  | #18 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 4P 100A | #19 |  |  | #20 | 4P 100A |  |  |  |  | X | OFF
[12 empty] | 총합: | 125.9866 | 115.9055 | 128.4985
7-DaHall 1-PDU-04 |  |  | PDU : 7-DaHall 1-PDU-04 | [5 empty] | Main CB 4P 400A
[12 empty] | MAIN 계측값 : | 88.3 | 66 | 69.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
정류기시스템#2 | O | ON | 45.9711 | 46.8483 | 49.3899 |  | 3P 150A | #01 |  | . | #02 | 3P 150A | 39.3655 | 11.4363 | 20.3818 |  | O | ON | 7-DaHall 1-RPP-02
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #03 | . | . | #04 | 3P 150A | 8.7539 | 7.4589 | 5.5276 |  | O | ON | 7-DaHall 1-RPP-04
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #05 | . |  | #06 | 3P 150A | 34.8428 | 11.1817 | 19.5182 |  | X | OFF
| X | OFF | 8.9521 | 7.1636 | 5.4091 |  | 3P 150A | #07 |  |  | #08 | 3P 150A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 3P 150A | #09 |  |  | #10 | 3P 150A | 0 | 0 | 0 |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #11 |  |  | #12 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #13 |  |  | #14 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #15 |  |  | #16 | 3P 100A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 100A | #17 |  |  | #18 | 3P 100A |  |  |  |  | X | OFF
| O | OFF |  |  |  |  | 4P 50A | #19 |  |  | #20 | 4P 50A |  |  |  |  | O | OFF
[12 empty] | 총합: | 137.8854 | 84.0888 | 100.2265
|  |  | 사용량 | 층 배분
DEK | IDC | IDC상면 | 329.6739 | 39.4% | [7 empty] | 7-1-A1 | 29.1128 | 25.2469 | 23.7262
| 세종 | 인터넷 | 154.9523 | 18.52% | [7 empty] | 7-1-B1 | 47.204 | 17.8888 | 24.6103
| 전송 | 전송 | 53.5501 | 6.4% | [7 empty] | 7-1-A3 | 6.9005 | 10.0847 | 4.8087
| 전송 | 정류기 | 273.3399 | 32.67% | [7 empty] | 7-1-B3 | 9.125 | 12.5146 | 5.2793
| 전송/인터넷 | NOC | 10.404 | 1.243% | [7 empty] | 7-1-A2 | 49.5024 | 54.2876 | 55.6226
| 8F Office |  | 14.8071 | 1.77% | [7 empty] | 7-1-B2 | 55.471 | 53.9967 | 63.1981
|  | 총 합 | 836.7272 | 100% | [7 empty] | 세종 정류기 | 88.3837 | 89.6559 | 95.3003
[12 empty] | 8F Office | 3.5731 | 3.5363 | 7.6977
[12 empty] | 총계 | 836.7272
184.08
Note on K18: 이현상: 변익준M에게 확인 요구 (2021.03.05)
Note on T21: 이현상: 기존부하명 : 전산랙 440BAY(B)
Note on A36: 이현상: 기존부하명 : 409BAY-B
Note on A37: 이현상: 기존부하명 : 410BAY-B 전원
Note on A68: 이현상: 기존부하명 : 409BAY-A
Note on A69: 이현상: 기존부하명 : 410BAY-A 전원
Note on A76: 이현상: 부하명은 207BAY-A(2)이지만, 실사용은 208BAY임

## 7F_current (hidden)
7F | A(전류)
7-DaHall 1-PDU-01-01 | [branch#001] [A] current
7-DaHall 1-PDU-01-02 | [branch#002] [A] current
7-DaHall 1-PDU-01-03 | [branch#003] [A] current
7-DaHall 1-PDU-01-04 | [branch#004] [A] current
7-DaHall 1-PDU-01-05 | [branch#005] [A] current
7-DaHall 1-PDU-01-06 | [branch#006] [A] current
7-DaHall 1-PDU-01-07 | [branch#007] [A] current
7-DaHall 1-PDU-01-08 | [branch#008] [A] current
7-DaHall 1-PDU-01-09 | [branch#009] [A] current
7-DaHall 1-PDU-01-10 | [branch#010] [A] current
7-DaHall 1-PDU-01-11 | [branch#011] [A] current
7-DaHall 1-PDU-01-12 | [branch#012] [A] current
7-DaHall 1-PDU-01-13 | [branch#013] [A] current
7-DaHall 1-PDU-01-14 | [branch#014] [A] current
7-DaHall 1-PDU-01-15 | [branch#015] [A] current
7-DaHall 1-PDU-01-16 | [branch#016] [A] current
7-DaHall 1-PDU-01-17 | [branch#017] [A] current
7-DaHall 1-PDU-01-18 | [branch#018] [A] current
7-DaHall 1-PDU-01-19 | [branch#019] [A] current
7-DaHall 1-PDU-01-20 | [branch#020] [A] current
7-DaHall 1-PDU-01-21 | [branch#021] [A] current
7-DaHall 1-PDU-01-22 | [branch#022] [A] current
7-DaHall 1-PDU-01-23 | [branch#023] [A] current
7-DaHall 1-PDU-01-24 | [branch#024] [A] current
7-DaHall 1-PDU-01-25 | [branch#025] [A] current
7-DaHall 1-PDU-01-26 | [branch#026] [A] current
7-DaHall 1-PDU-01-27 | [branch#027] [A] current
7-DaHall 1-PDU-01-28 | [branch#028] [A] current
7-DaHall 1-PDU-01-29 | [branch#029] [A] current
7-DaHall 1-PDU-01-30 | [branch#030] [A] current
7-DaHall 1-PDU-01-31 | [branch#031] [A] current
7-DaHall 1-PDU-01-32 | [branch#032] [A] current
7-DaHall 1-PDU-01-33 | [branch#033] [A] current
7-DaHall 1-PDU-01-34 | [branch#034] [A] current
7-DaHall 1-PDU-01-35 | [branch#035] [A] current
7-DaHall 1-PDU-01-36 | [branch#036] [A] current
7-DaHall 1-PDU-01-37 | [branch#037] [A] current
7-DaHall 1-PDU-01-38 | [branch#038] [A] current
7-DaHall 1-PDU-01-39 | [branch#039] [A] current
7-DaHall 1-PDU-01-40 | [branch#040] [A] current
7-DaHall 1-PDU-01-41 | [branch#041] [A] current
7-DaHall 1-PDU-01-42 | [branch#042] [A] current
7-DaHall 1-PDU-01-43 | [branch#043] [A] current
7-DaHall 1-PDU-01-44 | [branch#044] [A] current
7-DaHall 1-PDU-01-45 | [branch#045] [A] current
7-DaHall 1-PDU-01-46 | [branch#046] [A] current
7-DaHall 1-PDU-01-47 | [branch#047] [A] current
7-DaHall 1-PDU-01-48 | [branch#048] [A] current
7-DaHall 1-PDU-01-49 | [branch#049] [A] current
7-DaHall 1-PDU-01-50 | [branch#050] [A] current
7-DaHall 1-PDU-01-51 | [branch#051] [A] current
7-DaHall 1-PDU-01-52 | [branch#052] [A] current
7-DaHall 1-PDU-01-53 | [branch#053] [A] current
7-DaHall 1-PDU-01-54 | [branch#054] [A] current
7-DaHall 1-PDU-02-01 | [branch#001] [A] current
7-DaHall 1-PDU-02-02 | [branch#002] [A] current
7-DaHall 1-PDU-02-03 | [branch#003] [A] current
7-DaHall 1-PDU-02-04 | [branch#004] [A] current
7-DaHall 1-PDU-02-05 | [branch#005] [A] current
7-DaHall 1-PDU-02-06 | [branch#006] [A] current
7-DaHall 1-PDU-02-07 | [branch#007] [A] current
7-DaHall 1-PDU-02-08 | [branch#008] [A] current
7-DaHall 1-PDU-02-09 | [branch#009] [A] current
7-DaHall 1-PDU-02-10 | [branch#010] [A] current
7-DaHall 1-PDU-02-11 | [branch#011] [A] current
7-DaHall 1-PDU-02-12 | [branch#012] [A] current
7-DaHall 1-PDU-02-13 | [branch#013] [A] current
7-DaHall 1-PDU-02-14 | [branch#014] [A] current
7-DaHall 1-PDU-02-15 | [branch#015] [A] current
7-DaHall 1-PDU-02-16 | [branch#016] [A] current
7-DaHall 1-PDU-02-17 | [branch#017] [A] current
7-DaHall 1-PDU-02-18 | [branch#018] [A] current
7-DaHall 1-PDU-02-19 | [branch#019] [A] current
7-DaHall 1-PDU-02-20 | [branch#020] [A] current
7-DaHall 1-PDU-02-21 | [branch#021] [A] current
7-DaHall 1-PDU-02-22 | [branch#022] [A] current
7-DaHall 1-PDU-02-23 | [branch#023] [A] current
7-DaHall 1-PDU-02-24 | [branch#024] [A] current
7-DaHall 1-PDU-02-25 | [branch#025] [A] current
7-DaHall 1-PDU-02-26 | [branch#026] [A] current
7-DaHall 1-PDU-02-27 | [branch#027] [A] current
7-DaHall 1-PDU-02-28 | [branch#028] [A] current
7-DaHall 1-PDU-02-29 | [branch#029] [A] current
7-DaHall 1-PDU-02-30 | [branch#030] [A] current
7-DaHall 1-PDU-02-31 | [branch#031] [A] current
7-DaHall 1-PDU-02-32 | [branch#032] [A] current
7-DaHall 1-PDU-02-33 | [branch#033] [A] current
7-DaHall 1-PDU-02-34 | [branch#034] [A] current
7-DaHall 1-PDU-02-35 | [branch#035] [A] current
7-DaHall 1-PDU-02-36 | [branch#036] [A] current
7-DaHall 1-PDU-02-37 | [branch#037] [A] current
7-DaHall 1-PDU-02-38 | [branch#038] [A] current
7-DaHall 1-PDU-02-39 | [branch#039] [A] current
7-DaHall 1-PDU-02-40 | [branch#040] [A] current
7-DaHall 1-PDU-02-41 | [branch#041] [A] current
7-DaHall 1-PDU-02-42 | [branch#042] [A] current
7-DaHall 1-PDU-02-43 | [branch#043] [A] current
7-DaHall 1-PDU-02-44 | [branch#044] [A] current
7-DaHall 1-PDU-02-45 | [branch#045] [A] current
7-DaHall 1-PDU-02-46 | [branch#046] [A] current
7-DaHall 1-PDU-02-47 | [branch#047] [A] current
7-DaHall 1-PDU-02-48 | [branch#048] [A] current
7-DaHall 1-PDU-02-49 | [branch#049] [A] current
7-DaHall 1-PDU-02-50 | [branch#050] [A] current
7-DaHall 1-PDU-02-51 | [branch#051] [A] current
7-DaHall 1-PDU-02-52 | [branch#052] [A] current
7-DaHall 1-PDU-02-53 | [branch#053] [A] current
7-DaHall 1-PDU-02-54 | [branch#054] [A] current
7-DaHall 1-PDU-03-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
7-DaHall 1-PDU-03-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
7-DaHall 1-PDU-03-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
7-DaHall 1-PDU-03-04 | [branch#004] [R] I1 | [branch#004] [S] I2 | [branch#004] [T] I3
7-DaHall 1-PDU-03-05 | [branch#005] [R] I1 | [branch#005] [S] I2 | [branch#005] [T] I3
7-DaHall 1-PDU-03-06 | [branch#006] [R] I1 | [branch#006] [S] I2 | [branch#006] [T] I3
7-DaHall 1-PDU-03-07 | [branch#007] [R] I1 | [branch#007] [S] I2 | [branch#007] [T] I3
7-DaHall 1-PDU-03-08 | [branch#008] [R] I1 | [branch#008] [S] I2 | [branch#008] [T] I3
7-DaHall 1-PDU-03-09 | [branch#009] [R] I1 | [branch#009] [S] I2 | [branch#009] [T] I3
7-DaHall 1-PDU-03-10 | [branch#010] [R] I1 | [branch#010] [S] I2 | [branch#010] [T] I3
7-DaHall 1-PDU-04-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
7-DaHall 1-PDU-04-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
7-DaHall 1-PDU-04-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
7-DaHall 1-PDU-04-04 | [branch#004] [R] I1 | [branch#004] [S] I2 | [branch#004] [T] I3
7-DaHall 1-PDU-04-05 | [branch#005] [R] I1 | [branch#005] [S] I2 | [branch#005] [T] I3
7-DaHall 1-PDU-04-06 | [branch#006] [R] I1 | [branch#006] [S] I2 | [branch#006] [T] I3
7-DaHall 1-PDU-04-07 | [branch#007] [R] I1 | [branch#007] [S] I2 | [branch#007] [T] I3
7-DaHall 1-PDU-04-08 | [branch#008] [R] I1 | [branch#008] [S] I2 | [branch#008] [T] I3
7-DaHall 1-PDU-04-09 | [branch#009] [R] I1 | [branch#009] [S] I2 | [branch#009] [T] I3
7-DaHall 1-PDU-04-10 | [branch#010] [R] I1 | [branch#010] [S] I2 | [branch#010] [T] I3
7-DaHall 1-RPP-01-01 | [branch#001] [A] current
7-DaHall 1-RPP-01-02 | [branch#002] [A] current
7-DaHall 1-RPP-01-03 | [branch#003] [A] current
7-DaHall 1-RPP-01-04 | [branch#004] [A] current
7-DaHall 1-RPP-01-05 | [branch#005] [A] current
7-DaHall 1-RPP-01-06 | [branch#006] [A] current
7-DaHall 1-RPP-01-07 | [branch#007] [A] current
7-DaHall 1-RPP-01-08 | [branch#008] [A] current
7-DaHall 1-RPP-01-09 | [branch#009] [A] current
7-DaHall 1-RPP-01-10 | [branch#010] [A] current
7-DaHall 1-RPP-01-11 | [branch#011] [A] current
7-DaHall 1-RPP-01-12 | [branch#012] [A] current
7-DaHall 1-RPP-01-13 | [branch#013] [A] current
7-DaHall 1-RPP-01-14 | [branch#014] [A] current
7-DaHall 1-RPP-01-15 | [branch#015] [A] current
7-DaHall 1-RPP-01-16 | [branch#016] [A] current
7-DaHall 1-RPP-01-17 | [branch#017] [A] current
7-DaHall 1-RPP-01-18 | [branch#018] [A] current
7-DaHall 1-RPP-01-19 | [branch#019] [A] current
7-DaHall 1-RPP-01-20 | [branch#020] [A] current
7-DaHall 1-RPP-01-21 | [branch#021] [A] current
7-DaHall 1-RPP-01-22 | [branch#022] [A] current
7-DaHall 1-RPP-01-23 | [branch#023] [A] current
7-DaHall 1-RPP-01-24 | [branch#024] [A] current
7-DaHall 1-RPP-01-25 | [branch#025] [A] current
7-DaHall 1-RPP-01-26 | [branch#026] [A] current
7-DaHall 1-RPP-01-27 | [branch#027] [A] current
7-DaHall 1-RPP-01-28 | [branch#028] [A] current
7-DaHall 1-RPP-01-29 | [branch#029] [A] current
7-DaHall 1-RPP-01-30 | [branch#030] [A] current
7-DaHall 1-RPP-01-31 | [branch#031] [A] current
7-DaHall 1-RPP-01-32 | [branch#032] [A] current
7-DaHall 1-RPP-01-33 | [branch#033] [A] current
7-DaHall 1-RPP-01-34 | [branch#034] [A] current
7-DaHall 1-RPP-01-35 | [branch#035] [A] current
7-DaHall 1-RPP-01-36 | [branch#036] [A] current
7-DaHall 1-RPP-01-37 | [branch#037] [A] current
7-DaHall 1-RPP-01-38 | [branch#038] [A] current
7-DaHall 1-RPP-01-39 | [branch#039] [A] current
7-DaHall 1-RPP-01-40 | [branch#040] [A] current
7-DaHall 1-RPP-02-01 | [branch#001] [A] current
7-DaHall 1-RPP-02-02 | [branch#002] [A] current
7-DaHall 1-RPP-02-03 | [branch#003] [A] current
7-DaHall 1-RPP-02-04 | [branch#004] [A] current
7-DaHall 1-RPP-02-05 | [branch#005] [A] current
7-DaHall 1-RPP-02-06 | [branch#006] [A] current
7-DaHall 1-RPP-02-07 | [branch#007] [A] current
7-DaHall 1-RPP-02-08 | [branch#008] [A] current
7-DaHall 1-RPP-02-09 | [branch#009] [A] current
7-DaHall 1-RPP-02-10 | [branch#010] [A] current
7-DaHall 1-RPP-02-11 | [branch#011] [A] current
7-DaHall 1-RPP-02-12 | [branch#012] [A] current
7-DaHall 1-RPP-02-13 | [branch#013] [A] current
7-DaHall 1-RPP-02-14 | [branch#014] [A] current
7-DaHall 1-RPP-02-15 | [branch#015] [A] current
7-DaHall 1-RPP-02-16 | [branch#016] [A] current
7-DaHall 1-RPP-02-17 | [branch#017] [A] current
7-DaHall 1-RPP-02-18 | [branch#018] [A] current
7-DaHall 1-RPP-02-19 | [branch#019] [A] current
7-DaHall 1-RPP-02-20 | [branch#020] [A] current
7-DaHall 1-RPP-02-21 | [branch#021] [A] current
7-DaHall 1-RPP-02-22 | [branch#022] [A] current
7-DaHall 1-RPP-02-23 | [branch#023] [A] current
7-DaHall 1-RPP-02-24 | [branch#024] [A] current
7-DaHall 1-RPP-02-25 | [branch#025] [A] current
7-DaHall 1-RPP-02-26 | [branch#026] [A] current
7-DaHall 1-RPP-02-27 | [branch#027] [A] current
7-DaHall 1-RPP-02-28 | [branch#028] [A] current
7-DaHall 1-RPP-02-29 | [branch#029] [A] current
7-DaHall 1-RPP-02-30 | [branch#030] [A] current
7-DaHall 1-RPP-02-31 | [branch#031] [A] current
7-DaHall 1-RPP-02-32 | [branch#032] [A] current
7-DaHall 1-RPP-02-33 | [branch#033] [A] current
7-DaHall 1-RPP-02-34 | [branch#034] [A] current
7-DaHall 1-RPP-02-35 | [branch#035] [A] current
7-DaHall 1-RPP-02-36 | [branch#036] [A] current
7-DaHall 1-RPP-02-37 | [branch#037] [A] current
7-DaHall 1-RPP-02-38 | [branch#038] [A] current
7-DaHall 1-RPP-02-39 | [branch#039] [A] current
7-DaHall 1-RPP-02-40 | [branch#040] [A] current
7-DaHall 1-RPP-03-01 | [branch#001] [A] current
7-DaHall 1-RPP-03-02 | [branch#002] [A] current
7-DaHall 1-RPP-03-03 | [branch#003] [A] current
7-DaHall 1-RPP-03-04 | [branch#004] [A] current
7-DaHall 1-RPP-03-05 | [branch#005] [A] current
7-DaHall 1-RPP-03-06 | [branch#006] [A] current
7-DaHall 1-RPP-03-07 | [branch#007] [A] current
7-DaHall 1-RPP-03-08 | [branch#008] [A] current
7-DaHall 1-RPP-03-09 | [branch#009] [A] current
7-DaHall 1-RPP-03-10 | [branch#010] [A] current
7-DaHall 1-RPP-04-01 | [branch#001] [A] current
7-DaHall 1-RPP-04-02 | [branch#002] [A] current
7-DaHall 1-RPP-04-03 | [branch#003] [A] current
7-DaHall 1-RPP-04-04 | [branch#004] [A] current
7-DaHall 1-RPP-04-05 | [branch#005] [A] current
7-DaHall 1-RPP-04-06 | [branch#006] [A] current
7-DaHall 1-RPP-04-07 | [branch#007] [A] current
7-DaHall 1-RPP-04-08 | [branch#008] [A] current
7-DaHall 1-RPP-04-09 | [branch#009] [A] current
7-DaHall 1-RPP-04-10 | [branch#010] [A] current

## 6층_부하량(월간_MIN)
Date : 2023-11-01 ~ 2023-11-30
6-DaHall 1-CEP-05 | [7 empty] | Main CB 4P 350A
[10 empty] | MAIN 계측값 : | 2.3 | 2.1 | 2.9 | <- 실측값 |  |  | 5-DaHall 1-EH-01
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
5-DaHall 1-CEP-06 | O | ON | 0 | 0.75 | 0.67 |  | 4P 150A | #01
| X | OFF | 사 | 용 | 금 | 지 | 4P 50A | #02 | #03 | 4P 50A | 0 | 0 | 0 |  | X | OFF
5-DaHall 1-CRAC-14 (CF CRAC #02) | O | ON | 0 | 0 | 0 |  | 4P 50A | #04 | #05 | 4P 50A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 50A | #06 | #07 | 4P 50A | 0 | 0 | 0 |  | O | OFF | 급배기휀
| X | OFF | 0 | 0 | 0 |  | 4P 50A | #08 | #09 | 4P 50A | 0 | 0 | 0 |  | X | OFF
spare | X | OFF | 0 | 0 | 0 |  | 4P 50A | #10 | #11 | 4P 100A | 0 | 0 | 0 |  | O | ON | 8층 냉방분전반
| O | OFF | 0 |  |  |  | 2P 30A | #12 | #13 | 2P 30A | 0 |  |  |  | O | OFF
| O | OFF |  | 0 |  |  | 2P 30A | #14 | #15 | 2P 50A |  | 0 |  |  | O | ON | 7-DaHall 1-EH (7층 가습기 Main)
| O | OFF |  |  | 0 |  | 2P 30A | #16 | #17 | 2P 50A |  |  | 0 |  | O | ON | 6-DaHall 1-EH (6층 가습기 Main)
|  | 6층 사무실 | 0 | [6 empty] | 총합: | 0 | 0.75 | 0.67 | 0
[11 empty] | 1.42 | 0 | 0%
6-DaHall 1-PDU-13 |  | PDU : SEL1 - 6-1 - A7 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A7-18-6 | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | DE운용실 사무#1 A7-30-8
A7-18-7 | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | DE 출입통제Desk A7-31-1
A7-18-8 | O | ON | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | 6F DE 가청경보 PNL
A7-18-9 | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | OFF | A7-31-3
A7-28-1 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-4
A7-28-2 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | OFF | A7-31-5
A7-28-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | OFF | A7-31-6
A7-28-4 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-7
A7-28-5 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | A7-31-8
A7-28-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | #A7-28-3
A7-28-7 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | OFF | #A7-28-6
A7-28-8 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | OFF | #A7-29-3
A7-29-1 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | OFF | #A7-29-6
A7-29-2 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | A7-21-4(3) (M-14)
A7-29-3 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | A7-21-3(3) (M-13)
A7-29-4 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | A7-21-3(2) (M-13)
A7-29-5 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | A7-21-4(2) (M-14)
A7-29-6 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | OFF | A7-26-8(2)
A7-29-7 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | OFF | A7-26-9(2)
A7-29-8 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A7-28-9 (6층 인터넷장비)
A7-30-1 | O | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | OFF | A7-29-9
A7-30-2 | O | OFF |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | OFF | A7-30-9
A7-30-3 | O | OFF |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-9
A7-30-4 | O | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | A7-27-6
A7-30-5 | O | OFF |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | A7-26-6
A7-30-6 | O | OFF |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | ON | A4-19-1 (O-11)
A7-30-7 | O | OFF | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | OFF | A4-27-9 (G-19)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-14 |  | PDU : SEL1 - 6-1 - B7 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B7-18-6 | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | DE운용실 감시모니터 B7-30-8
B7-18-7 | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | DE운용실 사무#2 B7-31-1
B7-18-8 | O | ON | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-2
B7-18-9 | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | OFF | B7-31-3
B7-28-1 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-4
B7-28-2 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-5
B7-28-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | OFF | B7-31-6
B7-28-4 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-7
B7-28-5 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-8
B7-28-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | ON | B7-32-1 (사무실)
B7-28-7 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | OFF | B7-32-2 (사무실)
B7-28-8 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | OFF | B7-32-3 (사무실)
B7-29-1 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | OFF | B7-32-4 (사무실)
B7-29-2 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | B7-21-4(3) (M-14)
B7-29-3 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | B7-21-3(3) (M-13)
B7-29-4 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | B7-21-4(2) (M-13)
B7-29-5 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | B7-21-3(2) (M-14)
B7-29-6 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | OFF | B7-26-8(2)
B7-29-7 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | OFF | B7-26-9(2)
B7-29-8 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | OFF | B7-28-9
B7-30-1 | O | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | OFF | B7-29-9
B7-30-2 | O | OFF |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | OFF | B7-30-9
B7-30-3 | O | OFF |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-9
B7-30-4 | O | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | B7-26-6
B7-30-5 | O | OFF |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | B7-27-6
B7-30-6 | O | OFF |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | ON | B4-19-1 (O-11)
B7-30-7 | O | OFF | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | OFF | A4-27-8
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-09 |  | PDU : SEL1 - 6-1 - A5 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A3-21-1 (M-11) | O | ON | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | ON | A3-22-1 (L-11)
A3-21-2 (M-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | ON | A3-22-2 (L-12)
A3-21-3 (M-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | ON | A3-22-3 (L-13)
A3-21-4 (M-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | ON | A3-22-4 (L-14)
A3-21-5 (M-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | A3-22-5 (L-15)
A3-21-6 (M-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | A3-22-6 (L-16)
A3-21-7 (M-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | A3-22-7 (L-17)
A3-21-8 (M-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A3-22-8 (L-18)
A3-21-9 (M-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A3-22-9 (L-19)
#A3-19-4 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | A3-23-1 (K-11)
#A3-19-7 | O | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | A3-23-2 (K-12)
#A3-36-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A3-23-3 (K-13)
#A3-36-6 | O | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | A3-23-4 (K-14)
#A3-23-4 (K-14) | O | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | A3-23-5 (K-15)
#A3-23-7 (K-17) | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | A3-23-6 (K-16)
B4-19-7 (O-17) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | A3-23-7 / 6F-K-17
#A3-24-7 | O | OFF |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | A3-23-8 / 6F-K-18)
A3-24-8 (J-18) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | ON | A3-23-9 / 6F-K-19
A3-24-9 (J-19) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-1 (J-11)
#A3-25-4 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | A3-24-2 (J-12)
#A3-26-4 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | A3-24-3 (J-13)
#A3-27-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-4 (J-14)
A3-27-1 (G-11) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | A3-24-5 (J-15)
A3-27-2 (G-12) | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | OFF | A3-24-6 (J-16)
A3-27-3 (G-13) | O | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-7 (J-17)
[10 empty] | 총합: | 0 | 0 | 0 | 0
6-DaHall 1-PDU-10 |  | PDU : SEL1 - 6-1 - B5 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B3-21-1 (M-11) | O | ON | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | ON | B3-22-1 (L-11)
B3-21-2 (M-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | ON | B3-22-2 (L-12)
B3-21-3 (M-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | ON | B3-22-3 (L-13)
B3-21-4 (M-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | ON | B3-22-4 (L-14)
B3-21-5 (M-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | B3-22-5 (L-15)
B3-21-6 (M-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | B3-22-6 (L-16)
B3-21-7 (M-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | B3-22-7 (L-17)
B3-21-8 (M-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B3-22-8 (L-18)
B3-21-9 (M-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B3-22-9 (L-19)
#B3-20-4 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | B3-23-1 (K-11)
#B3-20-7 (N-17) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | B3-23-2 (K-12)
#B3-21-4 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B3-24-6 (J-16)
#B3-21-7 | O | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | B3-23-4 (K-14)
#B3-22-4 | O | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | B3-23-5 (K-15)
#B3-22-7 | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | B3-23-6 (K-16)
#B3-25-7 | O | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | B3-23-7 / 6F-K-17
#B3-26-7 | O | OFF |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B3-23-8 / 6F-K-18
B3-24-8 (J-18) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | ON | B3-23-9 / 6F-K-19
B3-24-9 (J-19) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-1 (J-11)
#B3-27-7 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | B3-24-2 (J-12)
B3-27-1 (G-11) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | B3-24-3 (J-13)
B3-27-2 (G-12) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-4 (J-14)
B3-27-3 (G-13) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | B3-24-5 (J-15)
spare | X | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B3-23-3 (K-13)
spare | X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-7 (J-17)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-11 |  | PDU : SEL1 - 6-1 - A6 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 5.1 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | OFF | A4-20-1 (N-11)
A4-19-2 (O-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | OFF | A4-20-2 (N-12)
A4-19-3 (O-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | OFF | A4-20-3 (N-13)
A4-19-4 (O-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | OFF | A4-20-4 (N-14)
A4-19-5 (O-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | A4-20-5 (N-15)
A4-19-6 (O-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | A4-20-6 (N-16)
A4-19-7 (O-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | A4-20-7 (N-17)
A4-19-8 (O-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A4-20-8 (N-18)
A4-19-9 (O-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A4-20-9 (N-19)
A4-36-1 (AG-19) | O | ON | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | A4-25-9 (I-19)
A4-36-2 (S-10) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-1 (H-11)
A4-36-3 (S-11) | O | ON |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-2 (H-12)
A4-36-4 (S-12) | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | OFF | A4-26-3 (H-13)
A4-36-5 (S-13) | O | ON |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-4 (H-14)
A4-36-6 (S-14) | O | ON |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-5 (H-15)
A4-36-7 (S-15) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | X | OFF
A4-36-8 (S-16) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-7 (H-17)
A4-25-1 (I-11) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-8 (H-18)
A4-25-2 (I-12) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | A4-26-9 (H-19)
A4-25-3 (I-13) | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | A4-27-4 (G-14)
A4-25-4 (I-14) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | A4-27-5 (G-15)
A4-25-5 (I-15) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | A4-36-9 (AG-20)
A4-25-6 (I-16) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | A4-27-7 (G-17)
Rack S-15 | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | X | OFF
Rack S-13 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-12 |  | PDU : SEL1 - 6-1 - B6 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 5.1 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-1 (N-11)
B4-19-2 (O-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B4-20-2 (N-12)
B4-19-3 (O-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | OFF | B4-20-3 (N-13)
B4-19-4 (O-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-4 (N-14)
B4-19-5 (O-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | B4-20-5 (N-15)
B4-19-6 (O-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | B4-20-6 (N-16)
#A3-24-4 | O | OFF | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-7 (N-17)
B4-19-8 (O-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B4-20-8 (N-18)
B4-19-9 (O-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B4-20-9 (N-19)
B4-36-1 (AG-19) | O | ON | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | B4-25-9 (I-19)
B4-36-2 (S-10) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-1 (H-11)
B4-36-3 (S-11) | O | ON |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-2 (H-12)
B4-36-4 (S-12) | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B4-26-3 (H-13)
B4-36-5 (S-13) | O | ON |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-4 (H-14)
B4-36-6 (S-14) | O | ON |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-5 (H-15)
B4-36-7 (S-15) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | X | OFF
B4-36-8 (S-16) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-7 (H-17)
B4-25-1 (I-11) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-8 (H-18)
B4-25-2 (I-12) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | B4-26-9 (H-19)
B4-25-3 (I-13) | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | B4-27-4 (G-14)
B4-25-4 (I-14) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | B4-27-5 (G-15)
B4-25-5 (I-15) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B4-36-9 (AG-20)
B4-25-6 (I-16) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | B4-27-7 (G-17)
Rack S-15 | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | OFF | B4-27-8 (G-18)
Rack S-13 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | B4-27-9 (G-19)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-01 |  | PDU : SEL1 - 6-1 - A1 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 21.6 | 21.2 | 16.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A1-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | ON | G1101(A)
A1-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | ON | G1103(A)
A1-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | ON | A1-35-3(AG-13)
A1-1-4 (AF-16) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | ON | A1-35-4(AG-14)
A1-1-5 (AF-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | A1-35-5(AG-15)
A1-1-6 (AF-14) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | A1-35-6(AG-16)
A1-1-7 (AF-13) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 2.28 |  |  |  | O | ON | A1-35-7(AG-17)
A1-1-8 (AF-12) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 2.19 |  |  | O | ON | A1-35-8 (AG-18)
A1-1-9 (AF-11) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A1-16-4 (R-14)
#A1-1-3 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | A1-16-5 (R-15)
#A1-1-7 | O | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | A1-16-6 (R-16)
#A1-35-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A1-16-7 (R-17)
6-1-A1-30-25 | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | A1-16-8 (R-18)
A1-13-1 (AA-11) | O | ON |  | 2.28 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | A1-16-9 (R-19)
A1-13-2 (AA-12) | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | OFF | #A1-13-4
A1-13-3 (AA-13) | O | ON | 1.26 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | OFF | #A1-16-4
A1-13-4 (AA-14) | O | ON |  | 1.53 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | X | OFF | A1-4-1
A1-13-5 (AA-15) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | ON | G1102(A)
A1-13-6 (AA-16) | O | ON | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | X | OFF | G1102 하부(미사용)
A1-13-7 (AA-17) | O | ON |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | A1-35-3(2)(위치 불명)
B209 / (AA-18) | O | ON |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | ON | B411
A1-13-9 (B410) | O | ON | 1.02 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B211 | A1-30-44 를 B211에 포설 예정('23.05월초)
A1-16-1 (R-11) | O | ON |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0.55 |  |  | O | ON | 신규 BMS(6F TPS실) Rack
A1-16-2 (R-12) | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | A1-4-8 (AC-12)
B210 / (AA-19) | O | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | ON | FMS 6층 전원
[10 empty] | 총합: | 4.56 | 6.55 | 0
6-DaHall 1-PDU-02 |  | PDU : SEL1 - 6-1 - B1 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 19.2 | 18.8 | 21.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B1-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | ON | G1101 (B)
B1-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | ON | G1103 (B)
B1-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | ON | B1-35-3(AG-13)
B1-1-4 (AF-16) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | ON | B1-35-4(AG-14)
B1-1-5 (AF-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | B1-35-5(AG-15)
B1-1-6 (AF-14) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | B1-35-6(AG-16)
B1-1-7 (AF-13) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 1.36 |  |  |  | O | ON | B1-35-7(AG-17)
B1-1-8 (AF-12) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 2.04 |  |  | O | ON | B1-35-8 (AG-18)
B1-1-9 (AF-11) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | X | OFF | 6-1-B1-30-18
#B1-2-3 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | B1-16-5 (R-15)
#B1-2-7 | O | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | B1-16-6 (R-16)
#B1-3-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | B1-16-7 (R-17)
6-1-B1-30-25 | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | B1-16-8 (R-18)
B1-13-1 (AA-11) | O | ON |  | 1.36 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | B1-16-9 (R-19)
B1-13-2 (AA-12) | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B210 / (AA-19) | B1-30-30 사용예정
B1-13-3 (AA-13) | O | ON | 1.29 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | OFF | #B1-16-7
B1-13-4 (AA-14) | O | ON |  | 1.67 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B1-16-4 (R-14)
B1-13-5 (AA-15) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | ON | G1102 (B)
B1-13-6 (AA-16) | O | ON | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | G1102 하부(도어락&CCTV)
B1-13-7 (AA-17) | O | ON |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | B1-35-3(2)(위치 불명)
B209 / (AA-18) | O | ON |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | ON | B411
B1-13-9 (B410) | O | ON | 1.41 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B211 | B1-30-44 를 B211에 포설 예정('23.05월초)
B1-16-1 (R-11) | O | ON |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | X | OFF | B1-4-7
B1-16-2 (R-12) | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B1-4-8 (AC-12)
| X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 4.06 | 5.07 | 0
6-DaHall 1-PDU-03 |  | PDU : SEL1 - 6-1 - A2 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 20.7 | 21.3 | 10.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A2-2-1 | O | ON | 2.61 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | X | OFF | A2-3-1
A2-2-2 | O | ON |  | 0.8 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | X | OFF | A2-3-2
A2-2-3 | O | ON |  |  | 0.79 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | X | OFF | A2-3-3
A2-2-4 | O | ON | 3.6 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | X | OFF | A2-3-4
A2-2-5 | O | ON |  | 2.03 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | X | OFF | A2-3-5
A2-2-6 | O | ON |  |  | 0 | `` | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | X | OFF | A2-3-6
A2-2-7 | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | X | OFF | A2-3-7
A2-2-8 | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A2-3-8 (AD-12)
A2-2-9 | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A2-3-9 (AD-11)
A2-5-1 | X | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | A2-6-8
A2-5-2 | X | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | A2-7-1 (V-17)
A2-5-3 | X | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A2-7-2 (V-17)
A2-5-4 | X | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | A2-7-3 (V-16)
A2-5-5 | X | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | A2-7-4 (V-15)
A2-5-6 | X | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | A2-7-5 (V-14)
A2-5-7 | X | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | A2-7-6 (V-13)
A2-5-8 (AB-12) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | A2-7-7 (V-12)
A2-5-9 (AB-11) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | A2-7-8 (V-11)
A2-6-1 | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | A2-8-1 (V-16)
A2-6-2 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | A2-8-2 (W-17)
A2-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | ON | A2-8-3 (W-16)
A2-6-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | ON | A2-8-4 (W-15)
A2-6-5 | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | ON | A2-8-5 (W-14)
A2-6-6 | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | A2-8-6 (W-13)
손혈관인식시스템 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 6.21 | 2.83 | 0.79
6-DaHall 1-PDU-04 |  | PDU : SEL1 - 6-1 - B2 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 18.6 | 29.1 | 14.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B2-2-1 | O | ON | 2.2 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | X | OFF | B2-3-1
B2-2-2 | O | ON |  | 0.85 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | X | OFF | B2-3-2
B2-2-3 | O | ON |  |  | 0.83 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | X | OFF | B2-3-3
B2-2-4 | O | ON | 1.74 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | X | OFF | B2-3-4
B2-2-5 | O | ON |  | 1.81 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | X | OFF | B2-3-5
B2-2-6 | O | ON |  |  | 0 | `` | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | X | OFF | B2-3-6
B2-2-7 | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | X | OFF | B2-3-7
B2-2-8 | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B2-3-8 (AD-12)
B2-2-9 | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B2-3-9 (AD-11)
B2-5-1 | X | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | B2-6-8
B2-5-2 | X | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | B2-7-1 (V-17)
B2-5-3 | X | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | B2-7-2 (V-17)
B2-5-4 | X | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | B2-7-3 (V-16)
B2-5-5 | X | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | B2-7-4 (V-15)
B2-5-6 | X | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | B2-7-5 (V-14)
B2-5-7 | X | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | B2-7-6 (V-13)
B2-5-8 (AB-12) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B2-7-7 (V-12)
B2-5-9 (AB-11) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | B2-7-8 (V-11)
B2-6-1 | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | B2-8-1 (V-16)
B2-6-2 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | B2-8-2 (W-17)
B2-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | ON | B2-8-3 (W-16)
B2-6-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | ON | B2-8-4 (W-15)
B2-6-5 | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | ON | B2-8-5 (W-14)
B2-6-6 | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B2-8-6 (W-13)
| X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 3.94 | 2.66 | 0.83
6-DaHall 1-PDU-05 |  | PDU : SEL1 - 6-1 - A3 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 19.5 | 43.6 | 27 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A5-8-7 (W-12) | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | ON | A5-15-1 (T-11)
A5-8-8 (W-11) | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | ON | A5-15-2 (T-12)
A5-9-1 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0.7 |  |  |  | O | ON | A5-15-3 (T-13)
A5-9-2 (X-17) | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 2.38 |  |  | O | ON | A5-15-4 (T-14)
A5-9-3 (X-16) | O | ON |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | ON | A5-15-5 (T-15)
A5-9-4 (X-15) | O | ON | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | A5-15-6 (T-16)
A5-9-5 (X-14) | O | ON |  | 2 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 3.2 |  |  | O | ON | A5-15-7 (T-17)
A5-9-6 (X-13) | O | ON |  |  | 2.5 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 1.53 |  | O | ON | A5-15-8 (T-18)
A5-9-7 (X-12) | O | ON | 0.86 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | A5-15-9
A5-9-8 (X-11) | O | ON |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | ON | A5-17-1 (Q-11)
A5-10-1 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | A5-17-2 (Q-12)
A807(A5-10-2) | O | ON | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | A5-17-3 (Q-13)
A5-10-3 (A806 - 1) | O | ON |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | A5-17-4 (Q-14)
A5-10-4 (A806 - 2) | O | ON |  |  | 0.25 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | A5-17-5 (Q-15)
A5-10-5 (Y-14) | O | ON | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | A5-17-6 (Q-16)
A5-10-6 (Y-13) | O | ON |  | 1.52 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | A5-17-7 (Q-17)
A5-10-7 (Y-12) | O | ON |  |  | 1.11 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | A5-17-8 (Q-18)
A5-10-8 (Y-11) | O | ON | 0.67 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | A5-17-9 (Q-19)
A5-14-1 (U-10) | O | ON |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | A5-18-1 (P-11)
A5-14-2 (U-11) | O | ON |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A5-18-2 (P-12)
A5-14-3 (U-12) | O | ON | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | A5-18-3 (P-13)
A5-14-4 (U-13) | O | ON |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | A5-18-4 (P-14)
A5-14-5 (U-14) | O | ON |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | A5-18-5 (P-15)
6-1-A3-47 | O | ON | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | ON | A5-16-3 (R-13)
A5-14-7 (U-16) | O | ON |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | ON | A5-4-9 (AC-11)
6-1-A3-51 | O | ON |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | A5-6-7
6-1-A3-53 | O | ON | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 4.15 |  |  |  | O | ON | A5-15-5(2) (T-15)
[10 empty] | 총합: | 6.38 | 9.1 | 5.39
6-DaHall 1-PDU-06 |  | PDU : SEL1 - 6-1 - B3 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 12.5 | 37.1 | 24.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B5-8-7 (W-12) | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | ON | B5-15-1 (T-11)
B5-8-8 (W-11) | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | ON | B5-15-2 (T-12)
B5-9-1 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0.68 |  |  |  | O | ON | B5-15-3 (T-13)
B5-9-2 | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 3.09 |  |  | O | ON | B5-15-4 (T-14)
B5-9-3 | O | ON |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | ON | B5-15-5 (T-15)
B5-9-4 (X-15) | O | ON | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | B5-15-6 (T-16)
B5-9-5 (X-14) | O | ON |  | 1.96 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 1.33 |  |  | O | ON | B5-15-7 (T-17)
B5-9-6 (X-13) | O | ON |  |  | 0.66 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0.38 |  | O | ON | B5-15-8 (T-18)
B5-9-7 (X-12) | O | ON | 0.82 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | B5-15-9
B5-9-8 (X-11) | O | ON |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | ON | B5-17-1 (Q-11)
B5-10-1 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | B5-17-2 (Q-12)
A807(B5-10-2) | O | ON | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | B5-17-3 (Q-13)
B5-10-3 (A806 - 1) | O | ON |  | 0.39 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | B5-17-4 (Q-14)
B5-10-4 (A806 - 2) | O | ON |  |  | 0.23 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | B5-17-5 (Q-15)
B5-10-5 (Y-14) | O | ON | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | B5-17-6 (Q-16)
B5-10-6 (Y-13) | O | ON |  | 0.38 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | B5-17-7 (Q-17)
B5-10-7 (Y-12) | O | ON |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | B5-17-8 (Q-18)
B5-10-8 (Y-11) | O | ON | 0.39 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | B5-17-9 (Q-19)
A5-14-1 (U-10) | O | ON |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | B5-18-1 (P-11)
A5-14-2 (U-11) | O | ON |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | B5-18-2 (P-12)
A5-14-3 (U-12) | O | ON | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | B5-18-3 (P-13)
A5-14-4 (U-13) | O | ON |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | B5-18-4 (P-14)
A5-14-5 (U-14) | O | ON |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | B5-18-5 (P-15)
6-1-B3-47 | O | ON | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | ON | B5-16-3 (R-13)
A5-14-7 (U-16) | O | ON |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | ON | B5-4-9 (AC-11)
6-1-B3-51 | O | ON |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | B5-6-7
6-1-B3-53 | O | ON | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 2.31 |  |  |  | O | ON | B5-15-5(2) (T-15)
[10 empty] | 총합: | 4.2 | 7.15 | 1.27
6-DaHall 1-PDU-07 |  | PDU : SEL1 - 6-1 - A4 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
#A6-4-4 | O | OFF |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | A6-4-1
#A6-4-7 | O | OFF |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | A6-4-2
#A6-5-4 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | A6-4-3
#A6-5-7 | O | OFF |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | ON | A6-4-4 (AC-16)
#A6-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | ON | A6-4-5 (AC-15)
#A6-6-6 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | A6-4-6 (AC-14)
#A6-7-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | ON | A6-4-7 (AC-13)
#A6-7-6 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | A6-5-1
#A6-8-3 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | A6-5-2
#A6-8-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | A6-5-3
#A6-9-3 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | A6-5-4 (AB-16)
#A6-9-6 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | A6-5-5 (AB-15)
#A6-10-3 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | A6-5-6 (AB-14)
#A6-10-6 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | A6-5-7 (AB-13)
#A6-14-4 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | OFF | A6-2-1
#A6-14-7 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | OFF | A6-2-2
#A6-15-4 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | OFF | A6-2-3
#A6-15-7 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | A6-2-4 (AE-16)
#A6-17-4 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | A6-2-5 (AE-15)
#A6-17-7 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A6-2-6 (AE-14)
A6-8-8(1) | O | ON | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | A6-2-7 (AE-13)
A6-8-7(1) | O | ON |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | A6-2-8 (AE-12)
A6-8-6(1) | O | ON |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | A6-2-9 (AE-11)
불량 | X | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | A6-3-1
A6-3-7 (AD-13) | O | ON |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | A6-3-2
A6-3-6 (AD-14) | O | ON |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | A6-3-3
A6-3-5 (AD-15) | O | ON | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | ON | A6-3-4 (AD-16)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-08 |  | PDU : SEL1 - 6-1 - B4 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
#B6-28-3 | X | OFF |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | B6-4-1
#B6-28-6 | X | OFF |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | B6-4-2
#B6-29-3 | X | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | B6-4-3
#B6-29-6 | X | OFF |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | ON | B6-4-4 (AC-16)
#B6-30-3 | X | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | ON | B6-4-5 (AC-15)
#B6-30-6 | X | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | B6-4-6 (AC-14)
#B6-31-3 | X | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | ON | B6-4-7 (AC-13)
#B6-31-6 | X | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | B6-5-1
#B6-32-3 | X | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | B6-5-2
#B6-32-6 | X | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | B6-5-3
#B6-33-3 | X | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | B6-5-4 (AB-16)
#B6-33-6 | X | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | B6-5-5 (AB-15)
| X | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | B6-5-6 (AB-14)
| X | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | B6-5-7 (AB-13)
| X | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | OFF | B6-2-1
| X | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | OFF | B6-2-2
| X | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | OFF | B6-2-3
| X | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | B6-2-4 (AE-16)
| X | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | B6-2-5 (AE-15)
| X | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | B6-2-6 (AE-14)
| X | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | B6-2-7 (AE-13)
B6-8-8(1) | O | ON |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | B6-2-8 (AE-12)
B6-8-7(1) | O | ON |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | B6-2-9 (AE-11)
B6-8-6(1) | O | ON | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | B6-3-1
B6-3-7 (AD-13) | O | ON |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | B6-3-2
B6-3-6 (AD-14) | O | ON |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | B6-3-3
B6-3-5 (AD-15) | O | ON | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | ON | B6-3-4 (AD-16)
[10 empty] | 총합: | 0 | 0 | 0
| IDC | 70.99

## 6F_current (hidden)
6F | A(전류)
6-DaHall 1-PDU-01-01 | [branch#001] [A] current
6-DaHall 1-PDU-01-02 | [branch#002] [A] current
6-DaHall 1-PDU-01-03 | [branch#003] [A] current
6-DaHall 1-PDU-01-04 | [branch#004] [A] current
6-DaHall 1-PDU-01-05 | [branch#005] [A] current
6-DaHall 1-PDU-01-06 | [branch#006] [A] current
6-DaHall 1-PDU-01-07 | [branch#007] [A] current
6-DaHall 1-PDU-01-08 | [branch#008] [A] current
6-DaHall 1-PDU-01-09 | [branch#009] [A] current
6-DaHall 1-PDU-01-10 | [branch#010] [A] current
6-DaHall 1-PDU-01-11 | [branch#011] [A] current
6-DaHall 1-PDU-01-12 | [branch#012] [A] current
6-DaHall 1-PDU-01-13 | [branch#013] [A] current
6-DaHall 1-PDU-01-14 | [branch#014] [A] current
6-DaHall 1-PDU-01-15 | [branch#015] [A] current
6-DaHall 1-PDU-01-16 | [branch#016] [A] current
6-DaHall 1-PDU-01-17 | [branch#017] [A] current
6-DaHall 1-PDU-01-18 | [branch#018] [A] current
6-DaHall 1-PDU-01-19 | [branch#019] [A] current
6-DaHall 1-PDU-01-20 | [branch#020] [A] current
6-DaHall 1-PDU-01-21 | [branch#021] [A] current
6-DaHall 1-PDU-01-22 | [branch#022] [A] current
6-DaHall 1-PDU-01-23 | [branch#023] [A] current
6-DaHall 1-PDU-01-24 | [branch#024] [A] current
6-DaHall 1-PDU-01-25 | [branch#025] [A] current
6-DaHall 1-PDU-01-26 | [branch#026] [A] current
6-DaHall 1-PDU-01-27 | [branch#027] [A] current
6-DaHall 1-PDU-01-28 | [branch#028] [A] current
6-DaHall 1-PDU-01-29 | [branch#029] [A] current
6-DaHall 1-PDU-01-30 | [branch#030] [A] current
6-DaHall 1-PDU-01-31 | [branch#031] [A] current
6-DaHall 1-PDU-01-32 | [branch#032] [A] current
6-DaHall 1-PDU-01-33 | [branch#033] [A] current
6-DaHall 1-PDU-01-34 | [branch#034] [A] current
6-DaHall 1-PDU-01-35 | [branch#035] [A] current
6-DaHall 1-PDU-01-36 | [branch#036] [A] current
6-DaHall 1-PDU-01-37 | [branch#037] [A] current
6-DaHall 1-PDU-01-38 | [branch#038] [A] current
6-DaHall 1-PDU-01-39 | [branch#039] [A] current
6-DaHall 1-PDU-01-40 | [branch#040] [A] current
6-DaHall 1-PDU-01-41 | [branch#041] [A] current
6-DaHall 1-PDU-01-42 | [branch#042] [A] current
6-DaHall 1-PDU-01-43 | [branch#043] [A] current
6-DaHall 1-PDU-01-44 | [branch#044] [A] current
6-DaHall 1-PDU-01-45 | [branch#045] [A] current
6-DaHall 1-PDU-01-46 | [branch#046] [A] current
6-DaHall 1-PDU-01-47 | [branch#047] [A] current
6-DaHall 1-PDU-01-48 | [branch#048] [A] current
6-DaHall 1-PDU-01-49 | [branch#049] [A] current
6-DaHall 1-PDU-01-50 | [branch#050] [A] current
6-DaHall 1-PDU-02-01 | [branch#001] [A] current
6-DaHall 1-PDU-02-02 | [branch#002] [A] current
6-DaHall 1-PDU-02-03 | [branch#003] [A] current
6-DaHall 1-PDU-02-04 | [branch#004] [A] current
6-DaHall 1-PDU-02-05 | [branch#005] [A] current
6-DaHall 1-PDU-02-06 | [branch#006] [A] current
6-DaHall 1-PDU-02-07 | [branch#007] [A] current
6-DaHall 1-PDU-02-08 | [branch#008] [A] current
6-DaHall 1-PDU-02-09 | [branch#009] [A] current
6-DaHall 1-PDU-02-10 | [branch#010] [A] current
6-DaHall 1-PDU-02-11 | [branch#011] [A] current
6-DaHall 1-PDU-02-12 | [branch#012] [A] current
6-DaHall 1-PDU-02-13 | [branch#013] [A] current
6-DaHall 1-PDU-02-14 | [branch#014] [A] current
6-DaHall 1-PDU-02-15 | [branch#015] [A] current
6-DaHall 1-PDU-02-16 | [branch#016] [A] current
6-DaHall 1-PDU-02-17 | [branch#017] [A] current
6-DaHall 1-PDU-02-18 | [branch#018] [A] current
6-DaHall 1-PDU-02-19 | [branch#019] [A] current
6-DaHall 1-PDU-02-20 | [branch#020] [A] current
6-DaHall 1-PDU-02-21 | [branch#021] [A] current
6-DaHall 1-PDU-02-22 | [branch#022] [A] current
6-DaHall 1-PDU-02-23 | [branch#023] [A] current
6-DaHall 1-PDU-02-24 | [branch#024] [A] current
6-DaHall 1-PDU-02-25 | [branch#025] [A] current
6-DaHall 1-PDU-02-26 | [branch#026] [A] current
6-DaHall 1-PDU-02-27 | [branch#027] [A] current
6-DaHall 1-PDU-02-28 | [branch#028] [A] current
6-DaHall 1-PDU-02-29 | [branch#029] [A] current
6-DaHall 1-PDU-02-30 | [branch#030] [A] current
6-DaHall 1-PDU-02-31 | [branch#031] [A] current
6-DaHall 1-PDU-02-32 | [branch#032] [A] current
6-DaHall 1-PDU-02-33 | [branch#033] [A] current
6-DaHall 1-PDU-02-34 | [branch#034] [A] current
6-DaHall 1-PDU-02-35 | [branch#035] [A] current
6-DaHall 1-PDU-02-36 | [branch#036] [A] current
6-DaHall 1-PDU-02-37 | [branch#037] [A] current
6-DaHall 1-PDU-02-38 | [branch#038] [A] current
6-DaHall 1-PDU-02-39 | [branch#039] [A] current
6-DaHall 1-PDU-02-40 | [branch#040] [A] current
6-DaHall 1-PDU-02-41 | [branch#041] [A] current
6-DaHall 1-PDU-02-42 | [branch#042] [A] current
6-DaHall 1-PDU-02-43 | [branch#043] [A] current
6-DaHall 1-PDU-02-44 | [branch#044] [A] current
6-DaHall 1-PDU-02-45 | [branch#045] [A] current
6-DaHall 1-PDU-02-46 | [branch#046] [A] current
6-DaHall 1-PDU-02-47 | [branch#047] [A] current
6-DaHall 1-PDU-02-48 | [branch#048] [A] current
6-DaHall 1-PDU-02-49 | [branch#049] [A] current
6-DaHall 1-PDU-02-50 | [branch#050] [A] current
6-DaHall 1-PDU-03-01 | [branch#001] [A] current
6-DaHall 1-PDU-03-02 | [branch#002] [A] current
6-DaHall 1-PDU-03-03 | [branch#003] [A] current
6-DaHall 1-PDU-03-04 | [branch#004] [A] current
6-DaHall 1-PDU-03-05 | [branch#005] [A] current
6-DaHall 1-PDU-03-06 | [branch#006] [A] current
6-DaHall 1-PDU-03-07 | [branch#007] [A] current
6-DaHall 1-PDU-03-08 | [branch#008] [A] current
6-DaHall 1-PDU-03-09 | [branch#009] [A] current
6-DaHall 1-PDU-03-10 | [branch#010] [A] current
6-DaHall 1-PDU-03-11 | [branch#011] [A] current
6-DaHall 1-PDU-03-12 | [branch#012] [A] current
6-DaHall 1-PDU-03-13 | [branch#013] [A] current
6-DaHall 1-PDU-03-14 | [branch#014] [A] current
6-DaHall 1-PDU-03-15 | [branch#015] [A] current
6-DaHall 1-PDU-03-16 | [branch#016] [A] current
6-DaHall 1-PDU-03-17 | [branch#017] [A] current
6-DaHall 1-PDU-03-18 | [branch#018] [A] current
6-DaHall 1-PDU-03-19 | [branch#019] [A] current
6-DaHall 1-PDU-03-20 | [branch#020] [A] current
6-DaHall 1-PDU-03-21 | [branch#021] [A] current
6-DaHall 1-PDU-03-22 | [branch#022] [A] current
6-DaHall 1-PDU-03-23 | [branch#023] [A] current
6-DaHall 1-PDU-03-24 | [branch#024] [A] current
6-DaHall 1-PDU-03-25 | [branch#025] [A] current
6-DaHall 1-PDU-03-26 | [branch#026] [A] current
6-DaHall 1-PDU-03-27 | [branch#027] [A] current
6-DaHall 1-PDU-03-28 | [branch#028] [A] current
6-DaHall 1-PDU-03-29 | [branch#029] [A] current
6-DaHall 1-PDU-03-30 | [branch#030] [A] current
6-DaHall 1-PDU-03-31 | [branch#031] [A] current
6-DaHall 1-PDU-03-32 | [branch#032] [A] current
6-DaHall 1-PDU-03-33 | [branch#033] [A] current
6-DaHall 1-PDU-03-34 | [branch#034] [A] current
6-DaHall 1-PDU-03-35 | [branch#035] [A] current
6-DaHall 1-PDU-03-36 | [branch#036] [A] current
6-DaHall 1-PDU-03-37 | [branch#037] [A] current
6-DaHall 1-PDU-03-38 | [branch#038] [A] current
6-DaHall 1-PDU-03-39 | [branch#039] [A] current
6-DaHall 1-PDU-03-40 | [branch#040] [A] current
6-DaHall 1-PDU-03-41 | [branch#041] [A] current
6-DaHall 1-PDU-03-42 | [branch#042] [A] current
6-DaHall 1-PDU-03-43 | [branch#043] [A] current
6-DaHall 1-PDU-03-44 | [branch#044] [A] current
6-DaHall 1-PDU-03-45 | [branch#045] [A] current
6-DaHall 1-PDU-03-46 | [branch#046] [A] current
6-DaHall 1-PDU-03-47 | [branch#047] [A] current
6-DaHall 1-PDU-03-48 | [branch#048] [A] current
6-DaHall 1-PDU-03-49 | [branch#049] [A] current
6-DaHall 1-PDU-03-50 | [branch#050] [A] current
6-DaHall 1-PDU-04-01 | [branch#001] [A] current
6-DaHall 1-PDU-04-02 | [branch#002] [A] current
6-DaHall 1-PDU-04-03 | [branch#003] [A] current
6-DaHall 1-PDU-04-04 | [branch#004] [A] current
6-DaHall 1-PDU-04-05 | [branch#005] [A] current
6-DaHall 1-PDU-04-06 | [branch#006] [A] current
6-DaHall 1-PDU-04-07 | [branch#007] [A] current
6-DaHall 1-PDU-04-08 | [branch#008] [A] current
6-DaHall 1-PDU-04-09 | [branch#009] [A] current
6-DaHall 1-PDU-04-10 | [branch#010] [A] current
6-DaHall 1-PDU-04-11 | [branch#011] [A] current
6-DaHall 1-PDU-04-12 | [branch#012] [A] current
6-DaHall 1-PDU-04-13 | [branch#013] [A] current
6-DaHall 1-PDU-04-14 | [branch#014] [A] current
6-DaHall 1-PDU-04-15 | [branch#015] [A] current
6-DaHall 1-PDU-04-16 | [branch#016] [A] current
6-DaHall 1-PDU-04-17 | [branch#017] [A] current
6-DaHall 1-PDU-04-18 | [branch#018] [A] current
6-DaHall 1-PDU-04-19 | [branch#019] [A] current
6-DaHall 1-PDU-04-20 | [branch#020] [A] current
6-DaHall 1-PDU-04-21 | [branch#021] [A] current
6-DaHall 1-PDU-04-22 | [branch#022] [A] current
6-DaHall 1-PDU-04-23 | [branch#023] [A] current
6-DaHall 1-PDU-04-24 | [branch#024] [A] current
6-DaHall 1-PDU-04-25 | [branch#025] [A] current
6-DaHall 1-PDU-04-26 | [branch#026] [A] current
6-DaHall 1-PDU-04-27 | [branch#027] [A] current
6-DaHall 1-PDU-04-28 | [branch#028] [A] current
6-DaHall 1-PDU-04-29 | [branch#029] [A] current
6-DaHall 1-PDU-04-30 | [branch#030] [A] current
6-DaHall 1-PDU-04-31 | [branch#031] [A] current
6-DaHall 1-PDU-04-32 | [branch#032] [A] current
6-DaHall 1-PDU-04-33 | [branch#033] [A] current
6-DaHall 1-PDU-04-34 | [branch#034] [A] current
6-DaHall 1-PDU-04-35 | [branch#035] [A] current
6-DaHall 1-PDU-04-36 | [branch#036] [A] current
6-DaHall 1-PDU-04-37 | [branch#037] [A] current
6-DaHall 1-PDU-04-38 | [branch#038] [A] current
6-DaHall 1-PDU-04-39 | [branch#039] [A] current
6-DaHall 1-PDU-04-40 | [branch#040] [A] current
6-DaHall 1-PDU-04-41 | [branch#041] [A] current
6-DaHall 1-PDU-04-42 | [branch#042] [A] current
6-DaHall 1-PDU-04-43 | [branch#043] [A] current
6-DaHall 1-PDU-04-44 | [branch#044] [A] current
6-DaHall 1-PDU-04-45 | [branch#045] [A] current
6-DaHall 1-PDU-04-46 | [branch#046] [A] current
6-DaHall 1-PDU-04-47 | [branch#047] [A] current
6-DaHall 1-PDU-04-48 | [branch#048] [A] current
6-DaHall 1-PDU-04-49 | [branch#049] [A] current
6-DaHall 1-PDU-04-50 | [branch#050] [A] current
6-DaHall 1-PDU-05-01 | [branch#001] [A] current
6-DaHall 1-PDU-05-02 | [branch#002] [A] current
6-DaHall 1-PDU-05-03 | [branch#003] [A] current
6-DaHall 1-PDU-05-04 | [branch#004] [A] current
6-DaHall 1-PDU-05-05 | [branch#005] [A] current
6-DaHall 1-PDU-05-06 | [branch#006] [A] current
6-DaHall 1-PDU-05-07 | [branch#007] [A] current
6-DaHall 1-PDU-05-08 | [branch#008] [A] current
6-DaHall 1-PDU-05-09 | [branch#009] [A] current
6-DaHall 1-PDU-05-10 | [branch#010] [A] current
6-DaHall 1-PDU-05-11 | [branch#011] [A] current
6-DaHall 1-PDU-05-12 | [branch#012] [A] current
6-DaHall 1-PDU-05-13 | [branch#013] [A] current
6-DaHall 1-PDU-05-14 | [branch#014] [A] current
6-DaHall 1-PDU-05-15 | [branch#015] [A] current
6-DaHall 1-PDU-05-16 | [branch#016] [A] current
6-DaHall 1-PDU-05-17 | [branch#017] [A] current
6-DaHall 1-PDU-05-18 | [branch#018] [A] current
6-DaHall 1-PDU-05-19 | [branch#019] [A] current
6-DaHall 1-PDU-05-20 | [branch#020] [A] current
6-DaHall 1-PDU-05-21 | [branch#021] [A] current
6-DaHall 1-PDU-05-22 | [branch#022] [A] current
6-DaHall 1-PDU-05-23 | [branch#023] [A] current
6-DaHall 1-PDU-05-24 | [branch#024] [A] current
6-DaHall 1-PDU-05-25 | [branch#025] [A] current
6-DaHall 1-PDU-05-26 | [branch#026] [A] current
6-DaHall 1-PDU-05-27 | [branch#027] [A] current
6-DaHall 1-PDU-05-28 | [branch#028] [A] current
6-DaHall 1-PDU-05-29 | [branch#029] [A] current
6-DaHall 1-PDU-05-30 | [branch#030] [A] current
6-DaHall 1-PDU-05-31 | [branch#031] [A] current
6-DaHall 1-PDU-05-32 | [branch#032] [A] current
6-DaHall 1-PDU-05-33 | [branch#033] [A] current
6-DaHall 1-PDU-05-34 | [branch#034] [A] current
6-DaHall 1-PDU-05-35 | [branch#035] [A] current
6-DaHall 1-PDU-05-36 | [branch#036] [A] current
6-DaHall 1-PDU-05-37 | [branch#037] [A] current
6-DaHall 1-PDU-05-38 | [branch#038] [A] current
6-DaHall 1-PDU-05-39 | [branch#039] [A] current
6-DaHall 1-PDU-05-40 | [branch#040] [A] current
6-DaHall 1-PDU-05-41 | [branch#041] [A] current
6-DaHall 1-PDU-05-42 | [branch#042] [A] current
6-DaHall 1-PDU-05-43 | [branch#043] [A] current
6-DaHall 1-PDU-05-44 | [branch#044] [A] current
6-DaHall 1-PDU-05-45 | [branch#045] [A] current
6-DaHall 1-PDU-05-46 | [branch#046] [A] current
6-DaHall 1-PDU-05-47 | [branch#047] [A] current
6-DaHall 1-PDU-05-48 | [branch#048] [A] current
6-DaHall 1-PDU-05-49 | [branch#049] [A] current
6-DaHall 1-PDU-05-50 | [branch#050] [A] current
6-DaHall 1-PDU-05-51 | [branch#051] [A] current
6-DaHall 1-PDU-05-52 | [branch#052] [A] current
6-DaHall 1-PDU-05-53 | [branch#053] [A] current
6-DaHall 1-PDU-05-54 | [branch#054] [A] current
6-DaHall 1-PDU-06-01 | [branch#001] [A] current
6-DaHall 1-PDU-06-02 | [branch#002] [A] current
6-DaHall 1-PDU-06-03 | [branch#003] [A] current
6-DaHall 1-PDU-06-04 | [branch#004] [A] current
6-DaHall 1-PDU-06-05 | [branch#005] [A] current
6-DaHall 1-PDU-06-06 | [branch#006] [A] current
6-DaHall 1-PDU-06-07 | [branch#007] [A] current
6-DaHall 1-PDU-06-08 | [branch#008] [A] current
6-DaHall 1-PDU-06-09 | [branch#009] [A] current
6-DaHall 1-PDU-06-10 | [branch#010] [A] current
6-DaHall 1-PDU-06-11 | [branch#011] [A] current
6-DaHall 1-PDU-06-12 | [branch#012] [A] current
6-DaHall 1-PDU-06-13 | [branch#013] [A] current
6-DaHall 1-PDU-06-14 | [branch#014] [A] current
6-DaHall 1-PDU-06-15 | [branch#015] [A] current
6-DaHall 1-PDU-06-16 | [branch#016] [A] current
6-DaHall 1-PDU-06-17 | [branch#017] [A] current
6-DaHall 1-PDU-06-18 | [branch#018] [A] current
6-DaHall 1-PDU-06-19 | [branch#019] [A] current
6-DaHall 1-PDU-06-20 | [branch#020] [A] current
6-DaHall 1-PDU-06-21 | [branch#021] [A] current
6-DaHall 1-PDU-06-22 | [branch#022] [A] current
6-DaHall 1-PDU-06-23 | [branch#023] [A] current
6-DaHall 1-PDU-06-24 | [branch#024] [A] current
6-DaHall 1-PDU-06-25 | [branch#025] [A] current
6-DaHall 1-PDU-06-26 | [branch#026] [A] current
6-DaHall 1-PDU-06-27 | [branch#027] [A] current
6-DaHall 1-PDU-06-28 | [branch#028] [A] current
6-DaHall 1-PDU-06-29 | [branch#029] [A] current
6-DaHall 1-PDU-06-30 | [branch#030] [A] current
6-DaHall 1-PDU-06-31 | [branch#031] [A] current
6-DaHall 1-PDU-06-32 | [branch#032] [A] current
6-DaHall 1-PDU-06-33 | [branch#033] [A] current
6-DaHall 1-PDU-06-34 | [branch#034] [A] current
6-DaHall 1-PDU-06-35 | [branch#035] [A] current
6-DaHall 1-PDU-06-36 | [branch#036] [A] current
6-DaHall 1-PDU-06-37 | [branch#037] [A] current
6-DaHall 1-PDU-06-38 | [branch#038] [A] current
6-DaHall 1-PDU-06-39 | [branch#039] [A] current
6-DaHall 1-PDU-06-40 | [branch#040] [A] current
6-DaHall 1-PDU-06-41 | [branch#041] [A] current
6-DaHall 1-PDU-06-42 | [branch#042] [A] current
6-DaHall 1-PDU-06-43 | [branch#043] [A] current
6-DaHall 1-PDU-06-44 | [branch#044] [A] current
6-DaHall 1-PDU-06-45 | [branch#045] [A] current
6-DaHall 1-PDU-06-46 | [branch#046] [A] current
6-DaHall 1-PDU-06-47 | [branch#047] [A] current
6-DaHall 1-PDU-06-48 | [branch#048] [A] current
6-DaHall 1-PDU-06-49 | [branch#049] [A] current
6-DaHall 1-PDU-06-50 | [branch#050] [A] current
6-DaHall 1-PDU-06-51 | [branch#051] [A] current
6-DaHall 1-PDU-06-52 | [branch#052] [A] current
6-DaHall 1-PDU-06-53 | [branch#053] [A] current
6-DaHall 1-PDU-06-54 | [branch#054] [A] current
6-DaHall 1-PDU-07-01 | [branch#001] [A] current
6-DaHall 1-PDU-07-02 | [branch#002] [A] current
6-DaHall 1-PDU-07-03 | [branch#003] [A] current
6-DaHall 1-PDU-07-04 | [branch#004] [A] current
6-DaHall 1-PDU-07-05 | [branch#005] [A] current
6-DaHall 1-PDU-07-06 | [branch#006] [A] current
6-DaHall 1-PDU-07-07 | [branch#007] [A] current
6-DaHall 1-PDU-07-08 | [branch#008] [A] current
6-DaHall 1-PDU-07-09 | [branch#009] [A] current
6-DaHall 1-PDU-07-10 | [branch#010] [A] current
6-DaHall 1-PDU-07-11 | [branch#011] [A] current
6-DaHall 1-PDU-07-12 | [branch#012] [A] current
6-DaHall 1-PDU-07-13 | [branch#013] [A] current
6-DaHall 1-PDU-07-14 | [branch#014] [A] current
6-DaHall 1-PDU-07-15 | [branch#015] [A] current
6-DaHall 1-PDU-07-16 | [branch#016] [A] current
6-DaHall 1-PDU-07-17 | [branch#017] [A] current
6-DaHall 1-PDU-07-18 | [branch#018] [A] current
6-DaHall 1-PDU-07-19 | [branch#019] [A] current
6-DaHall 1-PDU-07-20 | [branch#020] [A] current
6-DaHall 1-PDU-07-21 | [branch#021] [A] current
6-DaHall 1-PDU-07-22 | [branch#022] [A] current
6-DaHall 1-PDU-07-23 | [branch#023] [A] current
6-DaHall 1-PDU-07-24 | [branch#024] [A] current
6-DaHall 1-PDU-07-25 | [branch#025] [A] current
6-DaHall 1-PDU-07-26 | [branch#026] [A] current
6-DaHall 1-PDU-07-27 | [branch#027] [A] current
6-DaHall 1-PDU-07-28 | [branch#028] [A] current
6-DaHall 1-PDU-07-29 | [branch#029] [A] current
6-DaHall 1-PDU-07-30 | [branch#030] [A] current
6-DaHall 1-PDU-07-31 | [branch#031] [A] current
6-DaHall 1-PDU-07-32 | [branch#032] [A] current
6-DaHall 1-PDU-07-33 | [branch#033] [A] current
6-DaHall 1-PDU-07-34 | [branch#034] [A] current
6-DaHall 1-PDU-07-35 | [branch#035] [A] current
6-DaHall 1-PDU-07-36 | [branch#036] [A] current
6-DaHall 1-PDU-07-37 | [branch#037] [A] current
6-DaHall 1-PDU-07-38 | [branch#038] [A] current
6-DaHall 1-PDU-07-39 | [branch#039] [A] current
6-DaHall 1-PDU-07-40 | [branch#040] [A] current
6-DaHall 1-PDU-07-41 | [branch#041] [A] current
6-DaHall 1-PDU-07-42 | [branch#042] [A] current
6-DaHall 1-PDU-07-43 | [branch#043] [A] current
6-DaHall 1-PDU-07-44 | [branch#044] [A] current
6-DaHall 1-PDU-07-45 | [branch#045] [A] current
6-DaHall 1-PDU-07-46 | [branch#046] [A] current
6-DaHall 1-PDU-07-47 | [branch#047] [A] current
6-DaHall 1-PDU-07-48 | [branch#048] [A] current
6-DaHall 1-PDU-07-49 | [branch#049] [A] current
6-DaHall 1-PDU-07-50 | [branch#050] [A] current
6-DaHall 1-PDU-07-51 | [branch#051] [A] current
6-DaHall 1-PDU-07-52 | [branch#052] [A] current
6-DaHall 1-PDU-07-53 | [branch#053] [A] current
6-DaHall 1-PDU-07-54 | [branch#054] [A] current
6-DaHall 1-PDU-08-01 | [branch#001] [A] current
6-DaHall 1-PDU-08-02 | [branch#002] [A] current
6-DaHall 1-PDU-08-03 | [branch#003] [A] current
6-DaHall 1-PDU-08-04 | [branch#004] [A] current
6-DaHall 1-PDU-08-05 | [branch#005] [A] current
6-DaHall 1-PDU-08-06 | [branch#006] [A] current
6-DaHall 1-PDU-08-07 | [branch#007] [A] current
6-DaHall 1-PDU-08-08 | [branch#008] [A] current
6-DaHall 1-PDU-08-09 | [branch#009] [A] current
6-DaHall 1-PDU-08-10 | [branch#010] [A] current
6-DaHall 1-PDU-08-11 | [branch#011] [A] current
6-DaHall 1-PDU-08-12 | [branch#012] [A] current
6-DaHall 1-PDU-08-13 | [branch#013] [A] current
6-DaHall 1-PDU-08-14 | [branch#014] [A] current
6-DaHall 1-PDU-08-15 | [branch#015] [A] current
6-DaHall 1-PDU-08-16 | [branch#016] [A] current
6-DaHall 1-PDU-08-17 | [branch#017] [A] current
6-DaHall 1-PDU-08-18 | [branch#018] [A] current
6-DaHall 1-PDU-08-19 | [branch#019] [A] current
6-DaHall 1-PDU-08-20 | [branch#020] [A] current
6-DaHall 1-PDU-08-21 | [branch#021] [A] current
6-DaHall 1-PDU-08-22 | [branch#022] [A] current
6-DaHall 1-PDU-08-23 | [branch#023] [A] current
6-DaHall 1-PDU-08-24 | [branch#024] [A] current
6-DaHall 1-PDU-08-25 | [branch#025] [A] current
6-DaHall 1-PDU-08-26 | [branch#026] [A] current
6-DaHall 1-PDU-08-27 | [branch#027] [A] current
6-DaHall 1-PDU-08-28 | [branch#028] [A] current
6-DaHall 1-PDU-08-29 | [branch#029] [A] current
6-DaHall 1-PDU-08-30 | [branch#030] [A] current
6-DaHall 1-PDU-08-31 | [branch#031] [A] current
6-DaHall 1-PDU-08-32 | [branch#032] [A] current
6-DaHall 1-PDU-08-33 | [branch#033] [A] current
6-DaHall 1-PDU-08-34 | [branch#034] [A] current
6-DaHall 1-PDU-08-35 | [branch#035] [A] current
6-DaHall 1-PDU-08-36 | [branch#036] [A] current
6-DaHall 1-PDU-08-37 | [branch#037] [A] current
6-DaHall 1-PDU-08-38 | [branch#038] [A] current
6-DaHall 1-PDU-08-39 | [branch#039] [A] current
6-DaHall 1-PDU-08-40 | [branch#040] [A] current
6-DaHall 1-PDU-08-41 | [branch#041] [A] current
6-DaHall 1-PDU-08-42 | [branch#042] [A] current
6-DaHall 1-PDU-08-43 | [branch#043] [A] current
6-DaHall 1-PDU-08-44 | [branch#044] [A] current
6-DaHall 1-PDU-08-45 | [branch#045] [A] current
6-DaHall 1-PDU-08-46 | [branch#046] [A] current
6-DaHall 1-PDU-08-47 | [branch#047] [A] current
6-DaHall 1-PDU-08-48 | [branch#048] [A] current
6-DaHall 1-PDU-08-49 | [branch#049] [A] current
6-DaHall 1-PDU-08-50 | [branch#050] [A] current
6-DaHall 1-PDU-08-51 | [branch#051] [A] current
6-DaHall 1-PDU-08-52 | [branch#052] [A] current
6-DaHall 1-PDU-08-53 | [branch#053] [A] current
6-DaHall 1-PDU-08-54 | [branch#054] [A] current
6-DaHall 1-PDU-09-01 | [branch#001] [A] current
6-DaHall 1-PDU-09-02 | [branch#002] [A] current
6-DaHall 1-PDU-09-03 | [branch#003] [A] current
6-DaHall 1-PDU-09-04 | [branch#004] [A] current
6-DaHall 1-PDU-09-05 | [branch#005] [A] current
6-DaHall 1-PDU-09-06 | [branch#006] [A] current
6-DaHall 1-PDU-09-07 | [branch#007] [A] current
6-DaHall 1-PDU-09-08 | [branch#008] [A] current
6-DaHall 1-PDU-09-09 | [branch#009] [A] current
6-DaHall 1-PDU-09-10 | [branch#010] [A] current
6-DaHall 1-PDU-09-11 | [branch#011] [A] current
6-DaHall 1-PDU-09-12 | [branch#012] [A] current
6-DaHall 1-PDU-09-13 | [branch#013] [A] current
6-DaHall 1-PDU-09-14 | [branch#014] [A] current
6-DaHall 1-PDU-09-15 | [branch#015] [A] current
6-DaHall 1-PDU-09-16 | [branch#016] [A] current
6-DaHall 1-PDU-09-17 | [branch#017] [A] current
6-DaHall 1-PDU-09-18 | [branch#018] [A] current
6-DaHall 1-PDU-09-19 | [branch#019] [A] current
6-DaHall 1-PDU-09-20 | [branch#020] [A] current
6-DaHall 1-PDU-09-21 | [branch#021] [A] current
6-DaHall 1-PDU-09-22 | [branch#022] [A] current
6-DaHall 1-PDU-09-23 | [branch#023] [A] current
6-DaHall 1-PDU-09-24 | [branch#024] [A] current
6-DaHall 1-PDU-09-25 | [branch#025] [A] current
6-DaHall 1-PDU-09-26 | [branch#026] [A] current
6-DaHall 1-PDU-09-27 | [branch#027] [A] current
6-DaHall 1-PDU-09-28 | [branch#028] [A] current
6-DaHall 1-PDU-09-29 | [branch#029] [A] current
6-DaHall 1-PDU-09-30 | [branch#030] [A] current
6-DaHall 1-PDU-09-31 | [branch#031] [A] current
6-DaHall 1-PDU-09-32 | [branch#032] [A] current
6-DaHall 1-PDU-09-33 | [branch#033] [A] current
6-DaHall 1-PDU-09-34 | [branch#034] [A] current
6-DaHall 1-PDU-09-35 | [branch#035] [A] current
6-DaHall 1-PDU-09-36 | [branch#036] [A] current
6-DaHall 1-PDU-09-37 | [branch#037] [A] current
6-DaHall 1-PDU-09-38 | [branch#038] [A] current
6-DaHall 1-PDU-09-39 | [branch#039] [A] current
6-DaHall 1-PDU-09-40 | [branch#040] [A] current
6-DaHall 1-PDU-09-41 | [branch#041] [A] current
6-DaHall 1-PDU-09-42 | [branch#042] [A] current
6-DaHall 1-PDU-09-43 | [branch#043] [A] current
6-DaHall 1-PDU-09-44 | [branch#044] [A] current
6-DaHall 1-PDU-09-45 | [branch#045] [A] current
6-DaHall 1-PDU-09-46 | [branch#046] [A] current
6-DaHall 1-PDU-09-47 | [branch#047] [A] current
6-DaHall 1-PDU-09-48 | [branch#048] [A] current
6-DaHall 1-PDU-09-49 | [branch#049] [A] current
6-DaHall 1-PDU-09-50 | [branch#050] [A] current
6-DaHall 1-PDU-10-01 | [branch#001] [A] current
6-DaHall 1-PDU-10-02 | [branch#002] [A] current
6-DaHall 1-PDU-10-03 | [branch#003] [A] current
6-DaHall 1-PDU-10-04 | [branch#004] [A] current
6-DaHall 1-PDU-10-05 | [branch#005] [A] current
6-DaHall 1-PDU-10-06 | [branch#006] [A] current
6-DaHall 1-PDU-10-07 | [branch#007] [A] current
6-DaHall 1-PDU-10-08 | [branch#008] [A] current
6-DaHall 1-PDU-10-09 | [branch#009] [A] current
6-DaHall 1-PDU-10-10 | [branch#010] [A] current
6-DaHall 1-PDU-10-11 | [branch#011] [A] current
6-DaHall 1-PDU-10-12 | [branch#012] [A] current
6-DaHall 1-PDU-10-13 | [branch#013] [A] current
6-DaHall 1-PDU-10-14 | [branch#014] [A] current
6-DaHall 1-PDU-10-15 | [branch#015] [A] current
6-DaHall 1-PDU-10-16 | [branch#016] [A] current
6-DaHall 1-PDU-10-17 | [branch#017] [A] current
6-DaHall 1-PDU-10-18 | [branch#018] [A] current
6-DaHall 1-PDU-10-19 | [branch#019] [A] current
6-DaHall 1-PDU-10-20 | [branch#020] [A] current
6-DaHall 1-PDU-10-21 | [branch#021] [A] current
6-DaHall 1-PDU-10-22 | [branch#022] [A] current
6-DaHall 1-PDU-10-23 | [branch#023] [A] current
6-DaHall 1-PDU-10-24 | [branch#024] [A] current
6-DaHall 1-PDU-10-25 | [branch#025] [A] current
6-DaHall 1-PDU-10-26 | [branch#026] [A] current
6-DaHall 1-PDU-10-27 | [branch#027] [A] current
6-DaHall 1-PDU-10-28 | [branch#028] [A] current
6-DaHall 1-PDU-10-29 | [branch#029] [A] current
6-DaHall 1-PDU-10-30 | [branch#030] [A] current
6-DaHall 1-PDU-10-31 | [branch#031] [A] current
6-DaHall 1-PDU-10-32 | [branch#032] [A] current
6-DaHall 1-PDU-10-33 | [branch#033] [A] current
6-DaHall 1-PDU-10-34 | [branch#034] [A] current
6-DaHall 1-PDU-10-35 | [branch#035] [A] current
6-DaHall 1-PDU-10-36 | [branch#036] [A] current
6-DaHall 1-PDU-10-37 | [branch#037] [A] current
6-DaHall 1-PDU-10-38 | [branch#038] [A] current
6-DaHall 1-PDU-10-39 | [branch#039] [A] current
6-DaHall 1-PDU-10-40 | [branch#040] [A] current
6-DaHall 1-PDU-10-41 | [branch#041] [A] current
6-DaHall 1-PDU-10-42 | [branch#042] [A] current
6-DaHall 1-PDU-10-43 | [branch#043] [A] current
6-DaHall 1-PDU-10-44 | [branch#044] [A] current
6-DaHall 1-PDU-10-45 | [branch#045] [A] current
6-DaHall 1-PDU-10-46 | [branch#046] [A] current
6-DaHall 1-PDU-10-47 | [branch#047] [A] current
6-DaHall 1-PDU-10-48 | [branch#048] [A] current
6-DaHall 1-PDU-10-49 | [branch#049] [A] current
6-DaHall 1-PDU-10-50 | [branch#050] [A] current
6-DaHall 1-PDU-11-01 | [branch#001] [A] current
6-DaHall 1-PDU-11-02 | [branch#002] [A] current
6-DaHall 1-PDU-11-03 | [branch#003] [A] current
6-DaHall 1-PDU-11-04 | [branch#004] [A] current
6-DaHall 1-PDU-11-05 | [branch#005] [A] current
6-DaHall 1-PDU-11-06 | [branch#006] [A] current
6-DaHall 1-PDU-11-07 | [branch#007] [A] current
6-DaHall 1-PDU-11-08 | [branch#008] [A] current
6-DaHall 1-PDU-11-09 | [branch#009] [A] current
6-DaHall 1-PDU-11-10 | [branch#010] [A] current
6-DaHall 1-PDU-11-11 | [branch#011] [A] current
6-DaHall 1-PDU-11-12 | [branch#012] [A] current
6-DaHall 1-PDU-11-13 | [branch#013] [A] current
6-DaHall 1-PDU-11-14 | [branch#014] [A] current
6-DaHall 1-PDU-11-15 | [branch#015] [A] current
6-DaHall 1-PDU-11-16 | [branch#016] [A] current
6-DaHall 1-PDU-11-17 | [branch#017] [A] current
6-DaHall 1-PDU-11-18 | [branch#018] [A] current
6-DaHall 1-PDU-11-19 | [branch#019] [A] current
6-DaHall 1-PDU-11-20 | [branch#020] [A] current
6-DaHall 1-PDU-11-21 | [branch#021] [A] current
6-DaHall 1-PDU-11-22 | [branch#022] [A] current
6-DaHall 1-PDU-11-23 | [branch#023] [A] current
6-DaHall 1-PDU-11-24 | [branch#024] [A] current
6-DaHall 1-PDU-11-25 | [branch#025] [A] current
6-DaHall 1-PDU-11-26 | [branch#026] [A] current
6-DaHall 1-PDU-11-27 | [branch#027] [A] current
6-DaHall 1-PDU-11-28 | [branch#028] [A] current
6-DaHall 1-PDU-11-29 | [branch#029] [A] current
6-DaHall 1-PDU-11-30 | [branch#030] [A] current
6-DaHall 1-PDU-11-31 | [branch#031] [A] current
6-DaHall 1-PDU-11-32 | [branch#032] [A] current
6-DaHall 1-PDU-11-33 | [branch#033] [A] current
6-DaHall 1-PDU-11-34 | [branch#034] [A] current
6-DaHall 1-PDU-11-35 | [branch#035] [A] current
6-DaHall 1-PDU-11-36 | [branch#036] [A] current
6-DaHall 1-PDU-11-37 | [branch#037] [A] current
6-DaHall 1-PDU-11-38 | [branch#038] [A] current
6-DaHall 1-PDU-11-39 | [branch#039] [A] current
6-DaHall 1-PDU-11-40 | [branch#040] [A] current
6-DaHall 1-PDU-11-41 | [branch#041] [A] current
6-DaHall 1-PDU-11-42 | [branch#042] [A] current
6-DaHall 1-PDU-11-43 | [branch#043] [A] current
6-DaHall 1-PDU-11-44 | [branch#044] [A] current
6-DaHall 1-PDU-11-45 | [branch#045] [A] current
6-DaHall 1-PDU-11-46 | [branch#046] [A] current
6-DaHall 1-PDU-11-47 | [branch#047] [A] current
6-DaHall 1-PDU-11-48 | [branch#048] [A] current
6-DaHall 1-PDU-11-49 | [branch#049] [A] current
6-DaHall 1-PDU-11-50 | [branch#050] [A] current
6-DaHall 1-PDU-12-01 | [branch#001] [A] current
6-DaHall 1-PDU-12-02 | [branch#002] [A] current
6-DaHall 1-PDU-12-03 | [branch#003] [A] current
6-DaHall 1-PDU-12-04 | [branch#004] [A] current
6-DaHall 1-PDU-12-05 | [branch#005] [A] current
6-DaHall 1-PDU-12-06 | [branch#006] [A] current
6-DaHall 1-PDU-12-07 | [branch#007] [A] current
6-DaHall 1-PDU-12-08 | [branch#008] [A] current
6-DaHall 1-PDU-12-09 | [branch#009] [A] current
6-DaHall 1-PDU-12-10 | [branch#010] [A] current
6-DaHall 1-PDU-12-11 | [branch#011] [A] current
6-DaHall 1-PDU-12-12 | [branch#012] [A] current
6-DaHall 1-PDU-12-13 | [branch#013] [A] current
6-DaHall 1-PDU-12-14 | [branch#014] [A] current
6-DaHall 1-PDU-12-15 | [branch#015] [A] current
6-DaHall 1-PDU-12-16 | [branch#016] [A] current
6-DaHall 1-PDU-12-17 | [branch#017] [A] current
6-DaHall 1-PDU-12-18 | [branch#018] [A] current
6-DaHall 1-PDU-12-19 | [branch#019] [A] current
6-DaHall 1-PDU-12-20 | [branch#020] [A] current
6-DaHall 1-PDU-12-21 | [branch#021] [A] current
6-DaHall 1-PDU-12-22 | [branch#022] [A] current
6-DaHall 1-PDU-12-23 | [branch#023] [A] current
6-DaHall 1-PDU-12-24 | [branch#024] [A] current
6-DaHall 1-PDU-12-25 | [branch#025] [A] current
6-DaHall 1-PDU-12-26 | [branch#026] [A] current
6-DaHall 1-PDU-12-27 | [branch#027] [A] current
6-DaHall 1-PDU-12-28 | [branch#028] [A] current
6-DaHall 1-PDU-12-29 | [branch#029] [A] current
6-DaHall 1-PDU-12-30 | [branch#030] [A] current
6-DaHall 1-PDU-12-31 | [branch#031] [A] current
6-DaHall 1-PDU-12-32 | [branch#032] [A] current
6-DaHall 1-PDU-12-33 | [branch#033] [A] current
6-DaHall 1-PDU-12-34 | [branch#034] [A] current
6-DaHall 1-PDU-12-35 | [branch#035] [A] current
6-DaHall 1-PDU-12-36 | [branch#036] [A] current
6-DaHall 1-PDU-12-37 | [branch#037] [A] current
6-DaHall 1-PDU-12-38 | [branch#038] [A] current
6-DaHall 1-PDU-12-39 | [branch#039] [A] current
6-DaHall 1-PDU-12-40 | [branch#040] [A] current
6-DaHall 1-PDU-12-41 | [branch#041] [A] current
6-DaHall 1-PDU-12-42 | [branch#042] [A] current
6-DaHall 1-PDU-12-43 | [branch#043] [A] current
6-DaHall 1-PDU-12-44 | [branch#044] [A] current
6-DaHall 1-PDU-12-45 | [branch#045] [A] current
6-DaHall 1-PDU-12-46 | [branch#046] [A] current
6-DaHall 1-PDU-12-47 | [branch#047] [A] current
6-DaHall 1-PDU-12-48 | [branch#048] [A] current
6-DaHall 1-PDU-12-49 | [branch#049] [A] current
6-DaHall 1-PDU-12-50 | [branch#050] [A] current
6-DaHall 1-PDU-13-01 | [branch#001] [A] current
6-DaHall 1-PDU-13-02 | [branch#002] [A] current
6-DaHall 1-PDU-13-03 | [branch#003] [A] current
6-DaHall 1-PDU-13-04 | [branch#004] [A] current
6-DaHall 1-PDU-13-05 | [branch#005] [A] current
6-DaHall 1-PDU-13-06 | [branch#006] [A] current
6-DaHall 1-PDU-13-07 | [branch#007] [A] current
6-DaHall 1-PDU-13-08 | [branch#008] [A] current
6-DaHall 1-PDU-13-09 | [branch#009] [A] current
6-DaHall 1-PDU-13-10 | [branch#010] [A] current
6-DaHall 1-PDU-13-11 | [branch#011] [A] current
6-DaHall 1-PDU-13-12 | [branch#012] [A] current
6-DaHall 1-PDU-13-13 | [branch#013] [A] current
6-DaHall 1-PDU-13-14 | [branch#014] [A] current
6-DaHall 1-PDU-13-15 | [branch#015] [A] current
6-DaHall 1-PDU-13-16 | [branch#016] [A] current
6-DaHall 1-PDU-13-17 | [branch#017] [A] current
6-DaHall 1-PDU-13-18 | [branch#018] [A] current
6-DaHall 1-PDU-13-19 | [branch#019] [A] current
6-DaHall 1-PDU-13-20 | [branch#020] [A] current
6-DaHall 1-PDU-13-21 | [branch#021] [A] current
6-DaHall 1-PDU-13-22 | [branch#022] [A] current
6-DaHall 1-PDU-13-23 | [branch#023] [A] current
6-DaHall 1-PDU-13-24 | [branch#024] [A] current
6-DaHall 1-PDU-13-25 | [branch#025] [A] current
6-DaHall 1-PDU-13-26 | [branch#026] [A] current
6-DaHall 1-PDU-13-27 | [branch#027] [A] current
6-DaHall 1-PDU-13-28 | [branch#028] [A] current
6-DaHall 1-PDU-13-29 | [branch#029] [A] current
6-DaHall 1-PDU-13-30 | [branch#030] [A] current
6-DaHall 1-PDU-13-31 | [branch#031] [A] current
6-DaHall 1-PDU-13-32 | [branch#032] [A] current
6-DaHall 1-PDU-13-33 | [branch#033] [A] current
6-DaHall 1-PDU-13-34 | [branch#034] [A] current
6-DaHall 1-PDU-13-35 | [branch#035] [A] current
6-DaHall 1-PDU-13-36 | [branch#036] [A] current
6-DaHall 1-PDU-13-37 | [branch#037] [A] current
6-DaHall 1-PDU-13-38 | [branch#038] [A] current
6-DaHall 1-PDU-13-39 | [branch#039] [A] current
6-DaHall 1-PDU-13-40 | [branch#040] [A] current
6-DaHall 1-PDU-13-41 | [branch#041] [A] current
6-DaHall 1-PDU-13-42 | [branch#042] [A] current
6-DaHall 1-PDU-13-43 | [branch#043] [A] current
6-DaHall 1-PDU-13-44 | [branch#044] [A] current
6-DaHall 1-PDU-13-45 | [branch#045] [A] current
6-DaHall 1-PDU-13-46 | [branch#046] [A] current
6-DaHall 1-PDU-13-47 | [branch#047] [A] current
6-DaHall 1-PDU-13-48 | [branch#048] [A] current
6-DaHall 1-PDU-13-49 | [branch#049] [A] current
6-DaHall 1-PDU-13-50 | [branch#050] [A] current
6-DaHall 1-PDU-13-51 | [branch#051] [A] current
6-DaHall 1-PDU-13-52 | [branch#052] [A] current
6-DaHall 1-PDU-13-53 | [branch#053] [A] current
6-DaHall 1-PDU-13-54 | [branch#054] [A] current
6-DaHall 1-PDU-14-01 | [branch#001] [A] current
6-DaHall 1-PDU-14-02 | [branch#002] [A] current
6-DaHall 1-PDU-14-03 | [branch#003] [A] current
6-DaHall 1-PDU-14-04 | [branch#004] [A] current
6-DaHall 1-PDU-14-05 | [branch#005] [A] current
6-DaHall 1-PDU-14-06 | [branch#006] [A] current
6-DaHall 1-PDU-14-07 | [branch#007] [A] current
6-DaHall 1-PDU-14-08 | [branch#008] [A] current
6-DaHall 1-PDU-14-09 | [branch#009] [A] current
6-DaHall 1-PDU-14-10 | [branch#010] [A] current
6-DaHall 1-PDU-14-11 | [branch#011] [A] current
6-DaHall 1-PDU-14-12 | [branch#012] [A] current
6-DaHall 1-PDU-14-13 | [branch#013] [A] current
6-DaHall 1-PDU-14-14 | [branch#014] [A] current
6-DaHall 1-PDU-14-15 | [branch#015] [A] current
6-DaHall 1-PDU-14-16 | [branch#016] [A] current
6-DaHall 1-PDU-14-17 | [branch#017] [A] current
6-DaHall 1-PDU-14-18 | [branch#018] [A] current
6-DaHall 1-PDU-14-19 | [branch#019] [A] current
6-DaHall 1-PDU-14-20 | [branch#020] [A] current
6-DaHall 1-PDU-14-21 | [branch#021] [A] current
6-DaHall 1-PDU-14-22 | [branch#022] [A] current
6-DaHall 1-PDU-14-23 | [branch#023] [A] current
6-DaHall 1-PDU-14-24 | [branch#024] [A] current
6-DaHall 1-PDU-14-25 | [branch#025] [A] current
6-DaHall 1-PDU-14-26 | [branch#026] [A] current
6-DaHall 1-PDU-14-27 | [branch#027] [A] current
6-DaHall 1-PDU-14-28 | [branch#028] [A] current
6-DaHall 1-PDU-14-29 | [branch#029] [A] current
6-DaHall 1-PDU-14-30 | [branch#030] [A] current
6-DaHall 1-PDU-14-31 | [branch#031] [A] current
6-DaHall 1-PDU-14-32 | [branch#032] [A] current
6-DaHall 1-PDU-14-33 | [branch#033] [A] current
6-DaHall 1-PDU-14-34 | [branch#034] [A] current
6-DaHall 1-PDU-14-35 | [branch#035] [A] current
6-DaHall 1-PDU-14-36 | [branch#036] [A] current
6-DaHall 1-PDU-14-37 | [branch#037] [A] current
6-DaHall 1-PDU-14-38 | [branch#038] [A] current
6-DaHall 1-PDU-14-39 | [branch#039] [A] current
6-DaHall 1-PDU-14-40 | [branch#040] [A] current
6-DaHall 1-PDU-14-41 | [branch#041] [A] current
6-DaHall 1-PDU-14-42 | [branch#042] [A] current
6-DaHall 1-PDU-14-43 | [branch#043] [A] current
6-DaHall 1-PDU-14-44 | [branch#044] [A] current
6-DaHall 1-PDU-14-45 | [branch#045] [A] current
6-DaHall 1-PDU-14-46 | [branch#046] [A] current
6-DaHall 1-PDU-14-47 | [branch#047] [A] current
6-DaHall 1-PDU-14-48 | [branch#048] [A] current
6-DaHall 1-PDU-14-49 | [branch#049] [A] current
6-DaHall 1-PDU-14-50 | [branch#050] [A] current
6-DaHall 1-PDU-14-51 | [branch#051] [A] current
6-DaHall 1-PDU-14-52 | [branch#052] [A] current
6-DaHall 1-PDU-14-53 | [branch#053] [A] current
6-DaHall 1-PDU-14-54 | [branch#054] [A] current
6-DaHall 1-CEP-05-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
6-DaHall 1-CEP-05-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
6-DaHall 1-CEP-05-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
6-DaHall 1-CEP-05-04 | [branch#004] [R] I1 | [branch#004] [S] I2 | [branch#004] [T] I3
6-DaHall 1-CEP-05-05 | [branch#005] [R] I1 | [branch#005] [S] I2 | [branch#005] [T] I3
6-DaHall 1-CEP-05-06 | [branch#006] [R] I1 | [branch#006] [S] I2 | [branch#006] [T] I3
6-DaHall 1-CEP-05-07 | [branch#007] [R] I1 | [branch#007] [S] I2 | [branch#007] [T] I3
6-DaHall 1-CEP-05-08 | [branch#008] [R] I1 | [branch#008] [S] I2 | [branch#008] [T] I3
6-DaHall 1-CEP-05-09 | [branch#009] [R] I1 | [branch#009] [S] I2 | [branch#009] [T] I3
6-DaHall 1-CEP-05-10 | [branch#010] [R] I1 | [branch#010] [S] I2 | [branch#010] [T] I3
6-DaHall 1-CEP-05-11 | [branch#011] [R] I1 | [branch#011] [S] I2 | [branch#011] [T] I3
6-DaHall 1-CEP-05-12 | [branch#012] [A] current
6-DaHall 1-CEP-05-13 | [branch#013] [A] current
6-DaHall 1-CEP-05-14 | [branch#014] [A] current
6-DaHall 1-CEP-05-15 | [branch#015] [A] current
6-DaHall 1-CEP-05-16 | [branch#016] [A] current
6-DaHall 1-CEP-05-17 | [branch#017] [A] current

## 6층_부하량(월간_MAX)
Date : 2023-11-01 ~ 2023-11-30
6-DaHall 1-CEP-05 | [7 empty] | Main CB 4P 350A
[10 empty] | MAIN 계측값 : | 2.3 | 2.1 | 2.9 | <- 실측값 |  |  | 5-DaHall 1-EH-01
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
5-DaHall 1-CEP-06 | O | ON | 59.42 | 60.51 | 58.78 |  | 4P 150A | #01
| X | OFF | 사 | 용 | 금 | 지 | 4P 50A | #02 | #03 | 4P 50A | 0 | 0 | 0 |  | X | OFF
5-DaHall 1-CRAC-14 (CF CRAC #02) | O | ON | 0 | 0 | 0 |  | 4P 50A | #04 | #05 | 4P 50A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 50A | #06 | #07 | 4P 50A | 0 | 0 | 0 |  | O | OFF | 급배기휀
| X | OFF | 0 | 0 | 0 |  | 4P 50A | #08 | #09 | 4P 50A | 0 | 0 | 0 |  | X | OFF
spare | X | OFF | 0 | 0 | 0 |  | 4P 50A | #10 | #11 | 4P 100A | 53.54 | 53.5 | 66.13 |  | O | ON | 8층 냉방분전반
| O | OFF | 0 |  |  |  | 2P 30A | #12 | #13 | 2P 30A | 0 |  |  |  | O | OFF
| O | OFF |  | 48.86 |  |  | 2P 30A | #14 | #15 | 2P 50A |  | 15 |  |  | O | ON | 7-DaHall 1-EH (7층 가습기 Main)
| O | OFF |  |  | 8 |  | 2P 30A | #16 | #17 | 2P 50A |  |  | 13.74 |  | O | ON | 6-DaHall 1-EH (6층 가습기 Main)
|  | 6층 사무실 | 85.6 | [6 empty] | 총합: | 112.96 | 177.87 | 146.65 | 0
[11 empty] | 437.48 | 85.6 | 19.57%
6-DaHall 1-PDU-13 |  | PDU : SEL1 - 6-1 - A7 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A7-18-6 | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | DE운용실 사무#1 A7-30-8
A7-18-7 | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | DE 출입통제Desk A7-31-1
A7-18-8 | O | ON | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | 6F DE 가청경보 PNL
A7-18-9 | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | OFF | A7-31-3
A7-28-1 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-4
A7-28-2 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | OFF | A7-31-5
A7-28-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | OFF | A7-31-6
A7-28-4 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-7
A7-28-5 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | A7-31-8
A7-28-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | #A7-28-3
A7-28-7 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | OFF | #A7-28-6
A7-28-8 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | OFF | #A7-29-3
A7-29-1 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | OFF | #A7-29-6
A7-29-2 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | A7-21-4(3) (M-14)
A7-29-3 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | A7-21-3(3) (M-13)
A7-29-4 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | A7-21-3(2) (M-13)
A7-29-5 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | A7-21-4(2) (M-14)
A7-29-6 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | OFF | A7-26-8(2)
A7-29-7 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | OFF | A7-26-9(2)
A7-29-8 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A7-28-9 (6층 인터넷장비)
A7-30-1 | O | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | OFF | A7-29-9
A7-30-2 | O | OFF |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | OFF | A7-30-9
A7-30-3 | O | OFF |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-9
A7-30-4 | O | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | A7-27-6
A7-30-5 | O | OFF |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | A7-26-6
A7-30-6 | O | OFF |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | ON | A4-19-1 (O-11)
A7-30-7 | O | OFF | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | OFF | A4-27-9 (G-19)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-14 |  | PDU : SEL1 - 6-1 - B7 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B7-18-6 | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | DE운용실 감시모니터 B7-30-8
B7-18-7 | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | DE운용실 사무#2 B7-31-1
B7-18-8 | O | ON | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-2
B7-18-9 | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | OFF | B7-31-3
B7-28-1 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-4
B7-28-2 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-5
B7-28-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | OFF | B7-31-6
B7-28-4 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-7
B7-28-5 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-8
B7-28-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | ON | B7-32-1 (사무실)
B7-28-7 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | OFF | B7-32-2 (사무실)
B7-28-8 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | OFF | B7-32-3 (사무실)
B7-29-1 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | OFF | B7-32-4 (사무실)
B7-29-2 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | B7-21-4(3) (M-14)
B7-29-3 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | B7-21-3(3) (M-13)
B7-29-4 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | B7-21-4(2) (M-13)
B7-29-5 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | B7-21-3(2) (M-14)
B7-29-6 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | OFF | B7-26-8(2)
B7-29-7 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | OFF | B7-26-9(2)
B7-29-8 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | OFF | B7-28-9
B7-30-1 | O | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | OFF | B7-29-9
B7-30-2 | O | OFF |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | OFF | B7-30-9
B7-30-3 | O | OFF |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-9
B7-30-4 | O | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | B7-26-6
B7-30-5 | O | OFF |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | B7-27-6
B7-30-6 | O | OFF |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | ON | B4-19-1 (O-11)
B7-30-7 | O | OFF | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | OFF | A4-27-8
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-09 |  | PDU : SEL1 - 6-1 - A5 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A3-21-1 (M-11) | O | ON | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | ON | A3-22-1 (L-11)
A3-21-2 (M-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | ON | A3-22-2 (L-12)
A3-21-3 (M-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | ON | A3-22-3 (L-13)
A3-21-4 (M-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | ON | A3-22-4 (L-14)
A3-21-5 (M-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | A3-22-5 (L-15)
A3-21-6 (M-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | A3-22-6 (L-16)
A3-21-7 (M-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | A3-22-7 (L-17)
A3-21-8 (M-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A3-22-8 (L-18)
A3-21-9 (M-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A3-22-9 (L-19)
#A3-19-4 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | A3-23-1 (K-11)
#A3-19-7 | O | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | A3-23-2 (K-12)
#A3-36-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A3-23-3 (K-13)
#A3-36-6 | O | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | A3-23-4 (K-14)
#A3-23-4 (K-14) | O | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | A3-23-5 (K-15)
#A3-23-7 (K-17) | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | A3-23-6 (K-16)
B4-19-7 (O-17) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | A3-23-7 / 6F-K-17
#A3-24-7 | O | OFF |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | A3-23-8 / 6F-K-18)
A3-24-8 (J-18) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | ON | A3-23-9 / 6F-K-19
A3-24-9 (J-19) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-1 (J-11)
#A3-25-4 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | A3-24-2 (J-12)
#A3-26-4 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | A3-24-3 (J-13)
#A3-27-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-4 (J-14)
A3-27-1 (G-11) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | A3-24-5 (J-15)
A3-27-2 (G-12) | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | OFF | A3-24-6 (J-16)
A3-27-3 (G-13) | O | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-7 (J-17)
[10 empty] | 총합: | 0 | 0 | 0 | 0
6-DaHall 1-PDU-10 |  | PDU : SEL1 - 6-1 - B5 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B3-21-1 (M-11) | O | ON | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | ON | B3-22-1 (L-11)
B3-21-2 (M-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | ON | B3-22-2 (L-12)
B3-21-3 (M-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | ON | B3-22-3 (L-13)
B3-21-4 (M-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | ON | B3-22-4 (L-14)
B3-21-5 (M-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | B3-22-5 (L-15)
B3-21-6 (M-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | B3-22-6 (L-16)
B3-21-7 (M-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | B3-22-7 (L-17)
B3-21-8 (M-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B3-22-8 (L-18)
B3-21-9 (M-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B3-22-9 (L-19)
#B3-20-4 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | B3-23-1 (K-11)
#B3-20-7 (N-17) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | B3-23-2 (K-12)
#B3-21-4 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B3-24-6 (J-16)
#B3-21-7 | O | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | B3-23-4 (K-14)
#B3-22-4 | O | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | B3-23-5 (K-15)
#B3-22-7 | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | B3-23-6 (K-16)
#B3-25-7 | O | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | B3-23-7 / 6F-K-17
#B3-26-7 | O | OFF |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B3-23-8 / 6F-K-18
B3-24-8 (J-18) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | ON | B3-23-9 / 6F-K-19
B3-24-9 (J-19) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-1 (J-11)
#B3-27-7 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | B3-24-2 (J-12)
B3-27-1 (G-11) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | B3-24-3 (J-13)
B3-27-2 (G-12) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-4 (J-14)
B3-27-3 (G-13) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | B3-24-5 (J-15)
spare | X | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B3-23-3 (K-13)
spare | X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-7 (J-17)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-11 |  | PDU : SEL1 - 6-1 - A6 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 5.1 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | OFF | A4-20-1 (N-11)
A4-19-2 (O-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | OFF | A4-20-2 (N-12)
A4-19-3 (O-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | OFF | A4-20-3 (N-13)
A4-19-4 (O-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | OFF | A4-20-4 (N-14)
A4-19-5 (O-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 6.01 |  |  | O | ON | A4-20-5 (N-15)
A4-19-6 (O-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | A4-20-6 (N-16)
A4-19-7 (O-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | A4-20-7 (N-17)
A4-19-8 (O-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A4-20-8 (N-18)
A4-19-9 (O-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A4-20-9 (N-19)
A4-36-1 (AG-19) | O | ON | 6.52 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | A4-25-9 (I-19)
A4-36-2 (S-10) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-1 (H-11)
A4-36-3 (S-11) | O | ON |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-2 (H-12)
A4-36-4 (S-12) | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | OFF | A4-26-3 (H-13)
A4-36-5 (S-13) | O | ON |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-4 (H-14)
A4-36-6 (S-14) | O | ON |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-5 (H-15)
A4-36-7 (S-15) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | X | OFF
A4-36-8 (S-16) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-7 (H-17)
A4-25-1 (I-11) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-8 (H-18)
A4-25-2 (I-12) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | A4-26-9 (H-19)
A4-25-3 (I-13) | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | A4-27-4 (G-14)
A4-25-4 (I-14) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | A4-27-5 (G-15)
A4-25-5 (I-15) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | A4-36-9 (AG-20)
A4-25-6 (I-16) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | A4-27-7 (G-17)
Rack S-15 | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | X | OFF
Rack S-13 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 6.52 | 6.01 | 0
6-DaHall 1-PDU-12 |  | PDU : SEL1 - 6-1 - B6 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 5.1 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-1 (N-11)
B4-19-2 (O-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B4-20-2 (N-12)
B4-19-3 (O-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | OFF | B4-20-3 (N-13)
B4-19-4 (O-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-4 (N-14)
B4-19-5 (O-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 6.02 |  |  | O | ON | B4-20-5 (N-15)
B4-19-6 (O-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | B4-20-6 (N-16)
#A3-24-4 | O | OFF | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-7 (N-17)
B4-19-8 (O-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B4-20-8 (N-18)
B4-19-9 (O-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B4-20-9 (N-19)
B4-36-1 (AG-19) | O | ON | 6.54 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | B4-25-9 (I-19)
B4-36-2 (S-10) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-1 (H-11)
B4-36-3 (S-11) | O | ON |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-2 (H-12)
B4-36-4 (S-12) | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B4-26-3 (H-13)
B4-36-5 (S-13) | O | ON |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-4 (H-14)
B4-36-6 (S-14) | O | ON |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-5 (H-15)
B4-36-7 (S-15) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | X | OFF
B4-36-8 (S-16) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-7 (H-17)
B4-25-1 (I-11) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-8 (H-18)
B4-25-2 (I-12) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | B4-26-9 (H-19)
B4-25-3 (I-13) | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | B4-27-4 (G-14)
B4-25-4 (I-14) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | B4-27-5 (G-15)
B4-25-5 (I-15) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B4-36-9 (AG-20)
B4-25-6 (I-16) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | B4-27-7 (G-17)
Rack S-15 | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | OFF | B4-27-8 (G-18)
Rack S-13 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | B4-27-9 (G-19)
[10 empty] | 총합: | 6.54 | 6.02 | 0
6-DaHall 1-PDU-01 |  | PDU : SEL1 - 6-1 - A1 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 21.6 | 21.2 | 16.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A1-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 2 |  |  |  | O | ON | G1101(A)
A1-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 9.68 |  |  | O | ON | G1103(A)
A1-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 3.19 |  | O | ON | A1-35-3(AG-13)
A1-1-4 (AF-16) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 4.89 |  |  |  | O | ON | A1-35-4(AG-14)
A1-1-5 (AF-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 9.21 |  |  | O | ON | A1-35-5(AG-15)
A1-1-6 (AF-14) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 8.41 |  | O | ON | A1-35-6(AG-16)
A1-1-7 (AF-13) | O | ON | 2.06 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 7.06 |  |  |  | O | ON | A1-35-7(AG-17)
A1-1-8 (AF-12) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 5.17 |  |  | O | ON | A1-35-8 (AG-18)
A1-1-9 (AF-11) | O | ON |  |  | 2.05 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0.69 |  | O | ON | A1-16-4 (R-14)
#A1-1-3 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0.34 |  |  |  | O | ON | A1-16-5 (R-15)
#A1-1-7 | O | OFF |  | 0.99 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 5.78 |  |  | O | ON | A1-16-6 (R-16)
#A1-35-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A1-16-7 (R-17)
6-1-A1-30-25 | O | ON | 2.06 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 2 |  |  |  | O | ON | A1-16-8 (R-18)
A1-13-1 (AA-11) | O | ON |  | 5.28 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 3.08 |  |  | O | ON | A1-16-9 (R-19)
A1-13-2 (AA-12) | O | OFF |  |  | 4.91 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 9.12 |  | O | OFF | #A1-13-4
A1-13-3 (AA-13) | O | ON | 8.36 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 7.02 |  |  |  | O | OFF | #A1-16-4
A1-13-4 (AA-14) | O | ON |  | 5.14 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | X | OFF | A1-4-1
A1-13-5 (AA-15) | O | ON |  |  | 0.69 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 1.11 |  | O | ON | G1102(A)
A1-13-6 (AA-16) | O | ON | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | X | OFF | G1102 하부(미사용)
A1-13-7 (AA-17) | O | ON |  | 0.35 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | A1-35-3(2)(위치 불명)
B209 / (AA-18) | O | ON |  |  | 0.99 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 4.48 |  | O | ON | B411
A1-13-9 (B410) | O | ON | 5.6 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B211 | A1-30-44 를 B211에 포설 예정('23.05월초)
A1-16-1 (R-11) | O | ON |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 4.38 |  |  | O | ON | 신규 BMS(6F TPS실) Rack
A1-16-2 (R-12) | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0.57 |  | O | ON | A1-4-8 (AC-12)
B210 / (AA-19) | O | OFF | 9.67 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | ON | FMS 6층 전원
[10 empty] | 총합: | 51.06 | 49.06 | 36.21
6-DaHall 1-PDU-02 |  | PDU : SEL1 - 6-1 - B1 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 19.2 | 18.8 | 21.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B1-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 1.5 |  |  |  | O | ON | G1101 (B)
B1-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 7.46 |  |  | O | ON | G1103 (B)
B1-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 5.44 |  | O | ON | B1-35-3(AG-13)
B1-1-4 (AF-16) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 3.32 |  |  |  | O | ON | B1-35-4(AG-14)
B1-1-5 (AF-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 8.78 |  |  | O | ON | B1-35-5(AG-15)
B1-1-6 (AF-14) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 10.66 |  | O | ON | B1-35-6(AG-16)
B1-1-7 (AF-13) | O | ON | 2.41 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 8.72 |  |  |  | O | ON | B1-35-7(AG-17)
B1-1-8 (AF-12) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 5.16 |  |  | O | ON | B1-35-8 (AG-18)
B1-1-9 (AF-11) | O | ON |  |  | 2.22 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0.64 |  | X | OFF | 6-1-B1-30-18
#B1-2-3 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0.3 |  |  |  | O | ON | B1-16-5 (R-15)
#B1-2-7 | O | OFF |  | 0.79 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 4.53 |  |  | O | ON | B1-16-6 (R-16)
#B1-3-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | B1-16-7 (R-17)
6-1-B1-30-25 | O | ON | 2.39 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 1.5 |  |  |  | O | ON | B1-16-8 (R-18)
B1-13-1 (AA-11) | O | ON |  | 4.46 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 5.46 |  |  | O | ON | B1-16-9 (R-19)
B1-13-2 (AA-12) | O | OFF |  |  | 3.32 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 9.38 |  | O | OFF | B210 / (AA-19) | B1-30-30 사용예정
B1-13-3 (AA-13) | O | ON | 10.37 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 8.96 |  |  |  | O | OFF | #B1-16-7
B1-13-4 (AA-14) | O | ON |  | 5.08 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B1-16-4 (R-14)
B1-13-5 (AA-15) | O | ON |  |  | 0.64 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 2.4 |  | O | ON | G1102 (B)
B1-13-6 (AA-16) | O | ON | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | G1102 하부(도어락&CCTV)
B1-13-7 (AA-17) | O | ON |  | 0.33 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | B1-35-3(2)(위치 불명)
B209 / (AA-18) | O | ON |  |  | 1.62 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 4.58 |  | O | ON | B411
B1-13-9 (B410) | O | ON | 5.99 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B211 | B1-30-44 를 B211에 포설 예정('23.05월초)
B1-16-1 (R-11) | O | ON |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 4.5 |  |  | X | OFF | B1-4-7
B1-16-2 (R-12) | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B1-4-8 (AC-12)
| X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 45.46 | 46.55 | 40.9
6-DaHall 1-PDU-03 |  | PDU : SEL1 - 6-1 - A2 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 20.7 | 21.3 | 10.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A2-2-1 | O | ON | 6.75 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 6.15 |  |  |  | X | OFF | A2-3-1
A2-2-2 | O | ON |  | 6.17 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 4.1 |  |  | X | OFF | A2-3-2
A2-2-3 | O | ON |  |  | 5.77 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 3.52 |  | X | OFF | A2-3-3
A2-2-4 | O | ON | 6.77 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 4.27 |  |  |  | X | OFF | A2-3-4
A2-2-5 | O | ON |  | 5.87 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | X | OFF | A2-3-5
A2-2-6 | O | ON |  |  | 4.91 | `` | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | X | OFF | A2-3-6
A2-2-7 | O | ON | 8.12 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | X | OFF | A2-3-7
A2-2-8 | O | ON |  | 4.25 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A2-3-8 (AD-12)
A2-2-9 | O | ON |  |  | 2.14 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A2-3-9 (AD-11)
A2-5-1 | X | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | A2-6-8
A2-5-2 | X | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | A2-7-1 (V-17)
A2-5-3 | X | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A2-7-2 (V-17)
A2-5-4 | X | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | A2-7-3 (V-16)
A2-5-5 | X | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | A2-7-4 (V-15)
A2-5-6 | X | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | A2-7-5 (V-14)
A2-5-7 | X | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | A2-7-6 (V-13)
A2-5-8 (AB-12) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | A2-7-7 (V-12)
A2-5-9 (AB-11) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | A2-7-8 (V-11)
A2-6-1 | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | A2-8-1 (V-16)
A2-6-2 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | A2-8-2 (W-17)
A2-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | ON | A2-8-3 (W-16)
A2-6-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | ON | A2-8-4 (W-15)
A2-6-5 | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | ON | A2-8-5 (W-14)
A2-6-6 | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | A2-8-6 (W-13)
손혈관인식시스템 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 32.06 | 20.39 | 16.34
6-DaHall 1-PDU-04 |  | PDU : SEL1 - 6-1 - B2 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 18.6 | 29.1 | 14.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B2-2-1 | O | ON | 5.46 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 6.69 |  |  |  | X | OFF | B2-3-1
B2-2-2 | O | ON |  | 6.39 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 4.28 |  |  | X | OFF | B2-3-2
B2-2-3 | O | ON |  |  | 6.22 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 5.68 |  | X | OFF | B2-3-3
B2-2-4 | O | ON | 4.48 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 3.98 |  |  |  | X | OFF | B2-3-4
B2-2-5 | O | ON |  | 6.19 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | X | OFF | B2-3-5
B2-2-6 | O | ON |  |  | 6.43 | `` | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | X | OFF | B2-3-6
B2-2-7 | O | ON | 5.76 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | X | OFF | B2-3-7
B2-2-8 | O | ON |  | 4.01 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B2-3-8 (AD-12)
B2-2-9 | O | ON |  |  | 1.94 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B2-3-9 (AD-11)
B2-5-1 | X | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | B2-6-8
B2-5-2 | X | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | B2-7-1 (V-17)
B2-5-3 | X | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | B2-7-2 (V-17)
B2-5-4 | X | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | B2-7-3 (V-16)
B2-5-5 | X | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | B2-7-4 (V-15)
B2-5-6 | X | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | B2-7-5 (V-14)
B2-5-7 | X | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | B2-7-6 (V-13)
B2-5-8 (AB-12) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B2-7-7 (V-12)
B2-5-9 (AB-11) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | B2-7-8 (V-11)
B2-6-1 | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | B2-8-1 (V-16)
B2-6-2 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | B2-8-2 (W-17)
B2-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | ON | B2-8-3 (W-16)
B2-6-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | ON | B2-8-4 (W-15)
B2-6-5 | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | ON | B2-8-5 (W-14)
B2-6-6 | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B2-8-6 (W-13)
| X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 26.37 | 20.87 | 20.27
6-DaHall 1-PDU-05 |  | PDU : SEL1 - 6-1 - A3 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 19.5 | 43.6 | 27 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A5-8-7 (W-12) | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 13 |  |  | O | ON | A5-15-1 (T-11)
A5-8-8 (W-11) | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 5.74 |  | O | ON | A5-15-2 (T-12)
A5-9-1 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 1.76 |  |  |  | O | ON | A5-15-3 (T-13)
A5-9-2 (X-17) | O | ON |  | 2.15 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 3.94 |  |  | O | ON | A5-15-4 (T-14)
A5-9-3 (X-16) | O | ON |  |  | 1.04 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0.86 |  | O | ON | A5-15-5 (T-15)
A5-9-4 (X-15) | O | ON | 1.78 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 1.5 |  |  |  | O | ON | A5-15-6 (T-16)
A5-9-5 (X-14) | O | ON |  | 7.43 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 5.6 |  |  | O | ON | A5-15-7 (T-17)
A5-9-6 (X-13) | O | ON |  |  | 3.95 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 3.82 |  | O | ON | A5-15-8 (T-18)
A5-9-7 (X-12) | O | ON | 1.13 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0.68 |  |  |  | O | OFF | A5-15-9
A5-9-8 (X-11) | O | ON |  | 8.47 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 2.21 |  |  | O | ON | A5-17-1 (Q-11)
A5-10-1 | O | OFF |  |  | 2.08 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 6.08 |  | O | ON | A5-17-2 (Q-12)
A807(A5-10-2) | O | ON | 5.29 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 7.33 |  |  |  | O | ON | A5-17-3 (Q-13)
A5-10-3 (A806 - 1) | O | ON |  | 9.25 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 4.97 |  |  | O | ON | A5-17-4 (Q-14)
A5-10-4 (A806 - 2) | O | ON |  |  | 6.68 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 13.31 |  | O | ON | A5-17-5 (Q-15)
A5-10-5 (Y-14) | O | ON | 5.59 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0.72 |  |  |  | O | ON | A5-17-6 (Q-16)
A5-10-6 (Y-13) | O | ON |  | 3.68 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0.86 |  |  | O | ON | A5-17-7 (Q-17)
A5-10-7 (Y-12) | O | ON |  |  | 1.49 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 5.38 |  | O | ON | A5-17-8 (Q-18)
A5-10-8 (Y-11) | O | ON | 3.72 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | A5-17-9 (Q-19)
A5-14-1 (U-10) | O | ON |  | 7.58 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | A5-18-1 (P-11)
A5-14-2 (U-11) | O | ON |  |  | 2.27 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A5-18-2 (P-12)
A5-14-3 (U-12) | O | ON | 2.17 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | A5-18-3 (P-13)
A5-14-4 (U-13) | O | ON |  | 6.41 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | A5-18-4 (P-14)
A5-14-5 (U-14) | O | ON |  |  | 5.46 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | A5-18-5 (P-15)
6-1-A3-47 | O | ON | 5.85 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | ON | A5-16-3 (R-13)
A5-14-7 (U-16) | O | ON |  | 9.31 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | ON | A5-4-9 (AC-11)
6-1-A3-51 | O | ON |  |  | 5 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | A5-6-7
6-1-A3-53 | O | ON | 7.24 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 4.51 |  |  |  | O | ON | A5-15-5(2) (T-15)
[10 empty] | 총합: | 49.27 | 84.86 | 63.16
6-DaHall 1-PDU-06 |  | PDU : SEL1 - 6-1 - B3 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 12.5 | 37.1 | 24.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B5-8-7 (W-12) | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 11.95 |  |  | O | ON | B5-15-1 (T-11)
B5-8-8 (W-11) | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 4.53 |  | O | ON | B5-15-2 (T-12)
B5-9-1 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 1.91 |  |  |  | O | ON | B5-15-3 (T-13)
B5-9-2 | O | ON |  | 3.66 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 4.5 |  |  | O | ON | B5-15-4 (T-14)
B5-9-3 | O | ON |  |  | 1.02 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0.55 |  | O | ON | B5-15-5 (T-15)
B5-9-4 (X-15) | O | ON | 2.01 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | B5-15-6 (T-16)
B5-9-5 (X-14) | O | ON |  | 6.67 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 4.28 |  |  | O | ON | B5-15-7 (T-17)
B5-9-6 (X-13) | O | ON |  |  | 3.49 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 4.77 |  | O | ON | B5-15-8 (T-18)
B5-9-7 (X-12) | O | ON | 1.19 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0.39 |  |  |  | O | OFF | B5-15-9
B5-9-8 (X-11) | O | ON |  | 8.69 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 1.93 |  |  | O | ON | B5-17-1 (Q-11)
B5-10-1 | O | OFF |  |  | 0.45 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 5.29 |  | O | ON | B5-17-2 (Q-12)
A807(B5-10-2) | O | ON | 5.39 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 5.46 |  |  |  | O | ON | B5-17-3 (Q-13)
B5-10-3 (A806 - 1) | O | ON |  | 6.73 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 6.29 |  |  | O | ON | B5-17-4 (Q-14)
B5-10-4 (A806 - 2) | O | ON |  |  | 5.13 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 12.07 |  | O | ON | B5-17-5 (Q-15)
B5-10-5 (Y-14) | O | ON | 4.54 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0.72 |  |  |  | O | ON | B5-17-6 (Q-16)
B5-10-6 (Y-13) | O | ON |  | 4.47 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0.55 |  |  | O | ON | B5-17-7 (Q-17)
B5-10-7 (Y-12) | O | ON |  |  | 1.19 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 3.45 |  | O | ON | B5-17-8 (Q-18)
B5-10-8 (Y-11) | O | ON | 4.7 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | B5-17-9 (Q-19)
A5-14-1 (U-10) | O | ON |  | 7.8 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | B5-18-1 (P-11)
A5-14-2 (U-11) | O | ON |  |  | 1.93 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | B5-18-2 (P-12)
A5-14-3 (U-12) | O | ON | 1.07 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | B5-18-3 (P-13)
A5-14-4 (U-13) | O | ON |  | 5.67 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | B5-18-4 (P-14)
A5-14-5 (U-14) | O | ON |  |  | 5.53 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | B5-18-5 (P-15)
6-1-B3-47 | O | ON | 5.44 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | ON | B5-16-3 (R-13)
A5-14-7 (U-16) | O | ON |  | 1.49 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | ON | B5-4-9 (AC-11)
6-1-B3-51 | O | ON |  |  | 5.77 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | B5-6-7
6-1-B3-53 | O | ON | 1 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 2.9 |  |  |  | O | ON | B5-15-5(2) (T-15)
[10 empty] | 총합: | 36.72 | 74.68 | 55.17
6-DaHall 1-PDU-07 |  | PDU : SEL1 - 6-1 - A4 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
#A6-4-4 | O | OFF |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | A6-4-1
#A6-4-7 | O | OFF |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | A6-4-2
#A6-5-4 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | A6-4-3
#A6-5-7 | O | OFF |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | ON | A6-4-4 (AC-16)
#A6-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | ON | A6-4-5 (AC-15)
#A6-6-6 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | A6-4-6 (AC-14)
#A6-7-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | ON | A6-4-7 (AC-13)
#A6-7-6 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | A6-5-1
#A6-8-3 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | A6-5-2
#A6-8-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | A6-5-3
#A6-9-3 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | A6-5-4 (AB-16)
#A6-9-6 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | A6-5-5 (AB-15)
#A6-10-3 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | A6-5-6 (AB-14)
#A6-10-6 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | A6-5-7 (AB-13)
#A6-14-4 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | OFF | A6-2-1
#A6-14-7 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | OFF | A6-2-2
#A6-15-4 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | OFF | A6-2-3
#A6-15-7 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | A6-2-4 (AE-16)
#A6-17-4 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | A6-2-5 (AE-15)
#A6-17-7 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A6-2-6 (AE-14)
A6-8-8(1) | O | ON | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | A6-2-7 (AE-13)
A6-8-7(1) | O | ON |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | A6-2-8 (AE-12)
A6-8-6(1) | O | ON |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | A6-2-9 (AE-11)
불량 | X | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | A6-3-1
A6-3-7 (AD-13) | O | ON |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | A6-3-2
A6-3-6 (AD-14) | O | ON |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | A6-3-3
A6-3-5 (AD-15) | O | ON | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | ON | A6-3-4 (AD-16)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-08 |  | PDU : SEL1 - 6-1 - B4 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
#B6-28-3 | X | OFF |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | B6-4-1
#B6-28-6 | X | OFF |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | B6-4-2
#B6-29-3 | X | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | B6-4-3
#B6-29-6 | X | OFF |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | ON | B6-4-4 (AC-16)
#B6-30-3 | X | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | ON | B6-4-5 (AC-15)
#B6-30-6 | X | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | B6-4-6 (AC-14)
#B6-31-3 | X | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | ON | B6-4-7 (AC-13)
#B6-31-6 | X | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | B6-5-1
#B6-32-3 | X | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | B6-5-2
#B6-32-6 | X | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | B6-5-3
#B6-33-3 | X | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | B6-5-4 (AB-16)
#B6-33-6 | X | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | B6-5-5 (AB-15)
| X | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | B6-5-6 (AB-14)
| X | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | B6-5-7 (AB-13)
| X | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | OFF | B6-2-1
| X | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | OFF | B6-2-2
| X | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | OFF | B6-2-3
| X | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | B6-2-4 (AE-16)
| X | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | B6-2-5 (AE-15)
| X | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | B6-2-6 (AE-14)
| X | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | B6-2-7 (AE-13)
B6-8-8(1) | O | ON |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | B6-2-8 (AE-12)
B6-8-7(1) | O | ON |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | B6-2-9 (AE-11)
B6-8-6(1) | O | ON | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | B6-3-1
B6-3-7 (AD-13) | O | ON |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | B6-3-2
B6-3-6 (AD-14) | O | ON |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | B6-3-3
B6-3-5 (AD-15) | O | ON | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | ON | B6-3-4 (AD-16)
[10 empty] | 총합: | 0 | 0 | 0
| IDC | 794.49

## 6층_부하량(월간_AVG)
Date : 2023-11-01 ~ 2023-11-30
6-DaHall 1-CEP-05 | [7 empty] | Main CB 4P 350A
[10 empty] | MAIN 계측값 : | 2.3 | 2.1 | 2.9 | <- 실측값 |  |  | 5-DaHall 1-EH-01
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
5-DaHall 1-CEP-06 | O | ON | 0.17477 | 0.78112 | 0.69841 |  | 4P 150A | #01
| X | OFF | 사 | 용 | 금 | 지 | 4P 50A | #02 | #03 | 4P 50A | 0 | 0 | 0 |  | X | OFF
5-DaHall 1-CRAC-14 (CF CRAC #02) | O | ON | 0 | 0 | 0 |  | 4P 50A | #04 | #05 | 4P 50A | 0 | 0 | 0 |  | X | OFF
| X | OFF | 0 | 0 | 0 |  | 4P 50A | #06 | #07 | 4P 50A | 0 | 0 | 0 |  | O | OFF | 급배기휀
| X | OFF | 0 | 0 | 0 |  | 4P 50A | #08 | #09 | 4P 50A | 0 | 0 | 0 |  | X | OFF
spare | X | OFF | 0 | 0 | 0 |  | 4P 50A | #10 | #11 | 4P 100A | 6.2945 | 6.4056 | 8.1714 |  | O | ON | 8층 냉방분전반
| O | OFF | 0 |  |  |  | 2P 30A | #12 | #13 | 2P 30A | 0 |  |  |  | O | OFF
| O | OFF |  | 8.5118 |  |  | 2P 30A | #14 | #15 | 2P 50A |  | 10.3192 |  |  | O | ON | 7-DaHall 1-EH (7층 가습기 Main)
| O | OFF |  |  | 7.4438 |  | 2P 30A | #16 | #17 | 2P 50A |  |  | 6.3162 |  | O | ON | 6-DaHall 1-EH (6층 가습기 Main)
|  | 6층 사무실 | 32.591 | [6 empty] | 총합: | 6.4693 | 26.0177 | 22.6298 | 0
[11 empty] | 55.1169 | 32.591 | 59.13%
6-DaHall 1-PDU-13 |  | PDU : SEL1 - 6-1 - A7 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A7-18-6 | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | DE운용실 사무#1 A7-30-8
A7-18-7 | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | DE 출입통제Desk A7-31-1
A7-18-8 | O | ON | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | 6F DE 가청경보 PNL
A7-18-9 | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | OFF | A7-31-3
A7-28-1 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-4
A7-28-2 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | OFF | A7-31-5
A7-28-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | OFF | A7-31-6
A7-28-4 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-7
A7-28-5 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | A7-31-8
A7-28-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | #A7-28-3
A7-28-7 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | OFF | #A7-28-6
A7-28-8 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | OFF | #A7-29-3
A7-29-1 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | OFF | #A7-29-6
A7-29-2 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | A7-21-4(3) (M-14)
A7-29-3 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | A7-21-3(3) (M-13)
A7-29-4 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | A7-21-3(2) (M-13)
A7-29-5 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | A7-21-4(2) (M-14)
A7-29-6 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | OFF | A7-26-8(2)
A7-29-7 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | OFF | A7-26-9(2)
A7-29-8 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A7-28-9 (6층 인터넷장비)
A7-30-1 | O | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | OFF | A7-29-9
A7-30-2 | O | OFF |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | OFF | A7-30-9
A7-30-3 | O | OFF |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | OFF | A7-31-9
A7-30-4 | O | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | A7-27-6
A7-30-5 | O | OFF |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | A7-26-6
A7-30-6 | O | OFF |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | ON | A4-19-1 (O-11)
A7-30-7 | O | OFF | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | OFF | A4-27-9 (G-19)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-14 |  | PDU : SEL1 - 6-1 - B7 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B7-18-6 | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | DE운용실 감시모니터 B7-30-8
B7-18-7 | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | DE운용실 사무#2 B7-31-1
B7-18-8 | O | ON | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-2
B7-18-9 | O | ON |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | OFF | B7-31-3
B7-28-1 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-4
B7-28-2 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-5
B7-28-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | OFF | B7-31-6
B7-28-4 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-7
B7-28-5 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | B7-31-8
B7-28-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | ON | B7-32-1 (사무실)
B7-28-7 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | OFF | B7-32-2 (사무실)
B7-28-8 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | OFF | B7-32-3 (사무실)
B7-29-1 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | OFF | B7-32-4 (사무실)
B7-29-2 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | B7-21-4(3) (M-14)
B7-29-3 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | ON | B7-21-3(3) (M-13)
B7-29-4 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | ON | B7-21-4(2) (M-13)
B7-29-5 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | ON | B7-21-3(2) (M-14)
B7-29-6 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | OFF | B7-26-8(2)
B7-29-7 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | OFF | B7-26-9(2)
B7-29-8 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | OFF | B7-28-9
B7-30-1 | O | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | OFF | B7-29-9
B7-30-2 | O | OFF |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | OFF | B7-30-9
B7-30-3 | O | OFF |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | OFF | B7-31-9
B7-30-4 | O | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | B7-26-6
B7-30-5 | O | OFF |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | B7-27-6
B7-30-6 | O | OFF |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | ON | B4-19-1 (O-11)
B7-30-7 | O | OFF | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | OFF | A4-27-8
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-09 |  | PDU : SEL1 - 6-1 - A5 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A3-21-1 (M-11) | O | ON | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | ON | A3-22-1 (L-11)
A3-21-2 (M-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | ON | A3-22-2 (L-12)
A3-21-3 (M-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | ON | A3-22-3 (L-13)
A3-21-4 (M-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | ON | A3-22-4 (L-14)
A3-21-5 (M-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | A3-22-5 (L-15)
A3-21-6 (M-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | A3-22-6 (L-16)
A3-21-7 (M-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | A3-22-7 (L-17)
A3-21-8 (M-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A3-22-8 (L-18)
A3-21-9 (M-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A3-22-9 (L-19)
#A3-19-4 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | A3-23-1 (K-11)
#A3-19-7 | O | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | A3-23-2 (K-12)
#A3-36-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A3-23-3 (K-13)
#A3-36-6 | O | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | A3-23-4 (K-14)
#A3-23-4 (K-14) | O | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | A3-23-5 (K-15)
#A3-23-7 (K-17) | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | A3-23-6 (K-16)
B4-19-7 (O-17) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | A3-23-7 / 6F-K-17
#A3-24-7 | O | OFF |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | A3-23-8 / 6F-K-18)
A3-24-8 (J-18) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | ON | A3-23-9 / 6F-K-19
A3-24-9 (J-19) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-1 (J-11)
#A3-25-4 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | A3-24-2 (J-12)
#A3-26-4 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | A3-24-3 (J-13)
#A3-27-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-4 (J-14)
A3-27-1 (G-11) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | A3-24-5 (J-15)
A3-27-2 (G-12) | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | OFF | A3-24-6 (J-16)
A3-27-3 (G-13) | O | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | A3-24-7 (J-17)
[10 empty] | 총합: | 0 | 0 | 0 | 0
6-DaHall 1-PDU-10 |  | PDU : SEL1 - 6-1 - B5 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B3-21-1 (M-11) | O | ON | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | ON | B3-22-1 (L-11)
B3-21-2 (M-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | ON | B3-22-2 (L-12)
B3-21-3 (M-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | ON | B3-22-3 (L-13)
B3-21-4 (M-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | ON | B3-22-4 (L-14)
B3-21-5 (M-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | O | ON | B3-22-5 (L-15)
B3-21-6 (M-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | B3-22-6 (L-16)
B3-21-7 (M-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | B3-22-7 (L-17)
B3-21-8 (M-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B3-22-8 (L-18)
B3-21-9 (M-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B3-22-9 (L-19)
#B3-20-4 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | ON | B3-23-1 (K-11)
#B3-20-7 (N-17) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | B3-23-2 (K-12)
#B3-21-4 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B3-24-6 (J-16)
#B3-21-7 | O | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | B3-23-4 (K-14)
#B3-22-4 | O | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | B3-23-5 (K-15)
#B3-22-7 | O | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | B3-23-6 (K-16)
#B3-25-7 | O | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | B3-23-7 / 6F-K-17
#B3-26-7 | O | OFF |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B3-23-8 / 6F-K-18
B3-24-8 (J-18) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | ON | B3-23-9 / 6F-K-19
B3-24-9 (J-19) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-1 (J-11)
#B3-27-7 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | B3-24-2 (J-12)
B3-27-1 (G-11) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | B3-24-3 (J-13)
B3-27-2 (G-12) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-4 (J-14)
B3-27-3 (G-13) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | B3-24-5 (J-15)
spare | X | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B3-23-3 (K-13)
spare | X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | B3-24-7 (J-17)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-11 |  | PDU : SEL1 - 6-1 - A6 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 5.1 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | OFF | A4-20-1 (N-11)
A4-19-2 (O-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | OFF | A4-20-2 (N-12)
A4-19-3 (O-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | OFF | A4-20-3 (N-13)
A4-19-4 (O-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | OFF | A4-20-4 (N-14)
A4-19-5 (O-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 4.9703 |  |  | O | ON | A4-20-5 (N-15)
A4-19-6 (O-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | A4-20-6 (N-16)
A4-19-7 (O-17) | O | ON | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | ON | A4-20-7 (N-17)
A4-19-8 (O-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A4-20-8 (N-18)
A4-19-9 (O-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A4-20-9 (N-19)
A4-36-1 (AG-19) | O | ON | 5.1988 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | A4-25-9 (I-19)
A4-36-2 (S-10) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-1 (H-11)
A4-36-3 (S-11) | O | ON |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-2 (H-12)
A4-36-4 (S-12) | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | OFF | A4-26-3 (H-13)
A4-36-5 (S-13) | O | ON |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-4 (H-14)
A4-36-6 (S-14) | O | ON |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-5 (H-15)
A4-36-7 (S-15) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | X | OFF
A4-36-8 (S-16) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | OFF | A4-26-7 (H-17)
A4-25-1 (I-11) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | A4-26-8 (H-18)
A4-25-2 (I-12) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | A4-26-9 (H-19)
A4-25-3 (I-13) | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | A4-27-4 (G-14)
A4-25-4 (I-14) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | A4-27-5 (G-15)
A4-25-5 (I-15) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | A4-36-9 (AG-20)
A4-25-6 (I-16) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | A4-27-7 (G-17)
Rack S-15 | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | X | OFF
Rack S-13 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 5.1988 | 4.9703 | 0
6-DaHall 1-PDU-12 |  | PDU : SEL1 - 6-1 - B6 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 5.1 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-1 (N-11)
B4-19-2 (O-12) | O | ON |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B4-20-2 (N-12)
B4-19-3 (O-13) | O | ON |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 0 |  | O | OFF | B4-20-3 (N-13)
B4-19-4 (O-14) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-4 (N-14)
B4-19-5 (O-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 4.9403 |  |  | O | ON | B4-20-5 (N-15)
B4-19-6 (O-16) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | O | ON | B4-20-6 (N-16)
#A3-24-4 | O | OFF | 0 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | O | OFF | B4-20-7 (N-17)
B4-19-8 (O-18) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B4-20-8 (N-18)
B4-19-9 (O-19) | O | ON |  |  | 0 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B4-20-9 (N-19)
B4-36-1 (AG-19) | O | ON | 5.1819 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | B4-25-9 (I-19)
B4-36-2 (S-10) | O | ON |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-1 (H-11)
B4-36-3 (S-11) | O | ON |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-2 (H-12)
B4-36-4 (S-12) | O | ON | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B4-26-3 (H-13)
B4-36-5 (S-13) | O | ON |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-4 (H-14)
B4-36-6 (S-14) | O | ON |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-5 (H-15)
B4-36-7 (S-15) | O | ON | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | X | OFF
B4-36-8 (S-16) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | OFF | B4-26-7 (H-17)
B4-25-1 (I-11) | O | OFF |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | B4-26-8 (H-18)
B4-25-2 (I-12) | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | OFF | B4-26-9 (H-19)
B4-25-3 (I-13) | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | OFF | B4-27-4 (G-14)
B4-25-4 (I-14) | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | OFF | B4-27-5 (G-15)
B4-25-5 (I-15) | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B4-36-9 (AG-20)
B4-25-6 (I-16) | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | OFF | B4-27-7 (G-17)
Rack S-15 | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | OFF | B4-27-8 (G-18)
Rack S-13 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | OFF | B4-27-9 (G-19)
[10 empty] | 총합: | 5.1819 | 4.9403 | 0
6-DaHall 1-PDU-01 |  | PDU : SEL1 - 6-1 - A1 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 21.6 | 21.2 | 16.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A1-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 1.9073 |  |  |  | O | ON | G1101(A)
A1-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 3.3293 |  |  | O | ON | G1103(A)
A1-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 2.9359 |  | O | ON | A1-35-3(AG-13)
A1-1-4 (AF-16) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 4.6096 |  |  |  | O | ON | A1-35-4(AG-14)
A1-1-5 (AF-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 7.6267 |  |  | O | ON | A1-35-5(AG-15)
A1-1-6 (AF-14) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 7.1786 |  | O | ON | A1-35-6(AG-16)
A1-1-7 (AF-13) | O | ON | 1.8272 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 4.742 |  |  |  | O | ON | A1-35-7(AG-17)
A1-1-8 (AF-12) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 4.3582 |  |  | O | ON | A1-35-8 (AG-18)
A1-1-9 (AF-11) | O | ON |  |  | 1.7175 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0.65398 |  | O | ON | A1-16-4 (R-14)
#A1-1-3 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0.2262 |  |  |  | O | ON | A1-16-5 (R-15)
#A1-1-7 | O | OFF |  | 0.77522 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 4.1864 |  |  | O | ON | A1-16-6 (R-16)
#A1-35-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A1-16-7 (R-17)
6-1-A1-30-25 | O | ON | 1.8536 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 1.8658 |  |  |  | O | ON | A1-16-8 (R-18)
A1-13-1 (AA-11) | O | ON |  | 2.4816 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 2.8519 |  |  | O | ON | A1-16-9 (R-19)
A1-13-2 (AA-12) | O | OFF |  |  | 4.5167 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 7.4721 |  | O | OFF | #A1-13-4
A1-13-3 (AA-13) | O | ON | 3.0449 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 5.0895 |  |  |  | O | OFF | #A1-16-4
A1-13-4 (AA-14) | O | ON |  | 2.3846 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | X | OFF | A1-4-1
A1-13-5 (AA-15) | O | ON |  |  | 0.66837 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 1.0053 |  | O | ON | G1102(A)
A1-13-6 (AA-16) | O | ON | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | X | OFF | G1102 하부(미사용)
A1-13-7 (AA-17) | O | ON |  | 0.23171 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | A1-35-3(2)(위치 불명)
B209 / (AA-18) | O | ON |  |  | 0.79308 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 3.7994 |  | O | ON | B411
A1-13-9 (B410) | O | ON | 3.2719 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B211 | A1-30-44 를 B211에 포설 예정('23.05월초)
A1-16-1 (R-11) | O | ON |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 1.1849 |  |  | O | ON | 신규 BMS(6F TPS실) Rack
A1-16-2 (R-12) | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0.53761 |  | O | ON | A1-4-8 (AC-12)
B210 / (AA-19) | O | OFF | 7.7034 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | O | ON | FMS 6층 전원
[10 empty] | 총합: | 36.1413 | 29.4106 | 31.2784
6-DaHall 1-PDU-02 |  | PDU : SEL1 - 6-1 - B1 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 19.2 | 18.8 | 21.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B1-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 1.4397 |  |  |  | O | ON | G1101 (B)
B1-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 2.2968 |  |  | O | ON | G1103 (B)
B1-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 5.0405 |  | O | ON | B1-35-3(AG-13)
B1-1-4 (AF-16) | O | ON | 0 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 3.1141 |  |  |  | O | ON | B1-35-4(AG-14)
B1-1-5 (AF-15) | O | ON |  | 0 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 7.3766 |  |  | O | ON | B1-35-5(AG-15)
B1-1-6 (AF-14) | O | ON |  |  | 0 |  | 2P 30A | #11 | #12 | 2P 30A |  |  | 9.177 |  | O | ON | B1-35-6(AG-16)
B1-1-7 (AF-13) | O | ON | 2.1147 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 5.9326 |  |  |  | O | ON | B1-35-7(AG-17)
B1-1-8 (AF-12) | O | ON |  | 0 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 4.3999 |  |  | O | ON | B1-35-8 (AG-18)
B1-1-9 (AF-11) | O | ON |  |  | 1.8442 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0.60148 |  | X | OFF | 6-1-B1-30-18
#B1-2-3 | O | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0.20942 |  |  |  | O | ON | B1-16-5 (R-15)
#B1-2-7 | O | OFF |  | 0.59536 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 3.4016 |  |  | O | ON | B1-16-6 (R-16)
#B1-3-3 | O | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | B1-16-7 (R-17)
6-1-B1-30-25 | O | ON | 2.1427 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 1.4034 |  |  |  | O | ON | B1-16-8 (R-18)
B1-13-1 (AA-11) | O | ON |  | 1.4932 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 4.9425 |  |  | O | ON | B1-16-9 (R-19)
B1-13-2 (AA-12) | O | OFF |  |  | 3.0425 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 7.8247 |  | O | OFF | B210 / (AA-19) | B1-30-30 사용예정
B1-13-3 (AA-13) | O | ON | 3.3323 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 6.6958 |  |  |  | O | OFF | #B1-16-7
B1-13-4 (AA-14) | O | ON |  | 2.5159 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B1-16-4 (R-14)
B1-13-5 (AA-15) | O | ON |  |  | 0.62026 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 1.556 |  | O | ON | G1102 (B)
B1-13-6 (AA-16) | O | ON | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | G1102 하부(도어락&CCTV)
B1-13-7 (AA-17) | O | ON |  | 0.21443 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | B1-35-3(2)(위치 불명)
B209 / (AA-18) | O | ON |  |  | 0.61769 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 3.956 |  | O | ON | B411
B1-13-9 (B410) | O | ON | 3.5921 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | OFF | B211 | B1-30-44 를 B211에 포설 예정('23.05월초)
B1-16-1 (R-11) | O | ON |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 3.8235 |  |  | X | OFF | B1-4-7
B1-16-2 (R-12) | O | ON |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B1-4-8 (AC-12)
| X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 29.9769 | 31.0597 | 34.2804
6-DaHall 1-PDU-03 |  | PDU : SEL1 - 6-1 - A2 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 20.7 | 21.3 | 10.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A2-2-1 | O | ON | 4.5856 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 4.154 |  |  |  | X | OFF | A2-3-1
A2-2-2 | O | ON |  | 3.382 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 3.532 |  |  | X | OFF | A2-3-2
A2-2-3 | O | ON |  |  | 1.208 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 2.6374 |  | X | OFF | A2-3-3
A2-2-4 | O | ON | 4.0385 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 3.8164 |  |  |  | X | OFF | A2-3-4
A2-2-5 | O | ON |  | 3.4999 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | X | OFF | A2-3-5
A2-2-6 | O | ON |  |  | 2.8968 | `` | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | X | OFF | A2-3-6
A2-2-7 | O | ON | 5.0606 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | X | OFF | A2-3-7
A2-2-8 | O | ON |  | 3.9056 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | A2-3-8 (AD-12)
A2-2-9 | O | ON |  |  | 1.9962 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | A2-3-9 (AD-11)
A2-5-1 | X | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | A2-6-8
A2-5-2 | X | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | A2-7-1 (V-17)
A2-5-3 | X | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | A2-7-2 (V-17)
A2-5-4 | X | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | A2-7-3 (V-16)
A2-5-5 | X | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | A2-7-4 (V-15)
A2-5-6 | X | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | A2-7-5 (V-14)
A2-5-7 | X | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | A2-7-6 (V-13)
A2-5-8 (AB-12) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | A2-7-7 (V-12)
A2-5-9 (AB-11) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | A2-7-8 (V-11)
A2-6-1 | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | A2-8-1 (V-16)
A2-6-2 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | A2-8-2 (W-17)
A2-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | ON | A2-8-3 (W-16)
A2-6-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | ON | A2-8-4 (W-15)
A2-6-5 | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | ON | A2-8-5 (W-14)
A2-6-6 | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | A2-8-6 (W-13)
손혈관인식시스템 | O | ON | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 21.6552 | 14.3195 | 8.7384
6-DaHall 1-PDU-04 |  | PDU : SEL1 - 6-1 - B2 | [5 empty] | Main CB 4P 200A
[10 empty] | MAIN 계측값 : | 18.6 | 29.1 | 14.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B2-2-1 | O | ON | 3.411 |  |  |  | 2P 30A | #01 | #02 | 2P 30A | 4.5517 |  |  |  | X | OFF | B2-3-1
B2-2-2 | O | ON |  | 3.6815 |  |  | 2P 30A | #03 | #04 | 2P 30A |  | 3.7073 |  |  | X | OFF | B2-3-2
B2-2-3 | O | ON |  |  | 1.3535 |  | 2P 30A | #05 | #06 | 2P 30A |  |  | 4.3305 |  | X | OFF | B2-3-3
B2-2-4 | O | ON | 3.7081 |  |  |  | 2P 30A | #07 | #08 | 2P 30A | 3.5495 |  |  |  | X | OFF | B2-3-4
B2-2-5 | O | ON |  | 3.7827 |  |  | 2P 30A | #09 | #10 | 2P 30A |  | 0 |  |  | X | OFF | B2-3-5
B2-2-6 | O | ON |  |  | 4.349 | `` | 2P 30A | #11 | #12 | 2P 30A |  |  | 0 |  | X | OFF | B2-3-6
B2-2-7 | O | ON | 2.7069 |  |  |  | 2P 30A | #13 | #14 | 2P 30A | 0 |  |  |  | X | OFF | B2-3-7
B2-2-8 | O | ON |  | 3.6241 |  |  | 2P 30A | #15 | #16 | 2P 30A |  | 0 |  |  | O | ON | B2-3-8 (AD-12)
B2-2-9 | O | ON |  |  | 1.794 |  | 2P 30A | #17 | #18 | 2P 30A |  |  | 0 |  | O | ON | B2-3-9 (AD-11)
B2-5-1 | X | OFF | 0 |  |  |  | 2P 30A | #19 | #20 | 2P 30A | 0 |  |  |  | O | OFF | B2-6-8
B2-5-2 | X | OFF |  | 0 |  |  | 2P 30A | #21 | #22 | 2P 30A |  | 0 |  |  | O | ON | B2-7-1 (V-17)
B2-5-3 | X | OFF |  |  | 0 |  | 2P 30A | #23 | #24 | 2P 30A |  |  | 0 |  | O | ON | B2-7-2 (V-17)
B2-5-4 | X | OFF | 0 |  |  |  | 2P 30A | #25 | #26 | 2P 30A | 0 |  |  |  | O | ON | B2-7-3 (V-16)
B2-5-5 | X | OFF |  | 0 |  |  | 2P 30A | #27 | #28 | 2P 30A |  | 0 |  |  | O | ON | B2-7-4 (V-15)
B2-5-6 | X | OFF |  |  | 0 |  | 2P 30A | #29 | #30 | 2P 30A |  |  | 0 |  | O | ON | B2-7-5 (V-14)
B2-5-7 | X | OFF | 0 |  |  |  | 2P 30A | #31 | #32 | 2P 30A | 0 |  |  |  | O | ON | B2-7-6 (V-13)
B2-5-8 (AB-12) | O | ON |  | 0 |  |  | 2P 30A | #33 | #34 | 2P 30A |  | 0 |  |  | O | ON | B2-7-7 (V-12)
B2-5-9 (AB-11) | O | ON |  |  | 0 |  | 2P 30A | #35 | #36 | 2P 30A |  |  | 0 |  | O | OFF | B2-7-8 (V-11)
B2-6-1 | O | OFF | 0 |  |  |  | 2P 30A | #37 | #38 | 2P 30A | 0 |  |  |  | O | ON | B2-8-1 (V-16)
B2-6-2 | O | OFF |  | 0 |  |  | 2P 30A | #39 | #40 | 2P 30A |  | 0 |  |  | O | ON | B2-8-2 (W-17)
B2-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | #42 | 2P 30A |  |  | 0 |  | O | ON | B2-8-3 (W-16)
B2-6-4 | O | OFF | 0 |  |  |  | 2P 30A | #43 | #44 | 2P 30A | 0 |  |  |  | O | ON | B2-8-4 (W-15)
B2-6-5 | O | OFF |  | 0 |  |  | 2P 30A | #45 | #46 | 2P 30A |  | 0 |  |  | O | ON | B2-8-5 (W-14)
B2-6-6 | O | OFF |  |  | 0 |  | 2P 30A | #47 | #48 | 2P 30A |  |  | 0 |  | O | ON | B2-8-6 (W-13)
| X | OFF | 0 |  |  |  | 2P 30A | #49 | #50 | 2P 30A | 0 |  |  |  | X | OFF
[10 empty] | 총합: | 17.9273 | 14.7956 | 11.827
6-DaHall 1-PDU-05 |  | PDU : SEL1 - 6-1 - A3 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 19.5 | 43.6 | 27 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
A5-8-7 (W-12) | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 11.2383 |  |  | O | ON | A5-15-1 (T-11)
A5-8-8 (W-11) | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 5.0572 |  | O | ON | A5-15-2 (T-12)
A5-9-1 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0.90135 |  |  |  | O | ON | A5-15-3 (T-13)
A5-9-2 (X-17) | O | ON |  | 1.9103 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 2.8769 |  |  | O | ON | A5-15-4 (T-14)
A5-9-3 (X-16) | O | ON |  |  | 0.89207 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0.81076 |  | O | ON | A5-15-5 (T-15)
A5-9-4 (X-15) | O | ON | 1.679 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 1.3706 |  |  |  | O | ON | A5-15-6 (T-16)
A5-9-5 (X-14) | O | ON |  | 2.1577 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 4.6426 |  |  | O | ON | A5-15-7 (T-17)
A5-9-6 (X-13) | O | ON |  |  | 3.4769 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 3.0141 |  | O | ON | A5-15-8 (T-18)
A5-9-7 (X-12) | O | ON | 0.98465 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0.64266 |  |  |  | O | OFF | A5-15-9
A5-9-8 (X-11) | O | ON |  | 6.0168 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 1.9902 |  |  | O | ON | A5-17-1 (Q-11)
A5-10-1 | O | OFF |  |  | 1.7327 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 5.4581 |  | O | ON | A5-17-2 (Q-12)
A807(A5-10-2) | O | ON | 4.6003 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 3.9811 |  |  |  | O | ON | A5-17-3 (Q-13)
A5-10-3 (A806 - 1) | O | ON |  | 4.0564 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 4.0684 |  |  | O | ON | A5-17-4 (Q-14)
A5-10-4 (A806 - 2) | O | ON |  |  | 3.8298 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 11.2911 |  | O | ON | A5-17-5 (Q-15)
A5-10-5 (Y-14) | O | ON | 3.0856 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0.67087 |  |  |  | O | ON | A5-17-6 (Q-16)
A5-10-6 (Y-13) | O | ON |  | 1.7472 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0.80332 |  |  | O | ON | A5-17-7 (Q-17)
A5-10-7 (Y-12) | O | ON |  |  | 1.1758 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 4.6033 |  | O | ON | A5-17-8 (Q-18)
A5-10-8 (Y-11) | O | ON | 1.2189 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | A5-17-9 (Q-19)
A5-14-1 (U-10) | O | ON |  | 2.8963 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | A5-18-1 (P-11)
A5-14-2 (U-11) | O | ON |  |  | 2.0485 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A5-18-2 (P-12)
A5-14-3 (U-12) | O | ON | 1.6434 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | A5-18-3 (P-13)
A5-14-4 (U-13) | O | ON |  | 5.6121 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | A5-18-4 (P-14)
A5-14-5 (U-14) | O | ON |  |  | 4.8328 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | A5-18-5 (P-15)
6-1-A3-47 | O | ON | 4.0582 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | ON | A5-16-3 (R-13)
A5-14-7 (U-16) | O | ON |  | 8.0073 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | ON | A5-4-9 (AC-11)
6-1-A3-51 | O | ON |  |  | 3.9897 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | A5-6-7
6-1-A3-53 | O | ON | 5.3934 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 4.2204 |  |  |  | O | ON | A5-15-5(2) (T-15)
[10 empty] | 총합: | 34.4503 | 58.0237 | 52.2127
6-DaHall 1-PDU-06 |  | PDU : SEL1 - 6-1 - B3 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 12.5 | 37.1 | 24.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
B5-8-7 (W-12) | O | ON |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 10.1692 |  |  | O | ON | B5-15-1 (T-11)
B5-8-8 (W-11) | O | ON |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 3.9771 |  | O | ON | B5-15-2 (T-12)
B5-9-1 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0.91604 |  |  |  | O | ON | B5-15-3 (T-13)
B5-9-2 | O | ON |  | 3.3356 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 3.3545 |  |  | O | ON | B5-15-4 (T-14)
B5-9-3 | O | ON |  |  | 0.85562 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0.52556 |  | O | ON | B5-15-5 (T-15)
B5-9-4 (X-15) | O | ON | 1.844 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | B5-15-6 (T-16)
B5-9-5 (X-14) | O | ON |  | 3.2965 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 2.8993 |  |  | O | ON | B5-15-7 (T-17)
B5-9-6 (X-13) | O | ON |  |  | 2.8372 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 3.516 |  | O | ON | B5-15-8 (T-18)
B5-9-7 (X-12) | O | ON | 0.96036 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0.36842 |  |  |  | O | OFF | B5-15-9
B5-9-8 (X-11) | O | ON |  | 6.2576 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 1.8103 |  |  | O | ON | B5-17-1 (Q-11)
B5-10-1 | O | OFF |  |  | 0.35861 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 4.6349 |  | O | ON | B5-17-2 (Q-12)
A807(B5-10-2) | O | ON | 4.6799 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 3.6619 |  |  |  | O | ON | B5-17-3 (Q-13)
B5-10-3 (A806 - 1) | O | ON |  | 2.3916 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 4.6273 |  |  | O | ON | B5-17-4 (Q-14)
B5-10-4 (A806 - 2) | O | ON |  |  | 1.7876 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 10.2002 |  | O | ON | B5-17-5 (Q-15)
B5-10-5 (Y-14) | O | ON | 1.9383 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0.65334 |  |  |  | O | ON | B5-17-6 (Q-16)
B5-10-6 (Y-13) | O | ON |  | 0.94217 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0.51022 |  |  | O | ON | B5-17-7 (Q-17)
B5-10-7 (Y-12) | O | ON |  |  | 1.1485 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 3.0602 |  | O | ON | B5-17-8 (Q-18)
B5-10-8 (Y-11) | O | ON | 1.0842 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | B5-17-9 (Q-19)
A5-14-1 (U-10) | O | ON |  | 2.7648 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | B5-18-1 (P-11)
A5-14-2 (U-11) | O | ON |  |  | 1.8605 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | B5-18-2 (P-12)
A5-14-3 (U-12) | O | ON | 0.52803 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | B5-18-3 (P-13)
A5-14-4 (U-13) | O | ON |  | 4.77 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | B5-18-4 (P-14)
A5-14-5 (U-14) | O | ON |  |  | 4.9243 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | B5-18-5 (P-15)
6-1-B3-47 | O | ON | 3.7379 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | ON | B5-16-3 (R-13)
A5-14-7 (U-16) | O | ON |  | 1.3018 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | ON | B5-4-9 (AC-11)
6-1-B3-51 | O | ON |  |  | 4.5523 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | B5-6-7
6-1-B3-53 | O | ON | 0.57475 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 2.4267 |  |  |  | O | ON | B5-15-5(2) (T-15)
[10 empty] | 총합: | 23.3739 | 48.4308 | 44.2386
6-DaHall 1-PDU-07 |  | PDU : SEL1 - 6-1 - A4 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
#A6-4-4 | O | OFF |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | A6-4-1
#A6-4-7 | O | OFF |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | A6-4-2
#A6-5-4 | O | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | A6-4-3
#A6-5-7 | O | OFF |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | ON | A6-4-4 (AC-16)
#A6-6-3 | O | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | ON | A6-4-5 (AC-15)
#A6-6-6 | O | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | A6-4-6 (AC-14)
#A6-7-3 | O | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | ON | A6-4-7 (AC-13)
#A6-7-6 | O | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | A6-5-1
#A6-8-3 | O | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | A6-5-2
#A6-8-6 | O | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | A6-5-3
#A6-9-3 | O | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | A6-5-4 (AB-16)
#A6-9-6 | O | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | A6-5-5 (AB-15)
#A6-10-3 | O | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | A6-5-6 (AB-14)
#A6-10-6 | O | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | A6-5-7 (AB-13)
#A6-14-4 | O | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | OFF | A6-2-1
#A6-14-7 | O | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | OFF | A6-2-2
#A6-15-4 | O | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | OFF | A6-2-3
#A6-15-7 | O | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | A6-2-4 (AE-16)
#A6-17-4 | O | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | A6-2-5 (AE-15)
#A6-17-7 | O | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | A6-2-6 (AE-14)
A6-8-8(1) | O | ON | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | A6-2-7 (AE-13)
A6-8-7(1) | O | ON |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | A6-2-8 (AE-12)
A6-8-6(1) | O | ON |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | A6-2-9 (AE-11)
불량 | X | OFF | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | A6-3-1
A6-3-7 (AD-13) | O | ON |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | A6-3-2
A6-3-6 (AD-14) | O | ON |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | A6-3-3
A6-3-5 (AD-15) | O | ON | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | ON | A6-3-4 (AD-16)
[10 empty] | 총합: | 0 | 0 | 0
6-DaHall 1-PDU-08 |  | PDU : SEL1 - 6-1 - B4 | [5 empty] | Main CB 4P 300A
[10 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | NO. | NO. | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
#B6-28-3 | X | OFF |  | 0 |  |  | 2P 30A | #01 | #02 | 2P 30A |  | 0 |  |  | O | OFF | B6-4-1
#B6-28-6 | X | OFF |  |  | 0 |  | 2P 30A | #03 | #04 | 2P 30A |  |  | 0 |  | O | OFF | B6-4-2
#B6-29-3 | X | OFF | 0 |  |  |  | 2P 30A | #05 | #06 | 2P 30A | 0 |  |  |  | O | OFF | B6-4-3
#B6-29-6 | X | OFF |  | 0 |  |  | 2P 30A | #07 | #08 | 2P 30A |  | 0 |  |  | O | ON | B6-4-4 (AC-16)
#B6-30-3 | X | OFF |  |  | 0 |  | 2P 30A | #09 | #10 | 2P 30A |  |  | 0 |  | O | ON | B6-4-5 (AC-15)
#B6-30-6 | X | OFF | 0 |  |  |  | 2P 30A | #11 | #12 | 2P 30A | 0 |  |  |  | O | ON | B6-4-6 (AC-14)
#B6-31-3 | X | OFF |  | 0 |  |  | 2P 30A | #13 | #14 | 2P 30A |  | 0 |  |  | O | ON | B6-4-7 (AC-13)
#B6-31-6 | X | OFF |  |  | 0 |  | 2P 30A | #15 | #16 | 2P 30A |  |  | 0 |  | O | OFF | B6-5-1
#B6-32-3 | X | OFF | 0 |  |  |  | 2P 30A | #17 | #18 | 2P 30A | 0 |  |  |  | O | OFF | B6-5-2
#B6-32-6 | X | OFF |  | 0 |  |  | 2P 30A | #19 | #20 | 2P 30A |  | 0 |  |  | O | OFF | B6-5-3
#B6-33-3 | X | OFF |  |  | 0 |  | 2P 30A | #21 | #22 | 2P 30A |  |  | 0 |  | O | ON | B6-5-4 (AB-16)
#B6-33-6 | X | OFF | 0 |  |  |  | 2P 30A | #23 | #24 | 2P 30A | 0 |  |  |  | O | ON | B6-5-5 (AB-15)
| X | OFF |  | 0 |  |  | 2P 30A | #25 | #26 | 2P 30A |  | 0 |  |  | O | ON | B6-5-6 (AB-14)
| X | OFF |  |  | 0 |  | 2P 30A | #27 | #28 | 2P 30A |  |  | 0 |  | O | ON | B6-5-7 (AB-13)
| X | OFF | 0 |  |  |  | 2P 30A | #29 | #30 | 2P 30A | 0 |  |  |  | O | OFF | B6-2-1
| X | OFF |  | 0 |  |  | 2P 30A | #31 | #32 | 2P 30A |  | 0 |  |  | O | OFF | B6-2-2
| X | OFF |  |  | 0 |  | 2P 30A | #33 | #34 | 2P 30A |  |  | 0 |  | O | OFF | B6-2-3
| X | OFF | 0 |  |  |  | 2P 30A | #35 | #36 | 2P 30A | 0 |  |  |  | O | ON | B6-2-4 (AE-16)
| X | OFF |  | 0 |  |  | 2P 30A | #37 | #38 | 2P 30A |  | 0 |  |  | O | ON | B6-2-5 (AE-15)
| X | OFF |  |  | 0 |  | 2P 30A | #39 | #40 | 2P 30A |  |  | 0 |  | O | ON | B6-2-6 (AE-14)
| X | OFF | 0 |  |  |  | 2P 30A | #41 | #42 | 2P 30A | 0 |  |  |  | O | ON | B6-2-7 (AE-13)
B6-8-8(1) | O | ON |  | 0 |  |  | 2P 30A | #43 | #44 | 2P 30A |  | 0 |  |  | O | ON | B6-2-8 (AE-12)
B6-8-7(1) | O | ON |  |  | 0 |  | 2P 30A | #45 | #46 | 2P 30A |  |  | 0 |  | O | ON | B6-2-9 (AE-11)
B6-8-6(1) | O | ON | 0 |  |  |  | 2P 30A | #47 | #48 | 2P 30A | 0 |  |  |  | O | OFF | B6-3-1
B6-3-7 (AD-13) | O | ON |  | 0 |  |  | 2P 30A | #49 | #50 | 2P 30A |  | 0 |  |  | O | OFF | B6-3-2
B6-3-6 (AD-14) | O | ON |  |  | 0 |  | 2P 30A | #51 | #52 | 2P 30A |  |  | 0 |  | O | OFF | B6-3-3
B6-3-5 (AD-15) | O | ON | 0 |  |  |  | 2P 30A | #53 | #54 | 2P 30A | 0 |  |  |  | O | ON | B6-3-4 (AD-16)
[10 empty] | 총합: | 0 | 0 | 0
| IDC | 562.4315

## 5층_부하량(월간_MIN)
Date : 2023-11-01 ~ 2023-11-30
5-DaHall 1-CEP-05 | [8 empty] | Main CB 4P 350A
[12 empty] | MAIN 계측값 : | 62.2 | 67 | 61.8 | <- 실측값 |  |  | -1
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
5-DaHall 1-CRAC-16 보조 5F-2호기(구글) | O | ON | 0 | 0 | 0 |  | 4P 50A | #01 | . | . | #02 | 4P 50A | 0 | 0 | 0 |  | O | ON | 5-DaHall 1-CRAC-15 보조 5F-1호기(구글)
5-DaHall 1-CRAC-01 LG CRAC #01 | O | ON | 0 | 0 | 0 |  | 4P 50A | #03 | . | . | #04 | 4P 50A | 0 | 0 | 0 |  | O | ON | 5-DaHall 1-CRAC-02 LG CRAC #02
5-DaHall 1-CRAC-03 LG CRAC #03 | O | ON | 0 | 0 | 0 |  | 4P 50A | #05 | . | . | #06 | 4P 50A | 0 | 0 | 0 |  | O | ON | 5-DaHall 1-CRAC-04 LG CRAC #04
5-DaHall 1-CRAC-05 LG CRAC #05 | O | ON | 0 | 0 | 0 |  | 4P 50A | #07 | . | . | #08 | 4P 50A | 0 | 0 | 0 |  | O | ON | 5-DaHall 1-CRAC-06 LG CRAC #06
5-DaHall 1-CRAC-07 LG CRAC #07 | O | ON | 0 | 0 | 0 |  | 4P 50A | #09 | . | . | #10 | 4P 50A | 0 | 0 | 0 |  | O | ON | 5-DaHall 1-CRAC-08 LG CRAC #08
5-DaHall 1-CRAC-09 LG CRAC #09 | O | ON | 0 | 0 | 0 |  | 4P 50A | #11 | . | . | #12 | 4P 50A | 0 | 0 | 0 |  | O | ON | 5-DaHall 1-CRAC-13 CF CRAC #01
spare | X | OFF | 0 |  |  |  | 2P 30A | #13 | . | . | #14 | 2P 30A | 0 |  |  |  | X | OFF | spare
spare | X | OFF |  | 0 |  |  | 2P 30A | #15 | . | . | #16 | 2P 50A |  | 0 |  |  | O | ON | 5-DaHall 1-EH (5층 가습기 Main)
spare | X | OFF |  |  | 0 |  | 2P 30A | #17 | . | . | #18 | 2P 50A |  |  | 5.82 |  | O | ON | 4-DaHall 1-EH (4층 가습기 Main)
[12 empty] | 합계: | 0 | 0 | 5.82
5-DaHall 1-CEP-06 | [8 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 0.7 | 0 | 0.7 | <- 실측값
[10 empty] | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
[10 empty] | . | #01 | 4P 60A | 0.24 | 0 | 0.23 |  | O | ON | LG CRAC #10 (수냉식)
[10 empty] | . | #02 | 4P 60A | 0.24 | 0 | 0.23 |  | O | ON | LG CRAC #11 (수냉식)
[10 empty] | . | #03 | 4P 60A | 0.24 | 0 | 0.22 |  | O | ON | LG CRAC #12 (수냉식)
[10 empty] | . | #04 | 4P 60A | 0 | 0 | 0 |  | X | OFF | spare
[12 empty] | 합계: | 0.72 | 0 | 0.68
5-DaHall 1-PDU-01 |  | PDU : SEL1 - 5-1 - A1 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 34.6 | 37.8 | 27.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0.58 | 0.73 |  | O | ON | 보다폰정류기-A
1A-1-1 | O | ON | 0 |  |  |  | 2P 30A | #01 | CF상면 |  | #02 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-21 / 1A-2-11
1A-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | CF상면 | 구글202-A | #04 | 2P 30A |  | 0 |  |  | O | ON | 1A-2-12
1A-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | CF상면 | 구글201-A | #06 | 2P 30A |  |  | 1.52 |  | O | ON | 1A-2-13
1A-1-4 | O | OFF | 0 |  |  |  | 2P 30A | #07 | CF상면 |  | #08 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-24 / 1A-2-14
G1101 (1A-1-5) | O | ON |  | 9.29 |  |  | 2P 30A | #09 | cloudflare | 구글 시스템박스 | #10 | 2P 30A |  | 0 |  |  | O | ON | 1A-2-15
G1102 (1A-1-6) | O | ON |  |  | 8.18 |  | 2P 30A | #11 | cloudflare | 철거필요 | #12 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-1
G1103 (1A-1-7) | O | ON | 9.79 |  |  |  | 2P 30A | #13 | cloudflare | 철거필요 | #14 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-2
G1104 (1A-1-8) | O | ON |  | 0 |  |  | 2P 30A | #15 | cloudflare | 철거필요 | #16 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-3
G1105 (1A-1-9) | O | ON |  |  | 0 |  | 2P 30A | #17 | cloudflare | 철거필요 | #18 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-4
1A-1-10 | O | ON | 1.03 |  |  |  | 2P 30A | #19 | 구글104-A | 철거필요 | #20 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-5
1A-1-11 | O | ON |  | 1.39 |  |  | 2P 30A | #21 | 구글103-A | 철거필요 | #22 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-6
1A-1-12 | O | ON |  |  | 1.48 |  | 2P 30A | #23 | 구글102-A | 철거필요 | #24 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-7
1A-1-13 | O | ON | 0 |  |  |  | 2P 30A | #25 | 구글101-A | 철거필요 | #26 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-8
1A-1-14 | O | OFF |  | 0 |  |  | 2P 30A | #27 |  | 철거필요 | #28 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-9
1A-1-15 | O | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | O | OFF | 5F-P-20 / 1A-3-10
G1201 (1A-2-1) | O | ON | 8.84 |  |  |  | 2P 30A | #31 | cloudflare |  | #32 | 2P 30A | 0 |  |  |  | O | OFF | 5F-P-21 / 1A-3-11
G1202 (1A-2-2) | O | ON |  | 6.91 |  |  | 2P 30A | #33 | cloudflare |  | #34 | 2P 30A |  | 0 |  |  | O | OFF | 5F-P-22 / 1A-3-12
G1203 (1A-2-3) | O | ON |  |  | 7.84 |  | 2P 30A | #35 | cloudflare |  | #36 | 2P 30A |  |  | 0 |  | O | OFF | 5F-P-23 / 1A-3-13
G1204 (1A-2-4) | O | ON | 5.99 |  |  |  | 2P 30A | #37 | cloudflare |  | #38 | 2P 30A | 0 |  |  |  | O | OFF | 5F-P-24 / 1A-3-14
G1205 (1A-2-5) | O | ON |  | 8.6 |  |  | 2P 30A | #39 | cloudflare | ?? | #40 | 2P 30A |  | 0 |  |  | X | OFF
1A-2-6 | O | OFF |  |  | 0 |  | 2P 30A | #41 | CF상면 | 보다폰 케이지 안쪽 | #42 | 2P 30A |  |  | 0 |  | O | OFF | 1A-4-1
1A-2-7 | O | OFF | 0 |  |  |  | 2P 30A | #43 | CF상면 | 보다폰 케이지 안쪽 | #44 | 2P 30A | 0 |  |  |  | O | OFF | 1A-4-2
1A-2-8 | O | OFF |  | 0 |  |  | 2P 30A | #45 | CF상면 | 보다폰 케이지 안쪽 | #46 | 2P 30A |  | 0.35 |  |  | O | ON | 1A-4-3
1A-2-9 | O | OFF |  |  | 0 |  | 2P 30A | #47 | CF상면 | Vodafone | #48 | 2P 30A |  |  | 1.72 |  | O | ON | VF Rack#1-상
5F-Q-20 | O | OFF | 0 |  |  |  | 2P 30A | #49 |  | Vodafone | #50 | 2P 30A | 0 |  |  |  | O | ON | VF Rack#2-상
[12 empty] | 합계: | 25.65 | 27.12 | 21.47
5-DaHall 1-PDU-02 |  | PDU : SEL1 - 5-1 - B1 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 34.6 | 35.2 | 26.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0.66 | 0.73 |  | O | ON | 보다폰정류기-B
1B-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | CF상면 |  | #02 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-21 / 1B-2-11
1B-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | CF상면 | 구글202-A | #04 | 2P 30A |  | 0 |  |  | O | ON | 1B-2-12
1B-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | CF상면 | 구글201-A | #06 | 2P 30A |  |  | 1.24 |  | O | ON | 1B-2-13
1B-1-4 | O | OFF | 0 |  |  |  | 2P 30A | #07 | CF상면 |  | #08 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-24 / 1B-2-14
G1101 (1B-1-5) | O | ON |  | 7.69 |  |  | 2P 30A | #09 | cloudflare | 구글Cage 지문인식기 | #10 | 2P 30A |  | 0 |  |  | O | ON | 1B-2-15
G1102 (1B-1-6) | O | ON |  |  | 9.17 |  | 2P 30A | #11 | cloudflare |  | #12 | 2P 30A |  |  | 0 |  | O | OFF | 1B-3-1
G1103 (1B-1-7) | O | ON | 8.23 |  |  |  | 2P 30A | #13 | cloudflare |  | #14 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-2
G1104 (1B-1-8) | O | ON |  | 0 |  |  | 2P 30A | #15 | cloudflare |  | #16 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-3
G1105 (1B-1-9) | O | ON |  |  | 0 |  | 2P 30A | #17 | cloudflare |  | #18 | 2P 30A |  |  | 0 |  | O | ON | 1B-3-4
1B-1-10 | O | ON | 0 |  |  |  | 2P 30A | #19 | 구글104-A |  | #20 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-5
1B-1-11 | O | ON |  | 1.53 |  |  | 2P 30A | #21 | 구글103-A |  | #22 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-6
1B-1-12 | O | ON |  |  | 1.26 |  | 2P 30A | #23 | 구글102-A |  | #24 | 2P 30A |  |  | 0 |  | O | ON | 1B-3-7
1B-1-13 | O | ON | 0 |  |  |  | 2P 30A | #25 | 구글101-A |  | #26 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-8
1B-1-14 | O | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-9
1B-1-15 | O | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | O | ON | 5F-P-20 / 1B-3-10
G1201 (1A-2-1) | O | ON | 9.82 |  |  |  | 2P 30A | #31 | cloudflare |  | #32 | 2P 30A | 0 |  |  |  | O | ON | 5F-P-21 / 1B-3-11
G1202 (1B-2-2) | O | ON |  | 8.12 |  |  | 2P 30A | #33 | cloudflare |  | #34 | 2P 30A |  | 0 |  |  | O | ON | 5F-P-22 / 1B-3-12
G1203 (1B-2-3) | O | ON |  |  | 6.21 |  | 2P 30A | #35 | cloudflare |  | #36 | 2P 30A |  |  | 0 |  | O | ON | 5F-P-23 / 1B-3-13
G1204 (1B-2-4) | O | ON | 6.9 |  |  |  | 2P 30A | #37 | cloudflare |  | #38 | 2P 30A | 0 |  |  |  | O | ON | 5F-P-24 / 1B-3-14
G1205 (1B-2-5) | O | ON |  | 7.23 |  |  | 2P 30A | #39 | cloudflare |  | #40 | 2P 30A |  | 0 |  |  | O | OFF | 5F-P-25 / 1B-3-15
1B-2-6 | O | OFF |  |  | 0 |  | 2P 30A | #41 | CF상면 | ?? | #42 | 2P 30A |  |  | 0 |  | O | OFF | 1B-7-1(2)
1B-2-7 | O | OFF | 0 |  |  |  | 2P 30A | #43 | CF상면 |  | #44 | 2P 30A | 0 |  |  |  | O | OFF | 1B-4-2
1B-2-8 | O | OFF |  | 0 |  |  | 2P 30A | #45 | CF상면 | 보다폰 케이지 안쪽 | #46 | 2P 30A |  | 0.38 |  |  | O | ON | 1B-4-3
1B-2-9 | O | OFF |  |  | 0 |  | 2P 30A | #47 | CF상면 | Vodafone | #48 | 2P 30A |  |  | 1.09 |  | O | ON | VF Rack#1-하
5F-Q-20 | O | OFF | 0 |  |  |  | 2P 30A | #49 |  | Vodafone | #50 | 2P 30A | 0 |  |  |  | O | ON | VF Rack#2-하
[12 empty] | 합계: | 24.95 | 25.61 | 19.7
5-DaHall 1-PDU-03 |  | PDU : SEL1 - 5-1 - A2 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 26.8 | 15.9 | 18 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0 | 0 |  | X | OFF
5F-O-16 / 2A-4-6 | O | ON | 0 |  |  |  | 2P 30A | #01 |  | KG이니시스 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B221 (R13)-1
5F-O-17 / 2A-4-7 | O | ON |  | 0 |  |  | 2P 30A | #03 |  | KG이니시스 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B221 (R13)-2
5F-O-18 | O | ON |  |  | 0 |  | 2P 30A | #05 |  | KG이니시스 | #06 | 2P 30A |  |  | 0.53 |  | O | ON | B222 (R14)-1
5F-O-19 | O | ON | 0 |  |  |  | 2P 30A | #07 |  | KG이니시스 | #08 | 2P 30A | 1.26 |  |  |  | O | ON | B222 (R14)-2
5F-O-20 | O | ON |  | 0 |  |  | 2P 30A | #09 |  | KG이니시스 | #10 | 2P 30A |  | 2.04 |  |  | O | ON | B316 (R15)-1
5F-O-21 | O | ON |  |  | 0 |  | 2P 30A | #11 |  | KG이니시스 | #12 | 2P 30A |  |  | 1.74 |  | O | ON | B316 (R15)-2
5F-O-22 | O | ON | 0 |  |  |  | 2P 30A | #13 |  | KG이니시스 | #14 | 2P 30A | 0.34 |  |  |  | O | ON | B317 (R16)-1
5F-O-23 | O | ON |  | 0 |  |  | 2P 30A | #15 |  | KG이니시스 | #16 | 2P 30A |  | 3.69 |  |  | O | ON | B318 (R17)-1
5F-O-24 | O | ON |  |  | 0 |  | 2P 30A | #17 |  | KG이니시스 | #18 | 2P 30A |  |  | 0.84 |  | O | ON | B319 (R18)
2A-7-2(2) | X | OFF | 0 |  |  |  | 2P 30A | #19 | ?? | KG이니시스 | #20 | 2P 30A | 2.24 |  |  |  | O | ON | B320 (R19)
2A-5-1 | O | OFF |  | 0 |  |  | 2P 30A | #21 | 보다폰상면 | KG이니시스 | #22 | 2P 30A |  | 2.81 |  |  | O | ON | B321 (R20)
2A-5-2 | O | ON |  |  | 0 |  | 2P 30A | #23 | 보다폰상면 | KG이니시스 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B322 (R21)
2A-5-3 | O | ON | 0 |  |  |  | 2P 30A | #25 | 보다폰상면 | KG이니시스 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B416 (R22)
2A-5-4 | O | ON |  | 0 |  |  | 2P 30A | #27 | 보다폰상면 | KG이니시스 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B417 (R23)
2A-5-5 | O | ON |  |  | 0 |  | 2P 30A | #29 |  | KG이니시스 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B418 (R24)
5-1-A2-31 | X | OFF | 0 |  |  |  | 2P 30A | #31 |  | KG이니시스 | #32 | 2P 30A | 2.41 |  |  |  | O | ON | B116 (R12)
5-1-A2-33 | X | OFF |  | 0 |  |  | 2P 30A | #33 |  | KG이니시스 | #34 | 2P 30A |  | 2.14 |  |  | O | ON | B117 (R11)
5-1-A2-35 | X | OFF |  |  | 0 |  | 2P 30A | #35 |  | KG이니시스 | #36 | 2P 30A |  |  | 2.16 |  | O | ON | B118 (R10)
B317 (R16)-2 | O | ON | 2.59 |  |  |  | 2P 30A | #37 | KG이니시스 | KG이니시스 | #38 | 2P 30A | 2.31 |  |  |  | O | ON | B119 (R9)
B318 (R17)-2 | O | ON |  | 0 |  |  | 2P 30A | #39 | KG이니시스 | KG이니시스 | #40 | 2P 30A |  | 1.35 |  |  | O | ON | B120 (R8)
B221 (R13)-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | KG이니시스 | KG이니시스 | #42 | 2P 30A |  |  | 1.77 |  | O | ON | B121 (R7)
B222 (R14)-3 | O | ON | 2.17 |  |  |  | 2P 30A | #43 | KG이니시스 | KG이니시스 | #44 | 2P 30A | 2.85 |  |  |  | O | ON | B122 (R6)
B316 (R15)-3 | O | ON |  | 0 |  |  | 2P 30A | #45 | KG이니시스 | KG이니시스 | #46 | 2P 30A |  | 2.83 |  |  | O | ON | B216 (R5)
B219 (R2) | O | ON |  |  | 3.58 |  | 2P 30A | #47 | KG이니시스 | KG이니시스 | #48 | 2P 30A |  |  | 3.42 |  | O | ON | B217 (R4)
B220 (R1) | O | ON | 5.58 |  |  |  | 2P 30A | #49 | KG이니시스 | KG이니시스 | #50 | 2P 30A | 3.81 |  |  |  | O | ON | B218 (R3)
[12 empty] | 합계: | 25.56 | 14.86 | 14.04
5-DaHall 1-PDU-04 |  | PDU : SEL1 - 5-1 - B2 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 25.1 | 15.5 | 18.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| O | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0 | 0 |  | O | OFF
5F-O-16 / 2B-4-6 | O | ON | 0 |  |  |  | 2P 30A | #01 | 철거가능 | KG이니시스 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B221 (R13)-1
5F-O-17 / 2B-4-7 | O | ON |  | 0 |  |  | 2P 30A | #03 | 철거가능 | KG이니시스 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B221 (R13)-2
5F-O-18 | O | ON |  |  | 0 |  | 2P 30A | #05 | 철거가능 | KG이니시스 | #06 | 2P 30A |  |  | 0.53 |  | O | ON | B222 (R14)-1
5F-O-19 | O | ON | 0 |  |  |  | 2P 30A | #07 | 철거가능 | KG이니시스 | #08 | 2P 30A | 1.57 |  |  |  | O | ON | B222 (R14)-2
5F-O-20 | O | ON |  | 0 |  |  | 2P 30A | #09 | 철거가능 | KG이니시스 | #10 | 2P 30A |  | 1.98 |  |  | O | ON | B316 (R15)-1
5F-O-21 | O | ON |  |  | 0 |  | 2P 30A | #11 | 철거가능 | KG이니시스 | #12 | 2P 30A |  |  | 1.78 |  | O | ON | B316 (R15)-2
5F-O-22 | O | ON | 0 |  |  |  | 2P 30A | #13 | 철거가능 | KG이니시스 | #14 | 2P 30A | 0.4 |  |  |  | O | ON | B317 (R16)-1
5F-O-23 | O | ON |  | 0 |  |  | 2P 30A | #15 | 철거가능 | KG이니시스 | #16 | 2P 30A |  | 3.72 |  |  | O | ON | B318 (R17)-1
5F-O-24 | O | ON |  |  | 0 |  | 2P 30A | #17 | 철거가능 | KG이니시스 | #18 | 2P 30A |  |  | 0.85 |  | O | ON | B319 (R18)
2B-7-2(2) | O | OFF | 0 |  |  |  | 2P 30A | #19 | ?? | KG이니시스 | #20 | 2P 30A | 1.36 |  |  |  | O | ON | B320 (R19)
2B-5-1 | O | OFF |  | 0 |  |  | 2P 30A | #21 | 보다폰상면 | KG이니시스 | #22 | 2P 30A |  | 4.42 |  |  | O | ON | B321 (R20)
2B-5-2 | O | ON |  |  | 0 |  | 2P 30A | #23 | 보다폰상면 | KG이니시스 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B322 (R21)
2B-5-3 | O | ON | 0 |  |  |  | 2P 30A | #25 | 보다폰상면 | KG이니시스 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B416 (R22)
2B-5-4 | O | ON |  | 0 |  |  | 2P 30A | #27 | 보다폰상면 | KG이니시스 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B417 (R23)
2B-5-5 | O | ON |  |  | 0 |  | 2P 30A | #29 | 철거필요 | KG이니시스 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B418 (R24)
| X | OFF | 0 |  |  |  | 2P 30A | #31 | 철거필요 | KG이니시스 | #32 | 2P 30A | 0.26 |  |  |  | O | ON | B116 (R12)
| X | OFF |  | 0 |  |  | 2P 30A | #33 | 철거필요 | KG이니시스 | #34 | 2P 30A |  | 0.28 |  |  | O | ON | B117 (R11)
| X | OFF |  |  | 0 |  | 2P 30A | #35 | 철거가능 | KG이니시스 | #36 | 2P 30A |  |  | 2.27 |  | O | ON | B118 (R10)
B317 (R16)-2 | O | ON | 3.22 |  |  |  | 2P 30A | #37 | KG이니시스 | KG이니시스 | #38 | 2P 30A | 2.47 |  |  |  | O | ON | B119 (R9)
B318 (R17)-2 | O | ON |  | 0 |  |  | 2P 30A | #39 | KG이니시스 | KG이니시스 | #40 | 2P 30A |  | 1.44 |  |  | O | ON | B120 (R8)
B221 (R13)-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | KG이니시스 | KG이니시스 | #42 | 2P 30A |  |  | 1.57 |  | O | ON | B121 (R7)
B222 (R14)-3 | O | ON | 2.22 |  |  |  | 2P 30A | #43 | KG이니시스 | KG이니시스 | #44 | 2P 30A | 2.26 |  |  |  | O | ON | B122 (R6)
B316 (R15)-3 | O | ON |  | 0 |  |  | 2P 30A | #45 | KG이니시스 | KG이니시스 | #46 | 2P 30A |  | 2.29 |  |  | O | ON | B216 (R5)
B219 (R2) | O | ON |  |  | 3.94 |  | 2P 30A | #47 | KG이니시스 | KG이니시스 | #48 | 2P 30A |  |  | 2.93 |  | O | ON | B217 (R4)
B220 (R1) | O | ON | 5.3 |  |  |  | 2P 30A | #49 | KG이니시스 | KG이니시스 | #50 | 2P 30A | 3.63 |  |  |  | O | ON | B218 (R3)
[12 empty] | 합계: | 22.69 | 14.13 | 13.87
PDU6B-1T |  | PDU : | [6 empty] | Main CB 4P 150A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A |  |  |  |  | X | OFF
1T-1-3 | O | OFF |  |  |  |  | 3P 30A | #03 | CF상면 | . | #04 | 3P 30A |  |  |  |  | O | OFF | 1T-4-3
1T-1-6 | O | OFF |  |  |  |  | 3P 30A | #05 | CF상면 | . | #06 | 3P 30A |  |  |  |  | O | OFF | 1T-4-6
1T-1A9 | O | OFF |  |  |  |  | 3P 30A | #07 | . | . | #08 | 3P 30A |  |  |  |  | O | OFF | 1T-4-9
1T-1-12 | O | OFF |  |  |  |  | 3P 30A | #09 | Google상면 | . | #10 | 3P 30A |  |  |  |  | O | OFF | 1T-4-12
1T-2-3 | O | OFF |  |  |  |  | 3P 30A | #11 | CF상면 | . | #12 | 3P 20A |  |  |  |  | O | OFF | 1T-5-3
1T-2-6 | O | OFF |  |  |  |  | 3P 20A | #13 | . | . | #14 | 3P 20A |  |  |  |  | O | OFF | 1T-5-6
1T-2-9 | O | OFF |  |  |  |  | 3P 20A | #15 | . | . | #16 | 3P 20A |  |  |  |  | O | OFF | 1T-5-9
1T-2-12 | O | OFF |  |  |  |  | 3P 20A | #17 | Google상면 | . | #18 | 3P 20A |  |  |  |  | O | OFF | 1T-5-12
1T-3-3 | O | OFF |  |  |  |  | 3P 20A | #19 | . | . | #20 | 3P 20A |  |  |  |  | O | OFF | 1T-6-2
1T-3-6 | O | OFF |  |  |  |  | 3P 20A | #21 | . | . | #22 | 3P 20A |  |  |  |  | O | OFF | 1T-6-4
1T-3-9 | O | OFF |  |  |  |  | 3P 20A | #23 | . | . | #24 | 3P 20A |  |  |  |  | X | OFF
1T-3-12 | O | OFF |  |  |  |  | 3P 20A | #25 | . | . | #26 | 3P 20A |  |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-05 |  | PDU : SEL1 - 5-1 - A3 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  | 0 |  | 2P 30A | #01 |  |  | #02 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #03 |  |  | #04 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #13 |  |  | #14 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #19 |  |  | #20 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-2
| X | OFF |  | 0 |  |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-3
| X | OFF |  |  | 0 |  | 2P 30A | #25 |  |  | #26 | 2P 30A |  |  | 0 |  | O | OFF | 3A-12-3T
| X | OFF | 0 |  |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-4
| X | OFF |  | 0 |  |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-5
| X | OFF |  |  | 0 |  | 2P 30A | #31 |  |  | #32 | 2P 30A |  |  | 0 |  | O | OFF | 3A-12-6
| X | OFF | 0 |  |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-7
| X | OFF |  | 0 |  |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-8
| X | OFF |  |  | 0 |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #43 |  |  | #44 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-06 |  | PDU : SEL1 - 5-1 - B3 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  | 0 |  | 2P 30A | #01 |  |  | #02 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #03 |  |  | #04 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #13 |  |  | #14 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #19 |  |  | #20 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A | 0 |  |  |  | O | OFF | 3B-12-2
| X | OFF |  | 0 |  |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  | 0 |  |  | O | OFF | 3B-12-3
| X | OFF |  |  | 0 |  | 2P 30A | #25 |  |  | #26 | 2P 30A |  |  | 0 |  | O | OFF | 3B-12-4
| X | OFF | 0 |  |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A | 0 |  |  |  | O | OFF | 3B-12-5
| X | OFF |  | 0 |  |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  | 0 |  |  | O | OFF | 3B-12-6
| X | OFF |  |  | 0 |  | 2P 30A | #31 |  |  | #32 | 2P 30A |  |  | 0 |  | O | OFF | 3B-12-6T
| X | OFF | 0 |  |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A | 0 |  |  |  | O | OFF | 3B-12-7
| X | OFF |  | 0 |  |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  | 0 |  |  | O | OFF | 3B-12-8
| X | OFF |  |  | 0 |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #43 |  |  | #44 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-07 |  | PDU : SEL1 - 5-1 - A4 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 8.6 | 1.1 | 0.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
9A-1-5 (PCCW) /5F-A-14 | O | ON | 7.05 |  |  |  | 3P 30A | #01 | PCCW | 센츄리링크코리아 | #02 | 3P 30A | 0.99 |  |  |  | O | ON | 9A-1-8 / 5F-A-17
9A-1-6 / 5F-A-15 | O | ON |  | 0.4 |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A |  | 0 |  |  | O | ON | 9A-1-9 / 5F-A-18
9A-1-7 / 5F-A-16 | O | ON |  |  | 0 |  | 3P 30A | #05 | PCCW | 세종 인터넷(IES.YSM.S51) | #06 | 3P 30A |  |  | 0 |  | O | ON | 9A-1-10 / 5F-A-19
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #09 |  |  | #10 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 8.04 | 0.4 | 0
5-DaHall 1-PDU-09 |  | PDU : SEL1 - 5-1 - A5 | [6 empty] | Main CB 4P 200A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #03 |  |  | #04 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #09 |  |  | #10 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #37 |  |  | #38 | 3P 20A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-08 |  | PDU : SEL1 - 5-1 - B4 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 6.5 | 1.4 | 1.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01 | 코로케션 | 센츄리링크코리아 | #02 | 3P 30A | 1.16 |  |  |  | O | ON | 9B-1-8 / 5F-A-17
9B-1-6 / 5F-A-15 | O | ON |  | 0 |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A |  | 0 |  |  | O | ON | 9B-1-9 / 5F-A-18
9B-1-7 / 5F-A-16 | O | ON |  |  | 0 |  | 3P 30A | #05 | PCCW | 세종 인터넷(IES.YSM.S51) | #06 | 3P 30A |  |  | 0 |  | O | ON | 9B-1-10 / 5F-A-19
9B-1-5 (PCCW)/5F-A-14 | O | ON | 0 |  |  |  | 3P 30A | #07 | PCCW |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #09 |  |  | #10 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| O | ON |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 1.16 | 0 | 0
5-DaHall 1-PDU-10 |  | PDU : SEL1 - 5-1 - B5 | [6 empty] | Main CB 4P 200A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #03 |  |  | #04 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #09 |  |  | #10 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #37 |  |  | #38 | 3P 20A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-11 |  | PDU : SEL1 - 5-1 - A6 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 15.3 | 10.2 | 9.9 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
1A-1-1 / 5F-A-10 | O | ON | 0 |  |  |  | 3P 30A | #03 | 코로케션 |  | #04 | 3P 30A | 0 |  |  |  | O | OFF | A1-3-2
1A-1-2 / 5F-A-11 | O | ON |  | 0 |  |  | 3P 30A | #05 | 코로케션 | 코로케션 | #06 | 3P 30A |  | 0 |  |  | O | ON | A1-3-3
1A-1-2(2) | O | ON |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 20A |  |  | 0 |  | O | ON | A1-3-4
1A-1-3 / 5F-A-12 | O | ON | 0 |  |  |  | 3P 30A | #09 | PCCW | 코로케션 | #10 | 3P 20A | 0 |  |  |  | O | ON | A1-3-5
1A-1-4 / 5F-A-13 | O | ON |  | 0 |  |  | 3P 30A | #11 | PCCW | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | A1-3-6
1A-1-4(2) / 5F-A-13 (2) | O | ON |  |  | 0 |  | 3P 30A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 0 |  | O | ON | A1-3-7
A1-2-1 / 5F-B-10 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 0 |  |  |  | O | ON | A1-3-8
A1-2-2 / 5F-B-11 | O | ON |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 0 |  |  | O | ON | A1-3-9
A1-2-3 / 5F-B-12 | O | OFF |  |  | 0 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 0 |  | O | ON | A1-3-10
A1-2-4 / 5F-B-13 | O | ON | 0 |  |  |  | 3P 20A | #21 | 다코스 |  | #22 | 3P 20A | 0 |  |  |  | O | ON | A807 / 5F-D-16 / A1-4-7(2)
A1-2-5 / A605 (A) | O | ON |  | 0 |  |  | 3P 20A | #23 | 이비즈네트웍스 | PCCW | #24 | 3P 20A |  | 0 |  |  | O | ON | A1-5-10(2) / 5F-E-19
A1-2-6 / 5F-B-15 | O | ON |  |  | 0 |  | 3P 20A | #25 | 다코스 & NTT | PCCW | #26 | 3P 20A |  |  | 3.03 |  | O | ON | A1-1-3(2) / 5F-A-12(2)
A1-2-7 / 5F-B-16 | O | ON | 0 |  |  |  | 3P 20A | #27 | 제우스네트웍스 |  | #28 | 3P 20A | 0 |  |  |  | O | ON | A1-1-8(2) / 5F-A-17 (2)
A1-2-8 / 5F-B-17 | O | ON |  | 0 |  |  | 3P 20A | #29 | COLT |  | #30 | 3P 20A |  | 0 |  |  | O | ON | 5F-D-18 임시
A1-3-1 | O | OFF |  |  | 0 |  | 3P 20A | #31 |  | 코로케션 | #32 | 3P 20A |  |  | 0 |  | O | ON
[12 empty] | 합계: | 0 | 0 | 3.03
5-DaHall 1-PDU-13 |  | PDU : SEL1 - 5-1 - A7 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 12 | 18.7 | 14.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
A2-2-9 / 5F-B-18 | O | ON | 3.91 |  |  |  | 3P 30A | #03 | 코로케션 | 코로케션 | #04 | 3P 30A | 0 |  |  |  | O | ON | A2-5-4
A2-2-10 / 5F-B-19 | O | ON |  | 0 |  |  | 3P 30A | #05 | PCCW | 코로케션 | #06 | 3P 30A |  | 0 |  |  | O | ON | A2-5-5
A2-4-1 | O | ON |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 0 |  | O | ON | A2-5-6
A2-4-2 | O | ON | 0 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 30A | 0 |  |  |  | O | ON | A2-5-7
A2-4-3 | O | ON |  | 0 |  |  | 3P 20A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | A2-5-8
A2-4-4 | O | ON |  |  | 0.7 |  | 3P 20A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 0 |  | O | ON | A2-5-9
A2-4-5 / 5F-D-14 | O | ON | 0 |  |  |  | 3P 20A | #15 | PCCW | PCCW | #16 | 3P 20A | 0 |  |  |  | O | ON | A2-5-10 / 5F-E-19
A2-4-6 / 5F-D-15 | O | ON |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 0 |  |  | O | OFF | A2-6-1
A2-4-7 | O | ON |  |  | 5.14 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 0 |  | O | OFF | A2-6-2
A2-4-8 | O | ON | 0 |  |  |  | 3P 20A | #21 | 코로케션 | 코로케션 | #22 | 3P 20A | 0 |  |  |  | O | OFF | A2-6-3
A2-4-9 | O | ON |  | 0 |  |  | 3P 20A | #23 | 코로케션 | 코로케션 | #24 | 3P 20A |  | 0 |  |  | O | OFF | A2-6-4
A2-4-10 | O | ON |  |  | 0 |  | 3P 20A | #25 | 코로케션 | 코로케션 | #26 | 3P 20A |  |  | 0 |  | O | ON | A2-6-5 / F-14
A2-5-1 | O | ON | 0 |  |  |  | 3P 20A | #27 | 코로케션 | 코로케션 | #28 | 3P 20A | 0 |  |  |  | O | OFF | A2-6-6 / F-15
A2-5-2 | O | ON |  | 0 |  |  | 3P 20A | #29 | 코로케션 | 코로케션 | #30 | 3P 20A |  | 0 |  |  | O | OFF | A2-6-7 / F-16
A2-5-3 | O | ON |  |  | 0 |  | 3P 20A | #31 | 코로케션 | 코로케션 | #32 | 3P 20A |  |  | 0 |  | O | ON | A2-6-8 / F-17
[12 empty] | 합계: | 3.91 | 0 | 5.84
5-DaHall 1-PDU-15 |  | PDU : SEL1 - 5-1 - A8 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 19.1 | 6.2 | 14.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
AC PDU-3#A | O | ON | 5.97 | 1.25 | 7.85 |  | 3P 50A | #01(3상) | 텔스트라 | 텔스트라 | #02(3상) | 3P 50A | 0 | 0 | 0 |  | O | ON | TO:PDU(A)-3A
| X | OFF | 0 | 0 | 0 |  | 3P 50A | #03(3상) |  | Singtel-1 | #04(3상) | 3P 50A | 0 | 0 | 0 |  | X | OFF | DC정류기A
TRANSDUSER | O | OFF | 0 | 0 | 0 |  | 3P 30A | #05(3상) |  |  | #06(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF | customer con
PUD(A)-3-07 / 5F-B-17 (2) | O | ON | 0.65 |  |  |  | 3P 30A | #07 | COLT |  | #08 | 3P 30A | 0 |  |  |  | O | ON | A1007 / 5F-F-16
PUD(A)-3-09 / 5F-B-17 (3) | O | ON |  | 0 |  |  | 3P 30A | #09 | COLT |  | #10 | 3P 30A |  | 0 |  |  | O | OFF | A1006 / 5F-F-15
A603 / Colt, A-1 (23/08/23 On) | O | ON |  |  | 0 |  | 3P 30A | #11 |  | CMI | #12 | 3P 30A |  |  | 2.31 |  | O | ON | D-15랙(CMI)-A ('21.09.29 투입)
P여(A)-3 싱텔 SKB CWDM A전원 | O | ON | 0 |  |  |  | 3P 30A | #13 |  |  | #14 | 3P 30A | 0 |  |  |  | O | ON | A603 / Colt, 정류기A (23/08/23 On)
PUD(A)-2-15 | X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
PUD(A)-2-17 | X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
PUD(A)-2-19 | X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
PUD(A)-2-21 | X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
PUD(A)-2-23 | O | ON |  |  | 0 |  | 3P 20A | #23 | Singtel-2 |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
DACOM EOS | X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
PUD(A)-2-27 | X | OFF |  | 0 |  |  | 3P 20A | #27 |  | 다코스 & NTT | #28 | 3P 20A |  | 0 |  |  | O | ON | A3-2-6(2) / 5F-B-15 (2)
PUD(A)-2-29 | O | ON |  |  | 0.36 |  | 3P 20A | #29 | Singtel-2 |  | #30 | 3P 20A |  |  | 0 |  | X | OFF | TNSI A
[12 empty] | 합계: | 6.62 | 1.25 | 10.52
5-DaHall 1-PDU-12 |  | PDU : SEL1 - 5-1 - B6 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 20.1 | 13.1 | 14 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
1B-1-1 / 5F-A-10 | O | ON | 0 |  |  |  | 3P 30A | #03 | 코로케션 | 코로케션 | #04 | 3P 30A | 0 |  |  |  | O | ON | B1-3-3
1B-1-2 / 5F-A-11 | O | ON |  | 0 |  |  | 3P 30A | #05 | PCCW | 코로케션 | #06 | 3P 30A |  | 0 |  |  | O | ON | B1-3-4
| X | OFF |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 0 |  | O | ON | B1-3-5
1B-1-4 / 5F-A-13 | O | ON | 0 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 20A | 0 |  |  |  | O | ON | B1-3-6
1B-1-4(2) / 5F-A-13 (2) | O | ON |  | 0 |  |  | 3P 30A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | B1-3-7
B1-2-1 / 5F-B-10 | O | ON |  |  | 0 |  | 3P 20A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 0 |  | O | ON | B1-3-8
B1-2-2 / 5F-B-11 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 0 |  |  |  | O | ON | B1-3-9
B1-2-3 / 5F-B-12 | O | OFF |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 1.89 |  |  | O | ON | B1-3-10
B1-2-4 / 5F-B-13 | O | ON |  |  | 0 |  | 3P 20A | #19 | 다코스 |  | #20 | 3P 20A |  |  | 0 |  | X | OFF
B1-2-5 / A605 (B) | O | ON | 0 |  |  |  | 3P 20A | #21 | 이비즈네트웍스 |  | #22 | 3P 20A | 0 |  |  |  | X | OFF | A807 / 5F-D-16 / B1-4-7(2)
B1-2-6 / 5F-B-15 | O | ON |  | 0 |  |  | 3P 20A | #23 | 다코스 & NTT | PCCW | #24 | 3P 20A |  | 3.47 |  |  | O | ON | B1-5-10(2) / 5F-E-19
B1-2-7 / 5F-B-16 | O | ON |  |  | 3.11 |  | 3P 20A | #25 | 제우스네트웍스 | PCCW | #26 | 3P 20A |  |  | 0 |  | O | ON | 1B-1-3 / 5F-A-12
B1-2-8 / 5F-B-17 | O | ON | 0 |  |  |  | 3P 20A | #27 | COLT |  | #28 | 3P 20A | 3.48 |  |  |  | O | ON | B1-1-8(2) / 5F-A-17 (2)
B1-3-1 | O | ON |  | 0 |  |  | 3P 20A | #29 | 코로케션 | PCCW | #30 | 3P 20A |  | 5.67 |  |  | X | ON | B1-1-3(2) / 5F-A-12 (2)
B1-3-2 | O | OFF |  |  | 0 |  | 3P 20A | #31 | 코로케션 | 코로케션 | #32 | 3P 20A |  |  | 3.05 |  | O | ON | B1-2-9 / 5F-B-18
[12 empty] | 합계: | 3.48 | 11.03 | 6.16
5-DaHall 1-PDU-14 |  | PDU : SEL1 - 5-1 - B7 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 13.4 | 11.6 | 7.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
B2-2-10 / 5F-B-19 | O | ON | 0 |  |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A | 0 |  |  |  | O | ON | B2-5-5
B2-4-1 | O | ON |  | 0 |  |  | 3P 30A | #05 | 코로케션 | 코로케션 | #06 | 3P 30A |  | 0 |  |  | O | ON | B2-5-6
B2-4-2 | O | ON |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 0 |  | O | ON | B2-5-7
B2-4-3 | O | OFF | 0 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 30A | 0 |  |  |  | O | ON | B2-5-8
B2-4-4 | O | ON |  | 0 |  |  | 3P 20A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | B2-5-9
B2-4-5 / 5F-D-14 | O | ON |  |  | 0 |  | 3P 20A | #13 | PCCW | PCCW | #14 | 3P 20A |  |  | 0 |  | O | ON | B2-5-10 / 5F-E-19
B2-4-6 / 5F-D-15 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 0 |  |  |  | O | OFF | B2-6-1
B2-4-7 | O | ON |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 0 |  |  | O | OFF | B2-6-2
B2-4-8 | O | ON |  |  | 2.45 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 0 |  | O | OFF | B2-6-3
B2-4-9 | O | ON | 0 |  |  |  | 3P 20A | #21 | 코로케션 | 코로케션 | #22 | 3P 20A | 0 |  |  |  | O | OFF | B2-6-4
B2-4-10 | O | ON |  | 0 |  |  | 3P 20A | #23 | 코로케션 | 코로케션 | #24 | 3P 20A |  | 0 |  |  | O | ON | B2-6-5 / F-14
B2-5-1 | O | ON |  |  | 0 |  | 3P 20A | #25 | 코로케션 | 코로케션 | #26 | 3P 20A |  |  | 0 |  | O | OFF | B2-6-6 / F-15
B2-5-2 | O | ON | 0 |  |  |  | 3P 20A | #27 | 코로케션 | 코로케션 | #28 | 3P 20A | 0 |  |  |  | O | OFF | B2-6-7 / F-16
B2-5-3 | O | ON |  | 0 |  |  | 3P 20A | #29 | 코로케션 | 코로케션 | #30 | 3P 20A |  | 0 |  |  | O | ON | B2-6-8 / F-17
B2-5-4 | O | ON |  |  | 0 |  | 3P 20A | #31 | 코로케션 |  | #32 | 3P 20A |  |  | 0 |  | O | ON | FMS 5층 메인전원
[12 empty] | 합계: | 0 | 0 | 2.45
5-DaHall 1-PDU-16 |  | PDU : SEL1 - 5-1 - B8 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 20.1 | 11.1 | 16 | <- 실측값 |  |  | <- 디스플래이값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
AC PDU-3#B | O | ON | 4.66 | 1.33 | 6.05 |  | 3P 50A | #01(3상) | 텔스트라 | 텔스트라 | #02(3상) | 3P 50A | 0 | 0 | 0 |  | O | ON | TO:PDU(B)-3A
| X | OFF | 0 | 0 | 0 |  | 3P 50A | #03(3상) |  | Singtel-1 | #04(3상) | 3P 50A | 0 | 0 | 0 |  | X | OFF | DC정류기B
TRANSDUSER | X | OFF | 0 | 0 | 0 |  | 3P 30A | #05(3상) |  |  | #06(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF | customer con
PUD(B)-3-07 / 5F-B-17 (2) | O | ON | 1.51 |  |  |  | 3P 30A | #07 | COLT |  | #08 | 3P 30A | 0.41 |  |  |  | O | ON | A1007 / 5F-F-16
PUD(B)-3-09 / 5F-B-17 (3) | O | ON |  | 0.39 |  |  | 3P 30A | #09 | COLT |  | #10 | 3P 30A |  | 0 |  |  | X | OFF | A1006 / 5F-F-15
A603 / Colt, B-1 (23/08/23 On) | O | ON |  |  | 0 |  | 3P 30A | #11 |  | CMI | #12 | 3P 30A |  |  | 0 |  | O | ON | D-15랙(CMI)-B ('21.09.29 투입)
P여(B)-3 싱텔 SKB CWDM B전원 | O | ON | 0.42 |  |  |  | 3P 30A | #13 |  |  | #14 | 3P 30A | 1.48 |  |  |  | O | ON | A603 / Colt, 정류기B (23/08/23 On)
KT Rack #2 (소형 임시정류기) | O | ON |  | 2.18 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
KT Rack #3 (소형 임시정류기) | O | ON |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
KT Rack #4 (소형 임시정류기) | O | ON | 0 |  |  |  | 3P 20A | #19 |  | 4F BMS | #20 | 3P 20A | 0.59 |  |  |  | O | ON | 신규 BMS(4F TPS실) Rack
텔스트라 CCTV 모니터링PC 및 시스템 박스 | O | ON |  | 0.33 |  |  | 3P 20A | #21 |  | 5F BMS | #22 | 3P 20A |  | 0.59 |  |  | O | ON | 신규 BMS(5F TPS실) Rack
DACOM EOS | O | ON |  |  | 0 |  | 3P 20A | #23 | Singtel-2 | Singtel-2 | #24 | 3P 20A |  |  | 0 |  | O | ON | kt mspp 전원
| O | ON | 0.42 |  |  |  | 3P 20A | #25 | Singtel-2 |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
SKB2.5G전용 PDU B3 27 | O | ON |  | 0.57 |  |  | 3P 20A | #27 | Singtel-2 | 다코스 & NTT | #28 | 3P 20A |  | 0 |  |  | O | ON | B3-2-6(2) / 5F-B-15 (2)
데이콤 AC전원 | O | ON |  |  | 0.29 |  | 3P 20A | #29 | Singtel-2 | Singtel-2 | #30 | 3P 20A |  |  | 0.48 |  | O | ON | TNSI A
[12 empty] | 합계: | 9.49 | 5.39 | 6.82
PDU(C) | [8 empty] | Main CB 4P 50A
[12 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  |  |  | 3P 50A | #01(3상) |  |  | #02(3상) | 3P 50A |  |  |  |  | X | OFF
라우터룸 System box | O | ON |  |  |  |  | 3P 30A | #03(3상) | Singtel-2 |  | #04(3상) | 3P 30A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  |  |  | X | OFF
SYSTEM BOX | X | OFF |  |  |  |  | 3P 30A | #07 |  | Singtel-2 | #08 | 3P 30A |  |  |  |  | O | ON | SYSTEM BOX
customer con | X | OFF |  |  |  |  | 3P 20A | #09 |  | Singtel-2 | #10 | 3P 20A |  |  |  |  | O | ON | SYSTEM BOX
SYSTEM BOX | O | ON |  |  |  |  | 3P 20A | #11 | Singtel-2 |  | #12 | 3P 20A |  |  |  |  | X | OFF | customer con
| O | OFF |  |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A |  |  |  |  | X | OFF | customer con
M/S 단파 | O | ON |  |  |  |  | 3P 20A | #15 | Singtel-2 |  | #16 | 3P 20A |  |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-17 |  | PDU : SEL1 - 5-1 - A9 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 5.5 | 7.2 | 2.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RT-07 | ○ | ON | 0.6 |  |  |  | 2P 30A | #01 | U08-A-01 | U08-A-02 | #02 | 2P 30A | 0 |  |  |  | ○ | ON | RT-08
RT-09 | ○ | ON |  | 0 |  |  | 2P 30A | #03 | U08-A-03 | U08-A-04 | #04 | 2P 30A |  | 0 |  |  | ○ | ON | RT-10
RT-11 | ○ | ON |  |  | 0 |  | 2P 30A | #05 | U08-A-05 | U08-A-06 | #06 | 2P 30A |  |  | 0 |  | ○ | ON | RT-12
RT-13 | ○ | ON | 0 |  |  |  | 2P 30A | #07 | U08-A-07 | U08-A-08 | #08 | 2P 30A | 0 |  |  |  | ○ | ON | RT-14
RT-15 | ○ | ON |  | 0.75 |  |  | 2P 30A | #09 | U08-A-09 | U08-A-10 | #10 | 2P 30A |  | 0 |  |  | ○ | ON | RT-16
RT-17 | ○ | ON |  |  | 0 |  | 2P 30A | #11 | U08-A-11 | U08-A-12 | #12 | 2P 30A |  |  | 0 |  | ○ | ON | RT-18
RT-19 | ○ | ON | 0 |  |  |  | 2P 30A | #13 | U08-A-13 | U08-A-14 | #14 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-01
LSP-02 | ○ | OFF |  | 0 |  |  | 2P 30A | #15 | U08-A-15 | U08-A-16 | #16 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-03
LSP-04 | ○ | ON |  |  | 0 |  | 2P 30A | #17 | U08-A-17 | U08-A-18 | #18 | 2P 30A |  |  | 0 |  | ○ | OFF | LSP-05
LSP-06 | ○ | OFF | 0 |  |  |  | 2P 30A | #19 | U08-A-19 | U08-A-20 | #20 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-07
LSP-08 | ○ | OFF |  | 0 |  |  | 2P 30A | #21 | U08-A-21 | U08-A-22 | #22 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-09
LSP-10 | ○ | OFF |  |  | 0 |  | 2P 30A | #23 | U08-A-23 | U08-A-24 | #24 | 2P 30A |  |  | 0 |  | ○ | ON | MT-06
RT-08 정류기 | ○ | ON | 0 |  |  |  | 2P 30A | #25 | U08-A-25 |  | #26 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 0.6 | 0.75 | 0
5-DaHall 1-PDU-18 |  | PDU : SEL1 - 5-1 - B9 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 4.6 | 5 | 1.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RT-07 | ○ | ON | 0.82 |  |  |  | 2P 30A | #01 | U08-B-01 | U08-B-02 | #02 | 2P 30A | 0 |  |  |  | ○ | ON | RT-08
RT-09 | ○ | ON |  | 0 |  |  | 2P 30A | #03 | U08-B-03 | U08-B-04 | #04 | 2P 30A |  | 0 |  |  | ○ | ON | RT-10
RT-11 | ○ | ON |  |  | 0 |  | 2P 30A | #05 | U08-B-05 | U08-B-06 | #06 | 2P 30A |  |  | 0 |  | ○ | ON | RT-12
RT-13 | ○ | ON | 0 |  |  |  | 2P 30A | #07 | U08-B-07 | U08-B-08 | #08 | 2P 30A | 0 |  |  |  | ○ | ON | RT-14
RT-15 | ○ | ON |  | 0 |  |  | 2P 30A | #09 | U08-B-09 | U08-B-10 | #10 | 2P 30A |  | 0 |  |  | ○ | ON | RT-16
RT-17 | ○ | ON |  |  | 0 |  | 2P 30A | #11 | U08-B-11 | U08-B-12 | #12 | 2P 30A |  |  | 0 |  | ○ | ON | RT-18
RT-19 | ○ | ON | 0 |  |  |  | 2P 30A | #13 | U08-B-13 | U08-B-14 | #14 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-01
LSP-02 | ○ | OFF |  | 0 |  |  | 2P 30A | #15 | U08-B-15 | U08-B-16 | #16 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-03
LSP-04 | ○ | OFF |  |  | 0 |  | 2P 30A | #17 | U08-B-17 | U08-B-18 | #18 | 2P 30A |  |  | 0 |  | ○ | OFF | LSP-05
LSP-06 | ○ | OFF | 0 |  |  |  | 2P 30A | #19 | U08-B-19 | U08-B-20 | #20 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-07
LSP-08 | ○ | OFF |  | 0 |  |  | 2P 30A | #21 | U08-B-21 | U08-B-22 | #22 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-09
LSP-10 | ○ | OFF |  |  | 0 |  | 2P 30A | #23 | U08-B-23 | U08-B-24 | #24 | 2P 30A |  |  | 0 |  | ○ | ON | 시로코팬
RT-08 정류기 | ○ | ON | 0 |  |  |  | 2P 30A | #25 | U08-B-25 |  | #26 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 0.82 | 0 | 0
5-DaHall 1-PDU-19 |  | PDU : SEL1 - 5-1 - A10 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 35.1 | 38.9 | 22.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-1 | ○ | ON | 0 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 0.64 |  |  |  | ○ | ON | RTX Rack#8, R3-1-1
RTX Rack#2, R1-2-1 | ○ | ON |  | 0 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 0.87 |  |  | ○ | ON | RTX Rack#9, R3-2-1
RTX Rack#3, R1-3-1 | ○ | ON |  |  | 0 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 2.19 |  | ○ | ON | NW/Mgmt Rack, R3-3-1
RTX Rack#4, R2-1-1 | ○ | ON | 0.67 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 1.03 |  |  |  | ○ | ON | A40 Rack#1, R4-1-1
RTX Rack#5, R2-2-1 | ○ | ON |  | 0.68 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 0.5 |  |  | ○ | ON | A40 Rack#2, R4-2-1
RTX Rack#6, R2-3-1 | ○ | ON |  |  | 0 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 0 |  | ○ | ON | NetApp FAS#1, R4-3-1
RTX Rack#7, R2-4-1 | ○ | ON | 0.65 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 1.15 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-1
DGX Rack#1, R5-1-1 | ○ | ON |  | 0 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 1.16 |  |  | ○ | OFF | 예비Rack#1, R6-1-1
DGX Rack#2, R5-2-1 | ○ | ON |  |  | 1.83 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 1.15 |  | ○ | OFF | 예비Rack#2, R6-2-1
DGX Rack#3, R5-3-1 | ○ | ON | 1.12 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 1.16 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-1
| X | OFF |  | 0 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 0.84 |  |  | ○ | OFF | 예비Rack#4, R6-4-1
| X | OFF |  |  | 0 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 6.42 | 4.05 | 5.17
5-DaHall 1-PDU-20 |  | PDU : SEL1 - 5-1 - B10 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 28.1 | 32.6 | 23.1 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-2 | ○ | ON | 0 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 0.63 |  |  |  | ○ | ON | RTX Rack#8, R3-1-2
RTX Rack#2, R1-2-2 | ○ | ON |  | 0 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 0.92 |  |  | ○ | ON | RTX Rack#9, R3-2-2
RTX Rack#3, R1-3-2 | ○ | ON |  |  | 0 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 1.36 |  | ○ | ON | NW/Mgmt Rack, R3-3-2
RTX Rack#4, R2-1-2 | ○ | ON | 0.68 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 1.19 |  |  |  | ○ | ON | A40 Rack#1, R4-1-2
RTX Rack#5, R2-2-2 | ○ | ON |  | 0.59 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 0.63 |  |  | ○ | ON | A40 Rack#2, R4-2-2
RTX Rack#6, R2-3-2 | ○ | ON |  |  | 0 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 0 |  | ○ | ON | NetApp FAS#1, R4-3-2
RTX Rack#7, R2-4-2 | ○ | ON | 0.69 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 1.23 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-2
DGX Rack#1, R5-1-2 | ○ | ON |  | 0 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 1.03 |  |  | ○ | OFF | 예비Rack#1, R6-1-2
DGX Rack#2, R5-2-2 | ○ | ON |  |  | 2.5 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 1 |  | ○ | OFF | 예비Rack#2, R6-2-2
DGX Rack#3, R5-3-2 | ○ | ON | 1.07 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 0.86 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-2
| X | OFF |  | 0 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 0.59 |  |  | ○ | OFF | 예비Rack#4, R6-4-2
| X | OFF |  |  | 0 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 6.35 | 3.76 | 4.86
5-DaHall 1-PDU-21 |  | PDU : SEL1 - 5-1 - A11 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 41.9 | 33.6 | 29.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-3 | ○ | ON | 0 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 0.65 |  |  |  | ○ | ON | RTX Rack#8, R3-1-3
RTX Rack#2, R1-2-3 | ○ | ON |  | 0 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 0.66 |  |  | ○ | ON | RTX Rack#9, R3-2-3
RTX Rack#3, R1-3-3 | ○ | ON |  |  | 0 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 2.15 |  | ○ | ON | NW/Mgmt Rack, R3-3-3
RTX Rack#4, R2-1-3 | ○ | ON | 0.66 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 1.52 |  |  |  | ○ | ON | A40 Rack#1, R4-1-3
RTX Rack#5, R2-2-3 | ○ | ON |  | 0.66 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 1.1 |  |  | ○ | ON | A40 Rack#2, R4-2-3
RTX Rack#6, R2-3-3 | ○ | ON |  |  | 0 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 0 |  | ○ | ON | NetApp FAS#1, R4-3-3
RTX Rack#7, R2-4-3 | ○ | ON | 0.65 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 2.02 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-3
DGX Rack#1, R5-1-3 | ○ | ON |  | 0.85 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 0.5 |  |  | ○ | OFF | 예비Rack#1, R6-1-3
DGX Rack#2, R5-2-3 | ○ | ON |  |  | 0.86 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 1.19 |  | ○ | OFF | 예비Rack#2, R6-2-3
DGX Rack#3, R5-3-3 | ○ | ON | 1.76 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 0.86 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-3
| X | OFF |  | 0 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 0.85 |  |  | ○ | OFF | 예비Rack#4, R6-4-3
| X | OFF |  |  | 0 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 8.12 | 4.62 | 4.2
5-DaHall 1-PDU-22 |  | PDU : SEL1 - 5-1 - B11 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 37 | 27.7 | 24 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-4 | ○ | ON | 0 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 0.63 |  |  |  | ○ | ON | RTX Rack#8, R3-1-4
RTX Rack#2, R1-2-4 | ○ | ON |  | 0 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 0.62 |  |  | ○ | ON | RTX Rack#9, R3-2-4
RTX Rack#3, R1-3-4 | ○ | ON |  |  | 0 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 1.09 |  | ○ | ON | NW/Mgmt Rack, R3-3-4
RTX Rack#4, R2-1-4 | ○ | ON | 0.64 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 1.46 |  |  |  | ○ | ON | A40 Rack#1, R4-1-4
RTX Rack#5, R2-2-4 | ○ | ON |  | 0.58 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 1.14 |  |  | ○ | ON | A40 Rack#2, R4-2-4
RTX Rack#6, R2-3-4 | ○ | ON |  |  | 0 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 0 |  | ○ | ON | NetApp FAS#1, R4-3-4
RTX Rack#7, R2-4-4 | ○ | ON | 0.62 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 1.88 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-4
DGX Rack#1, R5-1-4 | ○ | ON |  | 0.85 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 0.57 |  |  | ○ | OFF | 예비Rack#1, R6-1-4
DGX Rack#2, R5-2-4 | ○ | ON |  |  | 0.84 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 0.91 |  | ○ | OFF | 예비Rack#2, R6-2-4
DGX Rack#3, R5-3-4 | ○ | ON | 2.27 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 0.59 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-4
| X | OFF |  | 0 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 0.59 |  |  | ○ | OFF | 예비Rack#4, R6-4-4
| X | OFF |  |  | 0 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 8.09 | 4.35 | 2.84
5층 TR룸
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
PDU-8 (A) | O | ON | 5.6 | 7.2 | 2.3 | 3.8 | 3P 200A | #08 | Singtel | Singtel | #08 | 3P 200A | 4.6 | 5 | 1.5 | 2.7 | O | ON | PDU-8 (B)
텔스트라 정류기 A1 | O | ON | 8.4 | 19.2 | 9.2 | 10.7 | 3P 30A | #03 | C2C | C2C | #04 | 3P 30A | 8.6 | 8.4 | 9 | 2.1 | O | ON | 텔스트라 정류기 A2
텔스트라 정류기 B1 | O | ON | 11.2 | 8 | 11.6 | 4 | 3P 30A | #05 | C2C | C2C | #06 | 3P 30A | 11.7 | 11.5 | 11.5 | 1.8 | O | ON | 텔스트라 정류기 B2
|  |  | 사용량 | 배분
| IDC |  | 303.08 | 57.34% | [7 empty] | 5-1-A1 | 25.65 | 27.12 | 21.47
| 텔스트라 |  | 27.44 | 5.192% | [7 empty] | 5-1-B1 | 24.95 | 25.61 | 19.7
| 텔스트라 정류기 |  | 128.3 | 24.27% | [7 empty] | 5-1-A2 | 25.56 | 14.86 | 14.04
| singtel PDU-8-A |  | 1.35 | 0.2554% | [7 empty] | 6-1-B2 | 22.69 | 14.13 | 13.87
| singtel PDU-8-B |  | 0.82 | 0.1551% | =>합계 | 0.4106% | [5 empty] | 5-1-A3 | 0 | 0 | 0
| singtel (기타) |  | 4.72 | 0.893% | [7 empty] | 5-1-B3 | 0 | 0 | 0
| LG CNS |  | 62.83 | 11.89% | [7 empty] | 5-1-A4 | 8.04 | 0.4 | 0
함계 | IDC |  | 528.54 | 100% | [7 empty] | 5-1-B4 | 1.16 | 0 | 0
[12 empty] | 5-1-A5 | 0 | 0 | 0
[12 empty] | 5-1-B5 | 0 | 0 | 0
[12 empty] | 5-1-A6 | 0 | 0 | 3.03
[12 empty] | 5-1-B6 | 3.48 | 11.03 | 6.16
[12 empty] | 5-1-A7 | 3.91 | 0 | 5.84
| C2C | [10 empty] | 5-1-B7 | 0 | 0 | 2.45
[12 empty] | 5-1-A8 | 6.62 | 1.25 | 10.52
[12 empty] | 5-1-B8 | 9.49 | 5.39 | 6.82
[12 empty] | 5-1-A9 | 0.6 | 0.75 | 0 | 1.35
[12 empty] | 5-1-B9 | 0.82 | 0 | 0 | 0.82
[12 empty] | 5-1-A10 | 6.42 | 4.05 | 5.17
|  |  |  | 복도 | [7 empty] | 5-1-B10 | 6.35 | 3.76 | 4.86
[12 empty] | 5-1-A11 | 8.12 | 4.62 | 4.2
[12 empty] | 5-1-B11 | 8.09 | 4.35 | 2.84 |  | 62.83
|  |  |  | ▼ | [8 empty] | 161.95 | 117.32 | 120.97 | 400.24
128.3
528.54
[5 empty] | Singtel-1 |  | Singtel-2 |  | Pacnet
Note on A226: 이현상: 계약전류 10A/랙 ? 초과시 AM연락 필요! (임영호팀장/장우창M/장태영M)
Note on A274: 이현상: 계약전류 10A/랙 ? 초과시 AM연락 필요 (임영호팀장/장우창M/장태영M)

## 5F_current (hidden)
5F | A(전류)
5-DaHall 1-PDU-01-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-01-02 | [branch#055] [A] current
5-DaHall 1-PDU-01-03 | [branch#002] [A] current
5-DaHall 1-PDU-01-04 | [branch#056] [A] current
5-DaHall 1-PDU-01-05 | [branch#003] [A] current
5-DaHall 1-PDU-01-06 | [branch#057] [A] current
5-DaHall 1-PDU-01-07 | [branch#004] [A] current
5-DaHall 1-PDU-01-08 | [branch#058] [A] current
5-DaHall 1-PDU-01-09 | [branch#005] [A] current
5-DaHall 1-PDU-01-10 | [branch#059] [A] current
5-DaHall 1-PDU-01-11 | [branch#006] [A] current
5-DaHall 1-PDU-01-12 | [branch#060] [A] current
5-DaHall 1-PDU-01-13 | [branch#007] [A] current
5-DaHall 1-PDU-01-14 | [branch#061] [A] current
5-DaHall 1-PDU-01-15 | [branch#008] [A] current
5-DaHall 1-PDU-01-16 | [branch#062] [A] current
5-DaHall 1-PDU-01-17 | [branch#009] [A] current
5-DaHall 1-PDU-01-18 | [branch#063] [A] current
5-DaHall 1-PDU-01-19 | [branch#010] [A] current
5-DaHall 1-PDU-01-20 | [branch#064] [A] current
5-DaHall 1-PDU-01-21 | [branch#011] [A] current
5-DaHall 1-PDU-01-22 | [branch#065] [A] current
5-DaHall 1-PDU-01-23 | [branch#012] [A] current
5-DaHall 1-PDU-01-24 | [branch#066] [A] current
5-DaHall 1-PDU-01-25 | [branch#013] [A] current
5-DaHall 1-PDU-01-26 | [branch#067] [A] current
5-DaHall 1-PDU-01-27 | [branch#014] [A] current
5-DaHall 1-PDU-01-28 | [branch#068] [A] current
5-DaHall 1-PDU-01-29 | [branch#015] [A] current
5-DaHall 1-PDU-01-30 | [branch#069] [A] current
5-DaHall 1-PDU-01-31 | [branch#016] [A] current
5-DaHall 1-PDU-01-32 | [branch#070] [A] current
5-DaHall 1-PDU-01-33 | [branch#017] [A] current
5-DaHall 1-PDU-01-34 | [branch#071] [A] current
5-DaHall 1-PDU-01-35 | [branch#018] [A] current
5-DaHall 1-PDU-01-36 | [branch#072] [A] current
5-DaHall 1-PDU-01-37 | [branch#019] [A] current
5-DaHall 1-PDU-01-38 | [branch#073] [A] current
5-DaHall 1-PDU-01-39 | [branch#020] [A] current
5-DaHall 1-PDU-01-40 | [branch#074] [A] current
5-DaHall 1-PDU-01-41 | [branch#021] [A] current
5-DaHall 1-PDU-01-42 | [branch#075] [A] current
5-DaHall 1-PDU-01-43 | [branch#022] [A] current
5-DaHall 1-PDU-01-44 | [branch#076] [A] current
5-DaHall 1-PDU-01-45 | [branch#023] [A] current
5-DaHall 1-PDU-01-46 | [branch#077] [A] current
5-DaHall 1-PDU-01-47 | [branch#024] [A] current
5-DaHall 1-PDU-01-48 | [branch#078] [A] current
5-DaHall 1-PDU-01-49 | [branch#025] [A] current
5-DaHall 1-PDU-01-50 | [branch#079] [A] current
5-DaHall 1-PDU-01-51 | [branch#026] [A] current
5-DaHall 1-PDU-01-52 | [branch#080] [A] current
5-DaHall 1-PDU-02-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-02-02 | [branch#055] [A] current
5-DaHall 1-PDU-02-03 | [branch#002] [A] current
5-DaHall 1-PDU-02-04 | [branch#056] [A] current
5-DaHall 1-PDU-02-05 | [branch#003] [A] current
5-DaHall 1-PDU-02-06 | [branch#057] [A] current
5-DaHall 1-PDU-02-07 | [branch#004] [A] current
5-DaHall 1-PDU-02-08 | [branch#058] [A] current
5-DaHall 1-PDU-02-09 | [branch#005] [A] current
5-DaHall 1-PDU-02-10 | [branch#059] [A] current
5-DaHall 1-PDU-02-11 | [branch#006] [A] current
5-DaHall 1-PDU-02-12 | [branch#060] [A] current
5-DaHall 1-PDU-02-13 | [branch#007] [A] current
5-DaHall 1-PDU-02-14 | [branch#061] [A] current
5-DaHall 1-PDU-02-15 | [branch#008] [A] current
5-DaHall 1-PDU-02-16 | [branch#062] [A] current
5-DaHall 1-PDU-02-17 | [branch#009] [A] current
5-DaHall 1-PDU-02-18 | [branch#063] [A] current
5-DaHall 1-PDU-02-19 | [branch#010] [A] current
5-DaHall 1-PDU-02-20 | [branch#064] [A] current
5-DaHall 1-PDU-02-21 | [branch#011] [A] current
5-DaHall 1-PDU-02-22 | [branch#065] [A] current
5-DaHall 1-PDU-02-23 | [branch#012] [A] current
5-DaHall 1-PDU-02-24 | [branch#066] [A] current
5-DaHall 1-PDU-02-25 | [branch#013] [A] current
5-DaHall 1-PDU-02-26 | [branch#067] [A] current
5-DaHall 1-PDU-02-27 | [branch#014] [A] current
5-DaHall 1-PDU-02-28 | [branch#068] [A] current
5-DaHall 1-PDU-02-29 | [branch#015] [A] current
5-DaHall 1-PDU-02-30 | [branch#069] [A] current
5-DaHall 1-PDU-02-31 | [branch#016] [A] current
5-DaHall 1-PDU-02-32 | [branch#070] [A] current
5-DaHall 1-PDU-02-33 | [branch#017] [A] current
5-DaHall 1-PDU-02-34 | [branch#071] [A] current
5-DaHall 1-PDU-02-35 | [branch#018] [A] current
5-DaHall 1-PDU-02-36 | [branch#072] [A] current
5-DaHall 1-PDU-02-37 | [branch#019] [A] current
5-DaHall 1-PDU-02-38 | [branch#073] [A] current
5-DaHall 1-PDU-02-39 | [branch#020] [A] current
5-DaHall 1-PDU-02-40 | [branch#074] [A] current
5-DaHall 1-PDU-02-41 | [branch#021] [A] current
5-DaHall 1-PDU-02-42 | [branch#075] [A] current
5-DaHall 1-PDU-02-43 | [branch#022] [A] current
5-DaHall 1-PDU-02-44 | [branch#076] [A] current
5-DaHall 1-PDU-02-45 | [branch#023] [A] current
5-DaHall 1-PDU-02-46 | [branch#077] [A] current
5-DaHall 1-PDU-02-47 | [branch#024] [A] current
5-DaHall 1-PDU-02-48 | [branch#078] [A] current
5-DaHall 1-PDU-02-49 | [branch#025] [A] current
5-DaHall 1-PDU-02-50 | [branch#079] [A] current
5-DaHall 1-PDU-02-51 | [branch#026] [A] current
5-DaHall 1-PDU-02-52 | [branch#080] [A] current
5-DaHall 1-PDU-03-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-03-02 | [branch#055] [A] current
5-DaHall 1-PDU-03-03 | [branch#002] [A] current
5-DaHall 1-PDU-03-04 | [branch#056] [A] current
5-DaHall 1-PDU-03-05 | [branch#003] [A] current
5-DaHall 1-PDU-03-06 | [branch#057] [A] current
5-DaHall 1-PDU-03-07 | [branch#004] [A] current
5-DaHall 1-PDU-03-08 | [branch#058] [A] current
5-DaHall 1-PDU-03-09 | [branch#005] [A] current
5-DaHall 1-PDU-03-10 | [branch#059] [A] current
5-DaHall 1-PDU-03-11 | [branch#006] [A] current
5-DaHall 1-PDU-03-12 | [branch#060] [A] current
5-DaHall 1-PDU-03-13 | [branch#007] [A] current
5-DaHall 1-PDU-03-14 | [branch#061] [A] current
5-DaHall 1-PDU-03-15 | [branch#008] [A] current
5-DaHall 1-PDU-03-16 | [branch#062] [A] current
5-DaHall 1-PDU-03-17 | [branch#009] [A] current
5-DaHall 1-PDU-03-18 | [branch#063] [A] current
5-DaHall 1-PDU-03-19 | [branch#010] [A] current
5-DaHall 1-PDU-03-20 | [branch#064] [A] current
5-DaHall 1-PDU-03-21 | [branch#011] [A] current
5-DaHall 1-PDU-03-22 | [branch#065] [A] current
5-DaHall 1-PDU-03-23 | [branch#012] [A] current
5-DaHall 1-PDU-03-24 | [branch#066] [A] current
5-DaHall 1-PDU-03-25 | [branch#013] [A] current
5-DaHall 1-PDU-03-26 | [branch#067] [A] current
5-DaHall 1-PDU-03-27 | [branch#014] [A] current
5-DaHall 1-PDU-03-28 | [branch#068] [A] current
5-DaHall 1-PDU-03-29 | [branch#015] [A] current
5-DaHall 1-PDU-03-30 | [branch#069] [A] current
5-DaHall 1-PDU-03-31 | [branch#016] [A] current
5-DaHall 1-PDU-03-32 | [branch#070] [A] current
5-DaHall 1-PDU-03-33 | [branch#017] [A] current
5-DaHall 1-PDU-03-34 | [branch#071] [A] current
5-DaHall 1-PDU-03-35 | [branch#018] [A] current
5-DaHall 1-PDU-03-36 | [branch#072] [A] current
5-DaHall 1-PDU-03-37 | [branch#019] [A] current
5-DaHall 1-PDU-03-38 | [branch#073] [A] current
5-DaHall 1-PDU-03-39 | [branch#020] [A] current
5-DaHall 1-PDU-03-40 | [branch#074] [A] current
5-DaHall 1-PDU-03-41 | [branch#021] [A] current
5-DaHall 1-PDU-03-42 | [branch#075] [A] current
5-DaHall 1-PDU-03-43 | [branch#022] [A] current
5-DaHall 1-PDU-03-44 | [branch#076] [A] current
5-DaHall 1-PDU-03-45 | [branch#023] [A] current
5-DaHall 1-PDU-03-46 | [branch#077] [A] current
5-DaHall 1-PDU-03-47 | [branch#024] [A] current
5-DaHall 1-PDU-03-48 | [branch#078] [A] current
5-DaHall 1-PDU-03-49 | [branch#025] [A] current
5-DaHall 1-PDU-03-50 | [branch#079] [A] current
5-DaHall 1-PDU-03-51 | [branch#026] [A] current
5-DaHall 1-PDU-03-52 | [branch#080] [A] current
5-DaHall 1-PDU-04-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-04-02 | [branch#055] [A] current
5-DaHall 1-PDU-04-03 | [branch#002] [A] current
5-DaHall 1-PDU-04-04 | [branch#056] [A] current
5-DaHall 1-PDU-04-05 | [branch#003] [A] current
5-DaHall 1-PDU-04-06 | [branch#057] [A] current
5-DaHall 1-PDU-04-07 | [branch#004] [A] current
5-DaHall 1-PDU-04-08 | [branch#058] [A] current
5-DaHall 1-PDU-04-09 | [branch#005] [A] current
5-DaHall 1-PDU-04-10 | [branch#059] [A] current
5-DaHall 1-PDU-04-11 | [branch#006] [A] current
5-DaHall 1-PDU-04-12 | [branch#060] [A] current
5-DaHall 1-PDU-04-13 | [branch#007] [A] current
5-DaHall 1-PDU-04-14 | [branch#061] [A] current
5-DaHall 1-PDU-04-15 | [branch#008] [A] current
5-DaHall 1-PDU-04-16 | [branch#062] [A] current
5-DaHall 1-PDU-04-17 | [branch#009] [A] current
5-DaHall 1-PDU-04-18 | [branch#063] [A] current
5-DaHall 1-PDU-04-19 | [branch#010] [A] current
5-DaHall 1-PDU-04-20 | [branch#064] [A] current
5-DaHall 1-PDU-04-21 | [branch#011] [A] current
5-DaHall 1-PDU-04-22 | [branch#065] [A] current
5-DaHall 1-PDU-04-23 | [branch#012] [A] current
5-DaHall 1-PDU-04-24 | [branch#066] [A] current
5-DaHall 1-PDU-04-25 | [branch#013] [A] current
5-DaHall 1-PDU-04-26 | [branch#067] [A] current
5-DaHall 1-PDU-04-27 | [branch#014] [A] current
5-DaHall 1-PDU-04-28 | [branch#068] [A] current
5-DaHall 1-PDU-04-29 | [branch#015] [A] current
5-DaHall 1-PDU-04-30 | [branch#069] [A] current
5-DaHall 1-PDU-04-31 | [branch#016] [A] current
5-DaHall 1-PDU-04-32 | [branch#070] [A] current
5-DaHall 1-PDU-04-33 | [branch#017] [A] current
5-DaHall 1-PDU-04-34 | [branch#071] [A] current
5-DaHall 1-PDU-04-35 | [branch#018] [A] current
5-DaHall 1-PDU-04-36 | [branch#072] [A] current
5-DaHall 1-PDU-04-37 | [branch#019] [A] current
5-DaHall 1-PDU-04-38 | [branch#073] [A] current
5-DaHall 1-PDU-04-39 | [branch#020] [A] current
5-DaHall 1-PDU-04-40 | [branch#074] [A] current
5-DaHall 1-PDU-04-41 | [branch#021] [A] current
5-DaHall 1-PDU-04-42 | [branch#075] [A] current
5-DaHall 1-PDU-04-43 | [branch#022] [A] current
5-DaHall 1-PDU-04-44 | [branch#076] [A] current
5-DaHall 1-PDU-04-45 | [branch#023] [A] current
5-DaHall 1-PDU-04-46 | [branch#077] [A] current
5-DaHall 1-PDU-04-47 | [branch#024] [A] current
5-DaHall 1-PDU-04-48 | [branch#078] [A] current
5-DaHall 1-PDU-04-49 | [branch#025] [A] current
5-DaHall 1-PDU-04-50 | [branch#079] [A] current
5-DaHall 1-PDU-04-51 | [branch#026] [A] current
5-DaHall 1-PDU-04-52 | [branch#080] [A] current
5-DaHall 1-PDU-05-01 | [branch#001] [A] current
5-DaHall 1-PDU-05-02 | [branch#002] [A] current
5-DaHall 1-PDU-05-03 | [branch#003] [A] current
5-DaHall 1-PDU-05-04 | [branch#004] [A] current
5-DaHall 1-PDU-05-05 | [branch#005] [A] current
5-DaHall 1-PDU-05-06 | [branch#006] [A] current
5-DaHall 1-PDU-05-07 | [branch#007] [A] current
5-DaHall 1-PDU-05-08 | [branch#008] [A] current
5-DaHall 1-PDU-05-09 | [branch#009] [A] current
5-DaHall 1-PDU-05-10 | [branch#010] [A] current
5-DaHall 1-PDU-05-11 | [branch#011] [A] current
5-DaHall 1-PDU-05-12 | [branch#012] [A] current
5-DaHall 1-PDU-05-13 | [branch#013] [A] current
5-DaHall 1-PDU-05-14 | [branch#014] [A] current
5-DaHall 1-PDU-05-15 | [branch#015] [A] current
5-DaHall 1-PDU-05-16 | [branch#016] [A] current
5-DaHall 1-PDU-05-17 | [branch#017] [A] current
5-DaHall 1-PDU-05-18 | [branch#018] [A] current
5-DaHall 1-PDU-05-19 | [branch#019] [A] current
5-DaHall 1-PDU-05-20 | [branch#020] [A] current
5-DaHall 1-PDU-05-21 | [branch#021] [A] current
5-DaHall 1-PDU-05-22 | [branch#022] [A] current
5-DaHall 1-PDU-05-23 | [branch#023] [A] current
5-DaHall 1-PDU-05-24 | [branch#024] [A] current
5-DaHall 1-PDU-05-25 | [branch#025] [A] current
5-DaHall 1-PDU-05-26 | [branch#026] [A] current
5-DaHall 1-PDU-05-27 | [branch#027] [A] current
5-DaHall 1-PDU-05-28 | [branch#028] [A] current
5-DaHall 1-PDU-05-29 | [branch#029] [A] current
5-DaHall 1-PDU-05-30 | [branch#030] [A] current
5-DaHall 1-PDU-05-31 | [branch#031] [A] current
5-DaHall 1-PDU-05-32 | [branch#032] [A] current
5-DaHall 1-PDU-05-33 | [branch#033] [A] current
5-DaHall 1-PDU-05-34 | [branch#034] [A] current
5-DaHall 1-PDU-05-35 | [branch#035] [A] current
5-DaHall 1-PDU-05-36 | [branch#036] [A] current
5-DaHall 1-PDU-05-37 | [branch#037] [A] current
5-DaHall 1-PDU-05-38 | [branch#038] [A] current
5-DaHall 1-PDU-05-39 | [branch#039] [A] current
5-DaHall 1-PDU-05-40 | [branch#040] [A] current
5-DaHall 1-PDU-05-41 | [branch#041] [A] current
5-DaHall 1-PDU-05-42 | [branch#042] [A] current
5-DaHall 1-PDU-05-43 | [branch#043] [A] current
5-DaHall 1-PDU-05-44 | [branch#044] [A] current
5-DaHall 1-PDU-05-45 | [branch#045] [A] current
5-DaHall 1-PDU-05-46 | [branch#046] [A] current
5-DaHall 1-PDU-05-47 | [branch#047] [A] current
5-DaHall 1-PDU-05-48 | [branch#048] [A] current
5-DaHall 1-PDU-05-49 | [branch#049] [A] current
5-DaHall 1-PDU-05-50 | [branch#050] [A] current
5-DaHall 1-PDU-05-51 | [branch#051] [A] current
5-DaHall 1-PDU-05-52 | [branch#052] [A] current
5-DaHall 1-PDU-05-53 | [branch#053] [A] current
5-DaHall 1-PDU-05-54 | [branch#054] [A] current
5-DaHall 1-PDU-06-01 | [branch#001] [A] current
5-DaHall 1-PDU-06-02 | [branch#002] [A] current
5-DaHall 1-PDU-06-03 | [branch#003] [A] current
5-DaHall 1-PDU-06-04 | [branch#004] [A] current
5-DaHall 1-PDU-06-05 | [branch#005] [A] current
5-DaHall 1-PDU-06-06 | [branch#006] [A] current
5-DaHall 1-PDU-06-07 | [branch#007] [A] current
5-DaHall 1-PDU-06-08 | [branch#008] [A] current
5-DaHall 1-PDU-06-09 | [branch#009] [A] current
5-DaHall 1-PDU-06-10 | [branch#010] [A] current
5-DaHall 1-PDU-06-11 | [branch#011] [A] current
5-DaHall 1-PDU-06-12 | [branch#012] [A] current
5-DaHall 1-PDU-06-13 | [branch#013] [A] current
5-DaHall 1-PDU-06-14 | [branch#014] [A] current
5-DaHall 1-PDU-06-15 | [branch#015] [A] current
5-DaHall 1-PDU-06-16 | [branch#016] [A] current
5-DaHall 1-PDU-06-17 | [branch#017] [A] current
5-DaHall 1-PDU-06-18 | [branch#018] [A] current
5-DaHall 1-PDU-06-19 | [branch#019] [A] current
5-DaHall 1-PDU-06-20 | [branch#020] [A] current
5-DaHall 1-PDU-06-21 | [branch#021] [A] current
5-DaHall 1-PDU-06-22 | [branch#022] [A] current
5-DaHall 1-PDU-06-23 | [branch#023] [A] current
5-DaHall 1-PDU-06-24 | [branch#024] [A] current
5-DaHall 1-PDU-06-25 | [branch#025] [A] current
5-DaHall 1-PDU-06-26 | [branch#026] [A] current
5-DaHall 1-PDU-06-27 | [branch#027] [A] current
5-DaHall 1-PDU-06-28 | [branch#028] [A] current
5-DaHall 1-PDU-06-29 | [branch#029] [A] current
5-DaHall 1-PDU-06-30 | [branch#030] [A] current
5-DaHall 1-PDU-06-31 | [branch#031] [A] current
5-DaHall 1-PDU-06-32 | [branch#032] [A] current
5-DaHall 1-PDU-06-33 | [branch#033] [A] current
5-DaHall 1-PDU-06-34 | [branch#034] [A] current
5-DaHall 1-PDU-06-35 | [branch#035] [A] current
5-DaHall 1-PDU-06-36 | [branch#036] [A] current
5-DaHall 1-PDU-06-37 | [branch#037] [A] current
5-DaHall 1-PDU-06-38 | [branch#038] [A] current
5-DaHall 1-PDU-06-39 | [branch#039] [A] current
5-DaHall 1-PDU-06-40 | [branch#040] [A] current
5-DaHall 1-PDU-06-41 | [branch#041] [A] current
5-DaHall 1-PDU-06-42 | [branch#042] [A] current
5-DaHall 1-PDU-06-43 | [branch#043] [A] current
5-DaHall 1-PDU-06-44 | [branch#044] [A] current
5-DaHall 1-PDU-06-45 | [branch#045] [A] current
5-DaHall 1-PDU-06-46 | [branch#046] [A] current
5-DaHall 1-PDU-06-47 | [branch#047] [A] current
5-DaHall 1-PDU-06-48 | [branch#048] [A] current
5-DaHall 1-PDU-06-49 | [branch#049] [A] current
5-DaHall 1-PDU-06-50 | [branch#050] [A] current
5-DaHall 1-PDU-06-51 | [branch#051] [A] current
5-DaHall 1-PDU-06-52 | [branch#052] [A] current
5-DaHall 1-PDU-06-53 | [branch#053] [A] current
5-DaHall 1-PDU-06-54 | [branch#054] [A] current
5-DaHall 1-PDU-07-01 | [branch#001] [A] current
5-DaHall 1-PDU-07-02 | [branch#002] [A] current
5-DaHall 1-PDU-07-03 | [branch#003] [A] current
5-DaHall 1-PDU-07-04 | [branch#004] [A] current
5-DaHall 1-PDU-07-05 | [branch#005] [A] current
5-DaHall 1-PDU-07-06 | [branch#006] [A] current
5-DaHall 1-PDU-07-07 | [branch#007] [A] current
5-DaHall 1-PDU-07-08 | [branch#008] [A] current
5-DaHall 1-PDU-07-09 | [branch#009] [A] current
5-DaHall 1-PDU-07-10 | [branch#010] [A] current
5-DaHall 1-PDU-07-11 | [branch#011] [A] current
5-DaHall 1-PDU-07-12 | [branch#012] [A] current
5-DaHall 1-PDU-07-13 | [branch#013] [A] current
5-DaHall 1-PDU-07-14 | [branch#014] [A] current
5-DaHall 1-PDU-07-15 | [branch#015] [A] current
5-DaHall 1-PDU-07-16 | [branch#016] [A] current
5-DaHall 1-PDU-07-17 | [branch#017] [A] current
5-DaHall 1-PDU-07-18 | [branch#018] [A] current
5-DaHall 1-PDU-07-19 | [branch#019] [A] current
5-DaHall 1-PDU-07-20 | [branch#020] [A] current
5-DaHall 1-PDU-07-21 | [branch#021] [A] current
5-DaHall 1-PDU-07-22 | [branch#022] [A] current
5-DaHall 1-PDU-07-23 | [branch#023] [A] current
5-DaHall 1-PDU-07-24 | [branch#024] [A] current
5-DaHall 1-PDU-07-25 | [branch#025] [A] current
5-DaHall 1-PDU-07-26 | [branch#026] [A] current
5-DaHall 1-PDU-07-27 | [branch#027] [A] current
5-DaHall 1-PDU-07-28 | [branch#028] [A] current
5-DaHall 1-PDU-07-29 | [branch#029] [A] current
5-DaHall 1-PDU-07-30 | [branch#030] [A] current
5-DaHall 1-PDU-07-31 | [branch#031] [A] current
5-DaHall 1-PDU-07-32 | [branch#032] [A] current
5-DaHall 1-PDU-07-33 | [branch#033] [A] current
5-DaHall 1-PDU-07-34 | [branch#034] [A] current
5-DaHall 1-PDU-07-35 | [branch#035] [A] current
5-DaHall 1-PDU-07-36 | [branch#036] [A] current
5-DaHall 1-PDU-08-01 | [branch#001] [A] current
5-DaHall 1-PDU-08-02 | [branch#002] [A] current
5-DaHall 1-PDU-08-03 | [branch#003] [A] current
5-DaHall 1-PDU-08-04 | [branch#004] [A] current
5-DaHall 1-PDU-08-05 | [branch#005] [A] current
5-DaHall 1-PDU-08-06 | [branch#006] [A] current
5-DaHall 1-PDU-08-07 | [branch#007] [A] current
5-DaHall 1-PDU-08-08 | [branch#008] [A] current
5-DaHall 1-PDU-08-09 | [branch#009] [A] current
5-DaHall 1-PDU-08-10 | [branch#010] [A] current
5-DaHall 1-PDU-08-11 | [branch#011] [A] current
5-DaHall 1-PDU-08-12 | [branch#012] [A] current
5-DaHall 1-PDU-08-13 | [branch#013] [A] current
5-DaHall 1-PDU-08-14 | [branch#014] [A] current
5-DaHall 1-PDU-08-15 | [branch#015] [A] current
5-DaHall 1-PDU-08-16 | [branch#016] [A] current
5-DaHall 1-PDU-08-17 | [branch#017] [A] current
5-DaHall 1-PDU-08-18 | [branch#018] [A] current
5-DaHall 1-PDU-08-19 | [branch#019] [A] current
5-DaHall 1-PDU-08-20 | [branch#020] [A] current
5-DaHall 1-PDU-08-21 | [branch#021] [A] current
5-DaHall 1-PDU-08-22 | [branch#022] [A] current
5-DaHall 1-PDU-08-23 | [branch#023] [A] current
5-DaHall 1-PDU-08-24 | [branch#024] [A] current
5-DaHall 1-PDU-08-25 | [branch#025] [A] current
5-DaHall 1-PDU-08-26 | [branch#026] [A] current
5-DaHall 1-PDU-08-27 | [branch#027] [A] current
5-DaHall 1-PDU-08-28 | [branch#028] [A] current
5-DaHall 1-PDU-08-29 | [branch#029] [A] current
5-DaHall 1-PDU-08-30 | [branch#030] [A] current
5-DaHall 1-PDU-08-31 | [branch#031] [A] current
5-DaHall 1-PDU-08-32 | [branch#032] [A] current
5-DaHall 1-PDU-08-33 | [branch#033] [A] current
5-DaHall 1-PDU-08-34 | [branch#034] [A] current
5-DaHall 1-PDU-08-35 | [branch#035] [A] current
5-DaHall 1-PDU-08-36 | [branch#036] [A] current
5-DaHall 1-PDU-09-01 | [branch#001] [A] current
5-DaHall 1-PDU-09-02 | [branch#002] [A] current
5-DaHall 1-PDU-09-03 | [branch#003] [A] current
5-DaHall 1-PDU-09-04 | [branch#004] [A] current
5-DaHall 1-PDU-09-05 | [branch#005] [A] current
5-DaHall 1-PDU-09-06 | [branch#006] [A] current
5-DaHall 1-PDU-09-07 | [branch#007] [A] current
5-DaHall 1-PDU-09-08 | [branch#008] [A] current
5-DaHall 1-PDU-09-09 | [branch#009] [A] current
5-DaHall 1-PDU-09-10 | [branch#010] [A] current
5-DaHall 1-PDU-09-11 | [branch#011] [A] current
5-DaHall 1-PDU-09-12 | [branch#012] [A] current
5-DaHall 1-PDU-09-13 | [branch#013] [A] current
5-DaHall 1-PDU-09-14 | [branch#014] [A] current
5-DaHall 1-PDU-09-15 | [branch#015] [A] current
5-DaHall 1-PDU-09-16 | [branch#016] [A] current
5-DaHall 1-PDU-09-17 | [branch#017] [A] current
5-DaHall 1-PDU-09-18 | [branch#018] [A] current
5-DaHall 1-PDU-09-19 | [branch#019] [A] current
5-DaHall 1-PDU-09-20 | [branch#020] [A] current
5-DaHall 1-PDU-09-21 | [branch#021] [A] current
5-DaHall 1-PDU-09-22 | [branch#022] [A] current
5-DaHall 1-PDU-09-23 | [branch#023] [A] current
5-DaHall 1-PDU-09-24 | [branch#024] [A] current
5-DaHall 1-PDU-09-25 | [branch#025] [A] current
5-DaHall 1-PDU-09-26 | [branch#026] [A] current
5-DaHall 1-PDU-09-27 | [branch#027] [A] current
5-DaHall 1-PDU-09-28 | [branch#028] [A] current
5-DaHall 1-PDU-09-29 | [branch#029] [A] current
5-DaHall 1-PDU-09-30 | [branch#030] [A] current
5-DaHall 1-PDU-09-31 | [branch#031] [A] current
5-DaHall 1-PDU-09-32 | [branch#032] [A] current
5-DaHall 1-PDU-09-33 | [branch#033] [A] current
5-DaHall 1-PDU-09-34 | [branch#034] [A] current
5-DaHall 1-PDU-09-35 | [branch#035] [A] current
5-DaHall 1-PDU-09-36 | [branch#036] [A] current
5-DaHall 1-PDU-09-37 | [branch#037] [A] current
5-DaHall 1-PDU-09-38 | [branch#038] [A] current
5-DaHall 1-PDU-10-01 | [branch#001] [A] current
5-DaHall 1-PDU-10-02 | [branch#002] [A] current
5-DaHall 1-PDU-10-03 | [branch#003] [A] current
5-DaHall 1-PDU-10-04 | [branch#004] [A] current
5-DaHall 1-PDU-10-05 | [branch#005] [A] current
5-DaHall 1-PDU-10-06 | [branch#006] [A] current
5-DaHall 1-PDU-10-07 | [branch#007] [A] current
5-DaHall 1-PDU-10-08 | [branch#008] [A] current
5-DaHall 1-PDU-10-09 | [branch#009] [A] current
5-DaHall 1-PDU-10-10 | [branch#010] [A] current
5-DaHall 1-PDU-10-11 | [branch#011] [A] current
5-DaHall 1-PDU-10-12 | [branch#012] [A] current
5-DaHall 1-PDU-10-13 | [branch#013] [A] current
5-DaHall 1-PDU-10-14 | [branch#014] [A] current
5-DaHall 1-PDU-10-15 | [branch#015] [A] current
5-DaHall 1-PDU-10-16 | [branch#016] [A] current
5-DaHall 1-PDU-10-17 | [branch#017] [A] current
5-DaHall 1-PDU-10-18 | [branch#018] [A] current
5-DaHall 1-PDU-10-19 | [branch#019] [A] current
5-DaHall 1-PDU-10-20 | [branch#020] [A] current
5-DaHall 1-PDU-10-21 | [branch#021] [A] current
5-DaHall 1-PDU-10-22 | [branch#022] [A] current
5-DaHall 1-PDU-10-23 | [branch#023] [A] current
5-DaHall 1-PDU-10-24 | [branch#024] [A] current
5-DaHall 1-PDU-10-25 | [branch#025] [A] current
5-DaHall 1-PDU-10-26 | [branch#026] [A] current
5-DaHall 1-PDU-10-27 | [branch#027] [A] current
5-DaHall 1-PDU-10-28 | [branch#028] [A] current
5-DaHall 1-PDU-10-29 | [branch#029] [A] current
5-DaHall 1-PDU-10-30 | [branch#030] [A] current
5-DaHall 1-PDU-10-31 | [branch#031] [A] current
5-DaHall 1-PDU-10-32 | [branch#032] [A] current
5-DaHall 1-PDU-10-33 | [branch#033] [A] current
5-DaHall 1-PDU-10-34 | [branch#034] [A] current
5-DaHall 1-PDU-10-35 | [branch#035] [A] current
5-DaHall 1-PDU-10-36 | [branch#036] [A] current
5-DaHall 1-PDU-10-37 | [branch#037] [A] current
5-DaHall 1-PDU-10-38 | [branch#038] [A] current
5-DaHall 1-PDU-11-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-11-02 | [branch#002] [A] current
5-DaHall 1-PDU-11-03 | [branch#003] [A] current
5-DaHall 1-PDU-11-04 | [branch#004] [A] current
5-DaHall 1-PDU-11-05 | [branch#005] [A] current
5-DaHall 1-PDU-11-06 | [branch#006] [A] current
5-DaHall 1-PDU-11-07 | [branch#007] [A] current
5-DaHall 1-PDU-11-08 | [branch#008] [A] current
5-DaHall 1-PDU-11-09 | [branch#009] [A] current
5-DaHall 1-PDU-11-10 | [branch#010] [A] current
5-DaHall 1-PDU-11-11 | [branch#011] [A] current
5-DaHall 1-PDU-11-12 | [branch#012] [A] current
5-DaHall 1-PDU-11-13 | [branch#013] [A] current
5-DaHall 1-PDU-11-14 | [branch#014] [A] current
5-DaHall 1-PDU-11-15 | [branch#015] [A] current
5-DaHall 1-PDU-11-16 | [branch#016] [A] current
5-DaHall 1-PDU-11-17 | [branch#017] [A] current
5-DaHall 1-PDU-11-18 | [branch#018] [A] current
5-DaHall 1-PDU-11-19 | [branch#019] [A] current
5-DaHall 1-PDU-11-20 | [branch#020] [A] current
5-DaHall 1-PDU-11-21 | [branch#021] [A] current
5-DaHall 1-PDU-11-22 | [branch#022] [A] current
5-DaHall 1-PDU-11-23 | [branch#023] [A] current
5-DaHall 1-PDU-11-24 | [branch#024] [A] current
5-DaHall 1-PDU-11-25 | [branch#025] [A] current
5-DaHall 1-PDU-11-26 | [branch#026] [A] current
5-DaHall 1-PDU-11-27 | [branch#027] [A] current
5-DaHall 1-PDU-11-28 | [branch#028] [A] current
5-DaHall 1-PDU-11-29 | [branch#029] [A] current
5-DaHall 1-PDU-11-30 | [branch#030] [A] current
5-DaHall 1-PDU-11-31 | [branch#031] [A] current
5-DaHall 1-PDU-11-32 | [branch#032] [A] current
5-DaHall 1-PDU-12-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-12-02 | [branch#002] [A] current
5-DaHall 1-PDU-12-03 | [branch#003] [A] current
5-DaHall 1-PDU-12-04 | [branch#004] [A] current
5-DaHall 1-PDU-12-05 | [branch#005] [A] current
5-DaHall 1-PDU-12-06 | [branch#006] [A] current
5-DaHall 1-PDU-12-07 | [branch#007] [A] current
5-DaHall 1-PDU-12-08 | [branch#008] [A] current
5-DaHall 1-PDU-12-09 | [branch#009] [A] current
5-DaHall 1-PDU-12-10 | [branch#010] [A] current
5-DaHall 1-PDU-12-11 | [branch#011] [A] current
5-DaHall 1-PDU-12-12 | [branch#012] [A] current
5-DaHall 1-PDU-12-13 | [branch#013] [A] current
5-DaHall 1-PDU-12-14 | [branch#014] [A] current
5-DaHall 1-PDU-12-15 | [branch#015] [A] current
5-DaHall 1-PDU-12-16 | [branch#016] [A] current
5-DaHall 1-PDU-12-17 | [branch#017] [A] current
5-DaHall 1-PDU-12-18 | [branch#018] [A] current
5-DaHall 1-PDU-12-19 | [branch#019] [A] current
5-DaHall 1-PDU-12-20 | [branch#020] [A] current
5-DaHall 1-PDU-12-21 | [branch#021] [A] current
5-DaHall 1-PDU-12-22 | [branch#022] [A] current
5-DaHall 1-PDU-12-23 | [branch#023] [A] current
5-DaHall 1-PDU-12-24 | [branch#024] [A] current
5-DaHall 1-PDU-12-25 | [branch#025] [A] current
5-DaHall 1-PDU-12-26 | [branch#026] [A] current
5-DaHall 1-PDU-12-27 | [branch#027] [A] current
5-DaHall 1-PDU-12-28 | [branch#028] [A] current
5-DaHall 1-PDU-12-29 | [branch#029] [A] current
5-DaHall 1-PDU-12-30 | [branch#030] [A] current
5-DaHall 1-PDU-12-31 | [branch#031] [A] current
5-DaHall 1-PDU-12-32 | [branch#032] [A] current
5-DaHall 1-PDU-13-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-13-02 | [branch#002] [A] current
5-DaHall 1-PDU-13-03 | [branch#003] [A] current
5-DaHall 1-PDU-13-04 | [branch#004] [A] current
5-DaHall 1-PDU-13-05 | [branch#005] [A] current
5-DaHall 1-PDU-13-06 | [branch#006] [A] current
5-DaHall 1-PDU-13-07 | [branch#007] [A] current
5-DaHall 1-PDU-13-08 | [branch#008] [A] current
5-DaHall 1-PDU-13-09 | [branch#009] [A] current
5-DaHall 1-PDU-13-10 | [branch#010] [A] current
5-DaHall 1-PDU-13-11 | [branch#011] [A] current
5-DaHall 1-PDU-13-12 | [branch#012] [A] current
5-DaHall 1-PDU-13-13 | [branch#013] [A] current
5-DaHall 1-PDU-13-14 | [branch#014] [A] current
5-DaHall 1-PDU-13-15 | [branch#015] [A] current
5-DaHall 1-PDU-13-16 | [branch#016] [A] current
5-DaHall 1-PDU-13-17 | [branch#017] [A] current
5-DaHall 1-PDU-13-18 | [branch#018] [A] current
5-DaHall 1-PDU-13-19 | [branch#019] [A] current
5-DaHall 1-PDU-13-20 | [branch#020] [A] current
5-DaHall 1-PDU-13-21 | [branch#021] [A] current
5-DaHall 1-PDU-13-22 | [branch#022] [A] current
5-DaHall 1-PDU-13-23 | [branch#023] [A] current
5-DaHall 1-PDU-13-24 | [branch#024] [A] current
5-DaHall 1-PDU-13-25 | [branch#025] [A] current
5-DaHall 1-PDU-13-26 | [branch#026] [A] current
5-DaHall 1-PDU-13-27 | [branch#027] [A] current
5-DaHall 1-PDU-13-28 | [branch#028] [A] current
5-DaHall 1-PDU-13-29 | [branch#029] [A] current
5-DaHall 1-PDU-13-30 | [branch#030] [A] current
5-DaHall 1-PDU-13-31 | [branch#031] [A] current
5-DaHall 1-PDU-13-32 | [branch#032] [A] current
5-DaHall 1-PDU-14-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-14-02 | [branch#002] [A] current
5-DaHall 1-PDU-14-03 | [branch#003] [A] current
5-DaHall 1-PDU-14-04 | [branch#004] [A] current
5-DaHall 1-PDU-14-05 | [branch#005] [A] current
5-DaHall 1-PDU-14-06 | [branch#006] [A] current
5-DaHall 1-PDU-14-07 | [branch#007] [A] current
5-DaHall 1-PDU-14-08 | [branch#008] [A] current
5-DaHall 1-PDU-14-09 | [branch#009] [A] current
5-DaHall 1-PDU-14-10 | [branch#010] [A] current
5-DaHall 1-PDU-14-11 | [branch#011] [A] current
5-DaHall 1-PDU-14-12 | [branch#012] [A] current
5-DaHall 1-PDU-14-13 | [branch#013] [A] current
5-DaHall 1-PDU-14-14 | [branch#014] [A] current
5-DaHall 1-PDU-14-15 | [branch#015] [A] current
5-DaHall 1-PDU-14-16 | [branch#016] [A] current
5-DaHall 1-PDU-14-17 | [branch#017] [A] current
5-DaHall 1-PDU-14-18 | [branch#018] [A] current
5-DaHall 1-PDU-14-19 | [branch#019] [A] current
5-DaHall 1-PDU-14-20 | [branch#020] [A] current
5-DaHall 1-PDU-14-21 | [branch#021] [A] current
5-DaHall 1-PDU-14-22 | [branch#022] [A] current
5-DaHall 1-PDU-14-23 | [branch#023] [A] current
5-DaHall 1-PDU-14-24 | [branch#024] [A] current
5-DaHall 1-PDU-14-25 | [branch#025] [A] current
5-DaHall 1-PDU-14-26 | [branch#026] [A] current
5-DaHall 1-PDU-14-27 | [branch#027] [A] current
5-DaHall 1-PDU-14-28 | [branch#028] [A] current
5-DaHall 1-PDU-14-29 | [branch#029] [A] current
5-DaHall 1-PDU-14-30 | [branch#030] [A] current
5-DaHall 1-PDU-14-31 | [branch#031] [A] current
5-DaHall 1-PDU-14-32 | [branch#032] [A] current
5-DaHall 1-PDU-15-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-15-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
5-DaHall 1-PDU-15-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
5-DaHall 1-PDU-15-04 | [branch#004] [R] I1 | [branch#004] [S] I2 | [branch#004] [T] I3
5-DaHall 1-PDU-15-05 | [branch#005] [R] I1 | [branch#005] [S] I2 | [branch#005] [T] I3
5-DaHall 1-PDU-15-06 | [branch#006] [R] I1 | [branch#006] [S] I2 | [branch#006] [T] I3
5-DaHall 1-PDU-15-07 | [branch#007] [A] current
5-DaHall 1-PDU-15-08 | [branch#008] [A] current
5-DaHall 1-PDU-15-09 | [branch#009] [A] current
5-DaHall 1-PDU-15-10 | [branch#010] [A] current
5-DaHall 1-PDU-15-11 | [branch#011] [A] current
5-DaHall 1-PDU-15-12 | [branch#012] [A] current
5-DaHall 1-PDU-15-13 | [branch#013] [A] current
5-DaHall 1-PDU-15-14 | [branch#014] [A] current
5-DaHall 1-PDU-15-15 | [branch#015] [A] current
5-DaHall 1-PDU-15-16 | [branch#016] [A] current
5-DaHall 1-PDU-15-17 | [branch#017] [A] current
5-DaHall 1-PDU-15-18 | [branch#018] [A] current
5-DaHall 1-PDU-15-19 | [branch#019] [A] current
5-DaHall 1-PDU-15-20 | [branch#020] [A] current
5-DaHall 1-PDU-15-21 | [branch#021] [A] current
5-DaHall 1-PDU-15-22 | [branch#022] [A] current
5-DaHall 1-PDU-15-23 | [branch#023] [A] current
5-DaHall 1-PDU-15-24 | [branch#024] [A] current
5-DaHall 1-PDU-15-25 | [branch#025] [A] current
5-DaHall 1-PDU-15-26 | [branch#026] [A] current
5-DaHall 1-PDU-15-27 | [branch#027] [A] current
5-DaHall 1-PDU-15-28 | [branch#028] [A] current
5-DaHall 1-PDU-15-29 | [branch#029] [A] current
5-DaHall 1-PDU-15-30 | [branch#030] [A] current
5-DaHall 1-PDU-16-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-PDU-16-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
5-DaHall 1-PDU-16-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
5-DaHall 1-PDU-16-04 | [branch#004] [R] I1 | [branch#004] [S] I2 | [branch#004] [T] I3
5-DaHall 1-PDU-16-05 | [branch#005] [R] I1 | [branch#005] [S] I2 | [branch#005] [T] I3
5-DaHall 1-PDU-16-06 | [branch#006] [R] I1 | [branch#006] [S] I2 | [branch#006] [T] I3
5-DaHall 1-PDU-16-07 | [branch#007] [A] current
5-DaHall 1-PDU-16-08 | [branch#008] [A] current
5-DaHall 1-PDU-16-09 | [branch#009] [A] current
5-DaHall 1-PDU-16-10 | [branch#010] [A] current
5-DaHall 1-PDU-16-11 | [branch#011] [A] current
5-DaHall 1-PDU-16-12 | [branch#012] [A] current
5-DaHall 1-PDU-16-13 | [branch#013] [A] current
5-DaHall 1-PDU-16-14 | [branch#014] [A] current
5-DaHall 1-PDU-16-15 | [branch#015] [A] current
5-DaHall 1-PDU-16-16 | [branch#016] [A] current
5-DaHall 1-PDU-16-17 | [branch#017] [A] current
5-DaHall 1-PDU-16-18 | [branch#018] [A] current
5-DaHall 1-PDU-16-19 | [branch#019] [A] current
5-DaHall 1-PDU-16-20 | [branch#020] [A] current
5-DaHall 1-PDU-16-21 | [branch#021] [A] current
5-DaHall 1-PDU-16-22 | [branch#022] [A] current
5-DaHall 1-PDU-16-23 | [branch#023] [A] current
5-DaHall 1-PDU-16-24 | [branch#024] [A] current
5-DaHall 1-PDU-16-25 | [branch#025] [A] current
5-DaHall 1-PDU-16-26 | [branch#026] [A] current
5-DaHall 1-PDU-16-27 | [branch#027] [A] current
5-DaHall 1-PDU-16-28 | [branch#028] [A] current
5-DaHall 1-PDU-16-29 | [branch#029] [A] current
5-DaHall 1-PDU-16-30 | [branch#030] [A] current
5-DaHall 1-PDU-17-01 | 0150 [branch#01] [A] current
5-DaHall 1-PDU-17-02 | 0290 [branch#02] [A] current
5-DaHall 1-PDU-17-03 | 0430 [branch#03] [A] current
5-DaHall 1-PDU-17-04 | 0570 [branch#04] [A] current
5-DaHall 1-PDU-17-05 | 0710 [branch#05] [A] current
5-DaHall 1-PDU-17-06 | 0850 [branch#06] [A] current
5-DaHall 1-PDU-17-07 | 0990 [branch#07] [A] current
5-DaHall 1-PDU-17-08 | 1130 [branch#08] [A] current
5-DaHall 1-PDU-17-09 | 1270 [branch#09] [A] current
5-DaHall 1-PDU-17-10 | 1410 [branch#10] [A] current
5-DaHall 1-PDU-17-11 | 1550 [branch#11] [A] current
5-DaHall 1-PDU-17-12 | 1690 [branch#12] [A] current
5-DaHall 1-PDU-17-13 | 1830 [branch#13] [A] current
5-DaHall 1-PDU-17-14 | 1970 [branch#14] [A] current
5-DaHall 1-PDU-17-15 | 2110 [branch#15] [A] current
5-DaHall 1-PDU-17-16 | 2250 [branch#16] [A] current
5-DaHall 1-PDU-17-17 | 2390 [branch#17] [A] current
5-DaHall 1-PDU-17-18 | 2530 [branch#18] [A] current
5-DaHall 1-PDU-17-19 | 2670 [branch#19] [A] current
5-DaHall 1-PDU-17-20 | 2810 [branch#20] [A] current
5-DaHall 1-PDU-17-21 | 2950 [branch#21] [A] current
5-DaHall 1-PDU-17-22 | 3090 [branch#22] [A] current
5-DaHall 1-PDU-17-23 | 3230 [branch#23] [A] current
5-DaHall 1-PDU-17-24 | 3370 [branch#24] [A] current
5-DaHall 1-PDU-17-25 | 3510 [branch#25] [A] current
5-DaHall 1-PDU-17-26 | 3650 [branch#26] [A] current
5-DaHall 1-PDU-17-27 | 3790 [branch#27] [A] current
5-DaHall 1-PDU-17-28 | 3930 [branch#28] [A] current
5-DaHall 1-PDU-17-29 | 4070 [branch#29] [A] current
5-DaHall 1-PDU-17-30 | 4210 [branch#30] [A] current
5-DaHall 1-PDU-17-31 | 4350 [branch#31] [A] current
5-DaHall 1-PDU-17-32 | 4490 [branch#32] [A] current
5-DaHall 1-PDU-17-33 | 4630 [branch#33] [A] current
5-DaHall 1-PDU-17-34 | 4770 [branch#34] [A] current
5-DaHall 1-PDU-18-01 | 0150 [branch#01] [A] current
5-DaHall 1-PDU-18-02 | 0290 [branch#02] [A] current
5-DaHall 1-PDU-18-03 | 0430 [branch#03] [A] current
5-DaHall 1-PDU-18-04 | 0570 [branch#04] [A] current
5-DaHall 1-PDU-18-05 | 0710 [branch#05] [A] current
5-DaHall 1-PDU-18-06 | 0850 [branch#06] [A] current
5-DaHall 1-PDU-18-07 | 0990 [branch#07] [A] current
5-DaHall 1-PDU-18-08 | 1130 [branch#08] [A] current
5-DaHall 1-PDU-18-09 | 1270 [branch#09] [A] current
5-DaHall 1-PDU-18-10 | 1410 [branch#10] [A] current
5-DaHall 1-PDU-18-11 | 1550 [branch#11] [A] current
5-DaHall 1-PDU-18-12 | 1690 [branch#12] [A] current
5-DaHall 1-PDU-18-13 | 1830 [branch#13] [A] current
5-DaHall 1-PDU-18-14 | 1970 [branch#14] [A] current
5-DaHall 1-PDU-18-15 | 2110 [branch#15] [A] current
5-DaHall 1-PDU-18-16 | 2250 [branch#16] [A] current
5-DaHall 1-PDU-18-17 | 2390 [branch#17] [A] current
5-DaHall 1-PDU-18-18 | 2530 [branch#18] [A] current
5-DaHall 1-PDU-18-19 | 2670 [branch#19] [A] current
5-DaHall 1-PDU-18-20 | 2810 [branch#20] [A] current
5-DaHall 1-PDU-18-21 | 2950 [branch#21] [A] current
5-DaHall 1-PDU-18-22 | 3090 [branch#22] [A] current
5-DaHall 1-PDU-18-23 | 3230 [branch#23] [A] current
5-DaHall 1-PDU-18-24 | 3370 [branch#24] [A] current
5-DaHall 1-PDU-18-25 | 3510 [branch#25] [A] current
5-DaHall 1-PDU-18-26 | 3650 [branch#26] [A] current
5-DaHall 1-PDU-18-27 | 3790 [branch#27] [A] current
5-DaHall 1-PDU-18-28 | 3930 [branch#28] [A] current
5-DaHall 1-PDU-18-29 | 4070 [branch#29] [A] current
5-DaHall 1-PDU-18-30 | 4210 [branch#30] [A] current
5-DaHall 1-PDU-18-31 | 4350 [branch#31] [A] current
5-DaHall 1-PDU-18-32 | 4490 [branch#32] [A] current
5-DaHall 1-PDU-18-33 | 4630 [branch#33] [A] current
5-DaHall 1-PDU-18-34 | 4770 [branch#34] [A] current
5-DaHall 1-PDU-19-01 | 0150 [branch#01] [A] current
5-DaHall 1-PDU-19-02 | 0290 [branch#02] [A] current
5-DaHall 1-PDU-19-03 | 0430 [branch#03] [A] current
5-DaHall 1-PDU-19-04 | 0570 [branch#04] [A] current
5-DaHall 1-PDU-19-05 | 0710 [branch#05] [A] current
5-DaHall 1-PDU-19-06 | 0850 [branch#06] [A] current
5-DaHall 1-PDU-19-07 | 0990 [branch#07] [A] current
5-DaHall 1-PDU-19-08 | 1130 [branch#08] [A] current
5-DaHall 1-PDU-19-09 | 1270 [branch#09] [A] current
5-DaHall 1-PDU-19-10 | 1410 [branch#10] [A] current
5-DaHall 1-PDU-19-11 | 1550 [branch#11] [A] current
5-DaHall 1-PDU-19-12 | 1690 [branch#12] [A] current
5-DaHall 1-PDU-19-13 | 1830 [branch#13] [A] current
5-DaHall 1-PDU-19-14 | 1970 [branch#14] [A] current
5-DaHall 1-PDU-19-15 | 2110 [branch#15] [A] current
5-DaHall 1-PDU-19-16 | 2250 [branch#16] [A] current
5-DaHall 1-PDU-19-17 | 2390 [branch#17] [A] current
5-DaHall 1-PDU-19-18 | 2530 [branch#18] [A] current
5-DaHall 1-PDU-19-19 | 2670 [branch#19] [A] current
5-DaHall 1-PDU-19-20 | 2810 [branch#20] [A] current
5-DaHall 1-PDU-19-21 | 2950 [branch#21] [A] current
5-DaHall 1-PDU-19-22 | 3090 [branch#22] [A] current
5-DaHall 1-PDU-19-23 | 3230 [branch#23] [A] current
5-DaHall 1-PDU-19-24 | 3370 [branch#24] [A] current
5-DaHall 1-PDU-20-01 | 0150 [branch#01] [A] current
5-DaHall 1-PDU-20-02 | 0290 [branch#02] [A] current
5-DaHall 1-PDU-20-03 | 0430 [branch#03] [A] current
5-DaHall 1-PDU-20-04 | 0570 [branch#04] [A] current
5-DaHall 1-PDU-20-05 | 0710 [branch#05] [A] current
5-DaHall 1-PDU-20-06 | 0850 [branch#06] [A] current
5-DaHall 1-PDU-20-07 | 0990 [branch#07] [A] current
5-DaHall 1-PDU-20-08 | 1130 [branch#08] [A] current
5-DaHall 1-PDU-20-09 | 1270 [branch#09] [A] current
5-DaHall 1-PDU-20-10 | 1410 [branch#10] [A] current
5-DaHall 1-PDU-20-11 | 1550 [branch#11] [A] current
5-DaHall 1-PDU-20-12 | 1690 [branch#12] [A] current
5-DaHall 1-PDU-20-13 | 1830 [branch#13] [A] current
5-DaHall 1-PDU-20-14 | 1970 [branch#14] [A] current
5-DaHall 1-PDU-20-15 | 2110 [branch#15] [A] current
5-DaHall 1-PDU-20-16 | 2250 [branch#16] [A] current
5-DaHall 1-PDU-20-17 | 2390 [branch#17] [A] current
5-DaHall 1-PDU-20-18 | 2530 [branch#18] [A] current
5-DaHall 1-PDU-20-19 | 2670 [branch#19] [A] current
5-DaHall 1-PDU-20-20 | 2810 [branch#20] [A] current
5-DaHall 1-PDU-20-21 | 2950 [branch#21] [A] current
5-DaHall 1-PDU-20-22 | 3090 [branch#22] [A] current
5-DaHall 1-PDU-20-23 | 3230 [branch#23] [A] current
5-DaHall 1-PDU-20-24 | 3370 [branch#24] [A] current
5-DaHall 1-PDU-21-01 | 0150 [branch#01] [A] current
5-DaHall 1-PDU-21-02 | 0290 [branch#02] [A] current
5-DaHall 1-PDU-21-03 | 0430 [branch#03] [A] current
5-DaHall 1-PDU-21-04 | 0570 [branch#04] [A] current
5-DaHall 1-PDU-21-05 | 0710 [branch#05] [A] current
5-DaHall 1-PDU-21-06 | 0850 [branch#06] [A] current
5-DaHall 1-PDU-21-07 | 0990 [branch#07] [A] current
5-DaHall 1-PDU-21-08 | 1130 [branch#08] [A] current
5-DaHall 1-PDU-21-09 | 1270 [branch#09] [A] current
5-DaHall 1-PDU-21-10 | 1410 [branch#10] [A] current
5-DaHall 1-PDU-21-11 | 1550 [branch#11] [A] current
5-DaHall 1-PDU-21-12 | 1690 [branch#12] [A] current
5-DaHall 1-PDU-21-13 | 1830 [branch#13] [A] current
5-DaHall 1-PDU-21-14 | 1970 [branch#14] [A] current
5-DaHall 1-PDU-21-15 | 2110 [branch#15] [A] current
5-DaHall 1-PDU-21-16 | 2250 [branch#16] [A] current
5-DaHall 1-PDU-21-17 | 2390 [branch#17] [A] current
5-DaHall 1-PDU-21-18 | 2530 [branch#18] [A] current
5-DaHall 1-PDU-21-19 | 2670 [branch#19] [A] current
5-DaHall 1-PDU-21-20 | 2810 [branch#20] [A] current
5-DaHall 1-PDU-21-21 | 2950 [branch#21] [A] current
5-DaHall 1-PDU-21-22 | 3090 [branch#22] [A] current
5-DaHall 1-PDU-21-23 | 3230 [branch#23] [A] current
5-DaHall 1-PDU-21-24 | 3370 [branch#24] [A] current
5-DaHall 1-PDU-22-01 | 0150 [branch#01] [A] current
5-DaHall 1-PDU-22-02 | 0290 [branch#02] [A] current
5-DaHall 1-PDU-22-03 | 0430 [branch#03] [A] current
5-DaHall 1-PDU-22-04 | 0570 [branch#04] [A] current
5-DaHall 1-PDU-22-05 | 0710 [branch#05] [A] current
5-DaHall 1-PDU-22-06 | 0850 [branch#06] [A] current
5-DaHall 1-PDU-22-07 | 0990 [branch#07] [A] current
5-DaHall 1-PDU-22-08 | 1130 [branch#08] [A] current
5-DaHall 1-PDU-22-09 | 1270 [branch#09] [A] current
5-DaHall 1-PDU-22-10 | 1410 [branch#10] [A] current
5-DaHall 1-PDU-22-11 | 1550 [branch#11] [A] current
5-DaHall 1-PDU-22-12 | 1690 [branch#12] [A] current
5-DaHall 1-PDU-22-13 | 1830 [branch#13] [A] current
5-DaHall 1-PDU-22-14 | 1970 [branch#14] [A] current
5-DaHall 1-PDU-22-15 | 2110 [branch#15] [A] current
5-DaHall 1-PDU-22-16 | 2250 [branch#16] [A] current
5-DaHall 1-PDU-22-17 | 2390 [branch#17] [A] current
5-DaHall 1-PDU-22-18 | 2530 [branch#18] [A] current
5-DaHall 1-PDU-22-19 | 2670 [branch#19] [A] current
5-DaHall 1-PDU-22-20 | 2810 [branch#20] [A] current
5-DaHall 1-PDU-22-21 | 2950 [branch#21] [A] current
5-DaHall 1-PDU-22-22 | 3090 [branch#22] [A] current
5-DaHall 1-PDU-22-23 | 3230 [branch#23] [A] current
5-DaHall 1-PDU-22-24 | 3370 [branch#24] [A] current
5-DaHall 1-CEP-05-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
5-DaHall 1-CEP-05-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
5-DaHall 1-CEP-05-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
5-DaHall 1-CEP-05-04 | [branch#004] [R] I1 | [branch#004] [S] I2 | [branch#004] [T] I3
5-DaHall 1-CEP-05-05 | [branch#005] [R] I1 | [branch#005] [S] I2 | [branch#005] [T] I3
5-DaHall 1-CEP-05-06 | [branch#006] [R] I1 | [branch#006] [S] I2 | [branch#006] [T] I3
5-DaHall 1-CEP-05-07 | [branch#007] [R] I1 | [branch#007] [S] I2 | [branch#007] [T] I3
5-DaHall 1-CEP-05-08 | [branch#008] [R] I1 | [branch#008] [S] I2 | [branch#008] [T] I3
5-DaHall 1-CEP-05-09 | [branch#009] [R] I1 | [branch#009] [S] I2 | [branch#009] [T] I3
5-DaHall 1-CEP-05-10 | [branch#010] [R] I1 | [branch#010] [S] I2 | [branch#010] [T] I3
5-DaHall 1-CEP-05-11 | [branch#011] [R] I1 | [branch#011] [S] I2 | [branch#011] [T] I3
5-DaHall 1-CEP-05-12 | [branch#012] [R] I1 | [branch#012] [S] I2 | [branch#012] [T] I3
5-DaHall 1-CEP-05-13 | [branch#012] [A] current
5-DaHall 1-CEP-05-14 | [branch#013] [A] current
5-DaHall 1-CEP-05-15 | [branch#014] [A] current
5-DaHall 1-CEP-05-16 | [branch#015] [A] current
5-DaHall 1-CEP-05-17 | [branch#016] [A] current
5-DaHall 1-CEP-05-18 | [branch#017] [A] current
5-DaHall 1-CEP-06-01 | 0205 [branch#01] [R] I1 | 0230 [branch#01] [S] I2 | 0255 [branch#01] [T] I3
5-DaHall 1-CEP-06-02 | 0345 [branch#02] [R] I1 | 0370 [branch#02] [S] I2 | 0395 [branch#02] [T] I3
5-DaHall 1-CEP-06-03 | 0485 [branch#03] [R] I1 | 0510 [branch#03] [S] I2 | 0535 [branch#03] [T] I3
5-DaHall 1-CEP-06-04 | 0625 [branch#04] [R] I1 | 0650 [branch#04] [S] I2 | 0675 [branch#04] [T] I3

## 5층_부하량(월간_MAX)
Date : 2023-11-01 ~ 2023-11-30
5-DaHall 1-CEP-05 | [8 empty] | Main CB 4P 350A
[12 empty] | MAIN 계측값 : | 62.2 | 67 | 61.8 | <- 실측값 |  |  | -1
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
5-DaHall 1-CRAC-16 보조 5F-2호기(구글) | O | ON | 0 | 0 | 0 |  | 4P 50A | #01 | . | . | #02 | 4P 50A | 0 | 0 | 0 |  | O | ON | 5-DaHall 1-CRAC-15 보조 5F-1호기(구글)
5-DaHall 1-CRAC-01 LG CRAC #01 | O | ON | 21.31 | 21.47 | 20.96 |  | 4P 50A | #03 | . | . | #04 | 4P 50A | 23.99 | 23.98 | 23.54 |  | O | ON | 5-DaHall 1-CRAC-02 LG CRAC #02
5-DaHall 1-CRAC-03 LG CRAC #03 | O | ON | 22.58 | 22.85 | 22.19 |  | 4P 50A | #05 | . | . | #06 | 4P 50A | 25.26 | 24.86 | 25.16 |  | O | ON | 5-DaHall 1-CRAC-04 LG CRAC #04
5-DaHall 1-CRAC-05 LG CRAC #05 | O | ON | 24.42 | 24.4 | 24.07 |  | 4P 50A | #07 | . | . | #08 | 4P 50A | 24.3 | 24.7 | 24.07 |  | O | ON | 5-DaHall 1-CRAC-06 LG CRAC #06
5-DaHall 1-CRAC-07 LG CRAC #07 | O | ON | 20.68 | 21 | 20.43 |  | 4P 50A | #09 | . | . | #10 | 4P 50A | 20.46 | 20.84 | 20.36 |  | O | ON | 5-DaHall 1-CRAC-08 LG CRAC #08
5-DaHall 1-CRAC-09 LG CRAC #09 | O | ON | 22.85 | 23.52 | 22.77 |  | 4P 50A | #11 | . | . | #12 | 4P 50A | 24.59 | 23.85 | 24.56 |  | O | ON | 5-DaHall 1-CRAC-13 CF CRAC #01
spare | X | OFF | 72.62 |  |  |  | 2P 30A | #13 | . | . | #14 | 2P 30A | 0 |  |  |  | X | OFF | spare
spare | X | OFF |  | 0 |  |  | 2P 30A | #15 | . | . | #16 | 2P 50A |  | 14.37 |  |  | O | ON | 5-DaHall 1-EH (5층 가습기 Main)
spare | X | OFF |  |  | 13.92 |  | 2P 30A | #17 | . | . | #18 | 2P 50A |  |  | 17.77 |  | O | ON | 4-DaHall 1-EH (4층 가습기 Main)
[12 empty] | 합계: | 303.06 | 245.84 | 259.8
5-DaHall 1-CEP-06 | [8 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 0.7 | 0 | 0.7 | <- 실측값
[10 empty] | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
[10 empty] | . | #01 | 4P 60A | 20.19 | 19.6 | 19.23 |  | O | ON | LG CRAC #10 (수냉식)
[10 empty] | . | #02 | 4P 60A | 20.8 | 20.48 | 20.24 |  | O | ON | LG CRAC #11 (수냉식)
[10 empty] | . | #03 | 4P 60A | 20.05 | 19.64 | 19.62 |  | O | ON | LG CRAC #12 (수냉식)
[10 empty] | . | #04 | 4P 60A | 0 | 0 | 0 |  | X | OFF | spare
[12 empty] | 합계: | 61.04 | 59.72 | 59.09
5-DaHall 1-PDU-01 |  | PDU : SEL1 - 5-1 - A1 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 34.6 | 37.8 | 27.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0.6 | 0.76 |  | O | ON | 보다폰정류기-A
1A-1-1 | O | ON | 0 |  |  |  | 2P 30A | #01 | CF상면 |  | #02 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-21 / 1A-2-11
1A-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | CF상면 | 구글202-A | #04 | 2P 30A |  | 0 |  |  | O | ON | 1A-2-12
1A-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | CF상면 | 구글201-A | #06 | 2P 30A |  |  | 1.55 |  | O | ON | 1A-2-13
1A-1-4 | O | OFF | 0 |  |  |  | 2P 30A | #07 | CF상면 |  | #08 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-24 / 1A-2-14
G1101 (1A-1-5) | O | ON |  | 15.96 |  |  | 2P 30A | #09 | cloudflare | 구글 시스템박스 | #10 | 2P 30A |  | 0 |  |  | O | ON | 1A-2-15
G1102 (1A-1-6) | O | ON |  |  | 12.94 |  | 2P 30A | #11 | cloudflare | 철거필요 | #12 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-1
G1103 (1A-1-7) | O | ON | 15.76 |  |  |  | 2P 30A | #13 | cloudflare | 철거필요 | #14 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-2
G1104 (1A-1-8) | O | ON |  | 0 |  |  | 2P 30A | #15 | cloudflare | 철거필요 | #16 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-3
G1105 (1A-1-9) | O | ON |  |  | 0 |  | 2P 30A | #17 | cloudflare | 철거필요 | #18 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-4
1A-1-10 | O | ON | 1.06 |  |  |  | 2P 30A | #19 | 구글104-A | 철거필요 | #20 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-5
1A-1-11 | O | ON |  | 1.55 |  |  | 2P 30A | #21 | 구글103-A | 철거필요 | #22 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-6
1A-1-12 | O | ON |  |  | 1.61 |  | 2P 30A | #23 | 구글102-A | 철거필요 | #24 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-7
1A-1-13 | O | ON | 0 |  |  |  | 2P 30A | #25 | 구글101-A | 철거필요 | #26 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-8
1A-1-14 | O | OFF |  | 0 |  |  | 2P 30A | #27 |  | 철거필요 | #28 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-9
1A-1-15 | O | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | O | OFF | 5F-P-20 / 1A-3-10
G1201 (1A-2-1) | O | ON | 12.07 |  |  |  | 2P 30A | #31 | cloudflare |  | #32 | 2P 30A | 0 |  |  |  | O | OFF | 5F-P-21 / 1A-3-11
G1202 (1A-2-2) | O | ON |  | 11.03 |  |  | 2P 30A | #33 | cloudflare |  | #34 | 2P 30A |  | 0 |  |  | O | OFF | 5F-P-22 / 1A-3-12
G1203 (1A-2-3) | O | ON |  |  | 13.11 |  | 2P 30A | #35 | cloudflare |  | #36 | 2P 30A |  |  | 0 |  | O | OFF | 5F-P-23 / 1A-3-13
G1204 (1A-2-4) | O | ON | 10.53 |  |  |  | 2P 30A | #37 | cloudflare |  | #38 | 2P 30A | 0 |  |  |  | O | OFF | 5F-P-24 / 1A-3-14
G1205 (1A-2-5) | O | ON |  | 13.42 |  |  | 2P 30A | #39 | cloudflare | ?? | #40 | 2P 30A |  | 0 |  |  | X | OFF
1A-2-6 | O | OFF |  |  | 0 |  | 2P 30A | #41 | CF상면 | 보다폰 케이지 안쪽 | #42 | 2P 30A |  |  | 0 |  | O | OFF | 1A-4-1
1A-2-7 | O | OFF | 0 |  |  |  | 2P 30A | #43 | CF상면 | 보다폰 케이지 안쪽 | #44 | 2P 30A | 0 |  |  |  | O | OFF | 1A-4-2
1A-2-8 | O | OFF |  | 0 |  |  | 2P 30A | #45 | CF상면 | 보다폰 케이지 안쪽 | #46 | 2P 30A |  | 0.7 |  |  | O | ON | 1A-4-3
1A-2-9 | O | OFF |  |  | 0 |  | 2P 30A | #47 | CF상면 | Vodafone | #48 | 2P 30A |  |  | 1.76 |  | O | ON | VF Rack#1-상
5F-Q-20 | O | OFF | 0 |  |  |  | 2P 30A | #49 |  | Vodafone | #50 | 2P 30A | 0 |  |  |  | O | ON | VF Rack#2-상
[12 empty] | 합계: | 39.42 | 43.26 | 31.73
5-DaHall 1-PDU-02 |  | PDU : SEL1 - 5-1 - B1 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 34.6 | 35.2 | 26.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0.67 | 0.75 |  | O | ON | 보다폰정류기-B
1B-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | CF상면 |  | #02 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-21 / 1B-2-11
1B-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | CF상면 | 구글202-A | #04 | 2P 30A |  | 0 |  |  | O | ON | 1B-2-12
1B-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | CF상면 | 구글201-A | #06 | 2P 30A |  |  | 1.26 |  | O | ON | 1B-2-13
1B-1-4 | O | OFF | 0 |  |  |  | 2P 30A | #07 | CF상면 |  | #08 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-24 / 1B-2-14
G1101 (1B-1-5) | O | ON |  | 13.34 |  |  | 2P 30A | #09 | cloudflare | 구글Cage 지문인식기 | #10 | 2P 30A |  | 0 |  |  | O | ON | 1B-2-15
G1102 (1B-1-6) | O | ON |  |  | 14.84 |  | 2P 30A | #11 | cloudflare |  | #12 | 2P 30A |  |  | 0 |  | O | OFF | 1B-3-1
G1103 (1B-1-7) | O | ON | 13.06 |  |  |  | 2P 30A | #13 | cloudflare |  | #14 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-2
G1104 (1B-1-8) | O | ON |  | 0 |  |  | 2P 30A | #15 | cloudflare |  | #16 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-3
G1105 (1B-1-9) | O | ON |  |  | 0 |  | 2P 30A | #17 | cloudflare |  | #18 | 2P 30A |  |  | 0 |  | O | ON | 1B-3-4
1B-1-10 | O | ON | 0 |  |  |  | 2P 30A | #19 | 구글104-A |  | #20 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-5
1B-1-11 | O | ON |  | 1.69 |  |  | 2P 30A | #21 | 구글103-A |  | #22 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-6
1B-1-12 | O | ON |  |  | 1.34 |  | 2P 30A | #23 | 구글102-A |  | #24 | 2P 30A |  |  | 0 |  | O | ON | 1B-3-7
1B-1-13 | O | ON | 0 |  |  |  | 2P 30A | #25 | 구글101-A |  | #26 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-8
1B-1-14 | O | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-9
1B-1-15 | O | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | O | ON | 5F-P-20 / 1B-3-10
G1201 (1A-2-1) | O | ON | 13.04 |  |  |  | 2P 30A | #31 | cloudflare |  | #32 | 2P 30A | 0 |  |  |  | O | ON | 5F-P-21 / 1B-3-11
G1202 (1B-2-2) | O | ON |  | 12.93 |  |  | 2P 30A | #33 | cloudflare |  | #34 | 2P 30A |  | 0 |  |  | O | ON | 5F-P-22 / 1B-3-12
G1203 (1B-2-3) | O | ON |  |  | 10.87 |  | 2P 30A | #35 | cloudflare |  | #36 | 2P 30A |  |  | 0 |  | O | ON | 5F-P-23 / 1B-3-13
G1204 (1B-2-4) | O | ON | 12.53 |  |  |  | 2P 30A | #37 | cloudflare |  | #38 | 2P 30A | 0 |  |  |  | O | ON | 5F-P-24 / 1B-3-14
G1205 (1B-2-5) | O | ON |  | 10.71 |  |  | 2P 30A | #39 | cloudflare |  | #40 | 2P 30A |  | 0 |  |  | O | OFF | 5F-P-25 / 1B-3-15
1B-2-6 | O | OFF |  |  | 0 |  | 2P 30A | #41 | CF상면 | ?? | #42 | 2P 30A |  |  | 0 |  | O | OFF | 1B-7-1(2)
1B-2-7 | O | OFF | 0 |  |  |  | 2P 30A | #43 | CF상면 |  | #44 | 2P 30A | 0 |  |  |  | O | OFF | 1B-4-2
1B-2-8 | O | OFF |  | 0 |  |  | 2P 30A | #45 | CF상면 | 보다폰 케이지 안쪽 | #46 | 2P 30A |  | 0.99 |  |  | O | ON | 1B-4-3
1B-2-9 | O | OFF |  |  | 0 |  | 2P 30A | #47 | CF상면 | Vodafone | #48 | 2P 30A |  |  | 1.13 |  | O | ON | VF Rack#1-하
5F-Q-20 | O | OFF | 0 |  |  |  | 2P 30A | #49 |  | Vodafone | #50 | 2P 30A | 0 |  |  |  | O | ON | VF Rack#2-하
[12 empty] | 합계: | 38.63 | 40.33 | 30.19
5-DaHall 1-PDU-03 |  | PDU : SEL1 - 5-1 - A2 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 26.8 | 15.9 | 18 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0 | 0 |  | X | OFF
5F-O-16 / 2A-4-6 | O | ON | 0 |  |  |  | 2P 30A | #01 |  | KG이니시스 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B221 (R13)-1
5F-O-17 / 2A-4-7 | O | ON |  | 0 |  |  | 2P 30A | #03 |  | KG이니시스 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B221 (R13)-2
5F-O-18 | O | ON |  |  | 0 |  | 2P 30A | #05 |  | KG이니시스 | #06 | 2P 30A |  |  | 0.73 |  | O | ON | B222 (R14)-1
5F-O-19 | O | ON | 0 |  |  |  | 2P 30A | #07 |  | KG이니시스 | #08 | 2P 30A | 1.78 |  |  |  | O | ON | B222 (R14)-2
5F-O-20 | O | ON |  | 0 |  |  | 2P 30A | #09 |  | KG이니시스 | #10 | 2P 30A |  | 4.61 |  |  | O | ON | B316 (R15)-1
5F-O-21 | O | ON |  |  | 0 |  | 2P 30A | #11 |  | KG이니시스 | #12 | 2P 30A |  |  | 2.06 |  | O | ON | B316 (R15)-2
5F-O-22 | O | ON | 0 |  |  |  | 2P 30A | #13 |  | KG이니시스 | #14 | 2P 30A | 2.6 |  |  |  | O | ON | B317 (R16)-1
5F-O-23 | O | ON |  | 0 |  |  | 2P 30A | #15 |  | KG이니시스 | #16 | 2P 30A |  | 4.46 |  |  | O | ON | B318 (R17)-1
5F-O-24 | O | ON |  |  | 0 |  | 2P 30A | #17 |  | KG이니시스 | #18 | 2P 30A |  |  | 5.69 |  | O | ON | B319 (R18)
2A-7-2(2) | X | OFF | 0 |  |  |  | 2P 30A | #19 | ?? | KG이니시스 | #20 | 2P 30A | 2.96 |  |  |  | O | ON | B320 (R19)
2A-5-1 | O | OFF |  | 0 |  |  | 2P 30A | #21 | 보다폰상면 | KG이니시스 | #22 | 2P 30A |  | 4.3 |  |  | O | ON | B321 (R20)
2A-5-2 | O | ON |  |  | 0 |  | 2P 30A | #23 | 보다폰상면 | KG이니시스 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B322 (R21)
2A-5-3 | O | ON | 0 |  |  |  | 2P 30A | #25 | 보다폰상면 | KG이니시스 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B416 (R22)
2A-5-4 | O | ON |  | 0 |  |  | 2P 30A | #27 | 보다폰상면 | KG이니시스 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B417 (R23)
2A-5-5 | O | ON |  |  | 0 |  | 2P 30A | #29 |  | KG이니시스 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B418 (R24)
5-1-A2-31 | X | OFF | 0 |  |  |  | 2P 30A | #31 |  | KG이니시스 | #32 | 2P 30A | 2.55 |  |  |  | O | ON | B116 (R12)
5-1-A2-33 | X | OFF |  | 0 |  |  | 2P 30A | #33 |  | KG이니시스 | #34 | 2P 30A |  | 2.41 |  |  | O | ON | B117 (R11)
5-1-A2-35 | X | OFF |  |  | 0 |  | 2P 30A | #35 |  | KG이니시스 | #36 | 2P 30A |  |  | 2.2 |  | O | ON | B118 (R10)
B317 (R16)-2 | O | ON | 4.41 |  |  |  | 2P 30A | #37 | KG이니시스 | KG이니시스 | #38 | 2P 30A | 2.55 |  |  |  | O | ON | B119 (R9)
B318 (R17)-2 | O | ON |  | 2.45 |  |  | 2P 30A | #39 | KG이니시스 | KG이니시스 | #40 | 2P 30A |  | 1.39 |  |  | O | ON | B120 (R8)
B221 (R13)-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | KG이니시스 | KG이니시스 | #42 | 2P 30A |  |  | 1.87 |  | O | ON | B121 (R7)
B222 (R14)-3 | O | ON | 3.38 |  |  |  | 2P 30A | #43 | KG이니시스 | KG이니시스 | #44 | 2P 30A | 3.37 |  |  |  | O | ON | B122 (R6)
B316 (R15)-3 | O | ON |  | 0 |  |  | 2P 30A | #45 | KG이니시스 | KG이니시스 | #46 | 2P 30A |  | 3.15 |  |  | O | ON | B216 (R5)
B219 (R2) | O | ON |  |  | 4.46 |  | 2P 30A | #47 | KG이니시스 | KG이니시스 | #48 | 2P 30A |  |  | 4.07 |  | O | ON | B217 (R4)
B220 (R1) | O | ON | 6.09 |  |  |  | 2P 30A | #49 | KG이니시스 | KG이니시스 | #50 | 2P 30A | 4.62 |  |  |  | O | ON | B218 (R3)
[12 empty] | 합계: | 34.31 | 22.77 | 21.08
5-DaHall 1-PDU-04 |  | PDU : SEL1 - 5-1 - B2 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 25.1 | 15.5 | 18.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| O | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0 | 0 |  | O | OFF
5F-O-16 / 2B-4-6 | O | ON | 0 |  |  |  | 2P 30A | #01 | 철거가능 | KG이니시스 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B221 (R13)-1
5F-O-17 / 2B-4-7 | O | ON |  | 0 |  |  | 2P 30A | #03 | 철거가능 | KG이니시스 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B221 (R13)-2
5F-O-18 | O | ON |  |  | 0 |  | 2P 30A | #05 | 철거가능 | KG이니시스 | #06 | 2P 30A |  |  | 0.73 |  | O | ON | B222 (R14)-1
5F-O-19 | O | ON | 0 |  |  |  | 2P 30A | #07 | 철거가능 | KG이니시스 | #08 | 2P 30A | 2.08 |  |  |  | O | ON | B222 (R14)-2
5F-O-20 | O | ON |  | 0 |  |  | 2P 30A | #09 | 철거가능 | KG이니시스 | #10 | 2P 30A |  | 4.46 |  |  | O | ON | B316 (R15)-1
5F-O-21 | O | ON |  |  | 0 |  | 2P 30A | #11 | 철거가능 | KG이니시스 | #12 | 2P 30A |  |  | 2.09 |  | O | ON | B316 (R15)-2
5F-O-22 | O | ON | 0 |  |  |  | 2P 30A | #13 | 철거가능 | KG이니시스 | #14 | 2P 30A | 3.34 |  |  |  | O | ON | B317 (R16)-1
5F-O-23 | O | ON |  | 0 |  |  | 2P 30A | #15 | 철거가능 | KG이니시스 | #16 | 2P 30A |  | 4.4 |  |  | O | ON | B318 (R17)-1
5F-O-24 | O | ON |  |  | 0 |  | 2P 30A | #17 | 철거가능 | KG이니시스 | #18 | 2P 30A |  |  | 5.5 |  | O | ON | B319 (R18)
2B-7-2(2) | O | OFF | 0 |  |  |  | 2P 30A | #19 | ?? | KG이니시스 | #20 | 2P 30A | 1.9 |  |  |  | O | ON | B320 (R19)
2B-5-1 | O | OFF |  | 0 |  |  | 2P 30A | #21 | 보다폰상면 | KG이니시스 | #22 | 2P 30A |  | 5.47 |  |  | O | ON | B321 (R20)
2B-5-2 | O | ON |  |  | 0 |  | 2P 30A | #23 | 보다폰상면 | KG이니시스 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B322 (R21)
2B-5-3 | O | ON | 0 |  |  |  | 2P 30A | #25 | 보다폰상면 | KG이니시스 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B416 (R22)
2B-5-4 | O | ON |  | 0 |  |  | 2P 30A | #27 | 보다폰상면 | KG이니시스 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B417 (R23)
2B-5-5 | O | ON |  |  | 0 |  | 2P 30A | #29 | 철거필요 | KG이니시스 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B418 (R24)
| X | OFF | 0 |  |  |  | 2P 30A | #31 | 철거필요 | KG이니시스 | #32 | 2P 30A | 0.73 |  |  |  | O | ON | B116 (R12)
| X | OFF |  | 0 |  |  | 2P 30A | #33 | 철거필요 | KG이니시스 | #34 | 2P 30A |  | 0.29 |  |  | O | ON | B117 (R11)
| X | OFF |  |  | 0 |  | 2P 30A | #35 | 철거가능 | KG이니시스 | #36 | 2P 30A |  |  | 2.32 |  | O | ON | B118 (R10)
B317 (R16)-2 | O | ON | 5.04 |  |  |  | 2P 30A | #37 | KG이니시스 | KG이니시스 | #38 | 2P 30A | 2.73 |  |  |  | O | ON | B119 (R9)
B318 (R17)-2 | O | ON |  | 2.14 |  |  | 2P 30A | #39 | KG이니시스 | KG이니시스 | #40 | 2P 30A |  | 1.48 |  |  | O | ON | B120 (R8)
B221 (R13)-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | KG이니시스 | KG이니시스 | #42 | 2P 30A |  |  | 1.62 |  | O | ON | B121 (R7)
B222 (R14)-3 | O | ON | 3.41 |  |  |  | 2P 30A | #43 | KG이니시스 | KG이니시스 | #44 | 2P 30A | 2.59 |  |  |  | O | ON | B122 (R6)
B316 (R15)-3 | O | ON |  | 0 |  |  | 2P 30A | #45 | KG이니시스 | KG이니시스 | #46 | 2P 30A |  | 2.53 |  |  | O | ON | B216 (R5)
B219 (R2) | O | ON |  |  | 4.78 |  | 2P 30A | #47 | KG이니시스 | KG이니시스 | #48 | 2P 30A |  |  | 3.54 |  | O | ON | B217 (R4)
B220 (R1) | O | ON | 5.86 |  |  |  | 2P 30A | #49 | KG이니시스 | KG이니시스 | #50 | 2P 30A | 4.43 |  |  |  | O | ON | B218 (R3)
[12 empty] | 합계: | 32.11 | 20.77 | 20.58
PDU6B-1T |  | PDU : | [6 empty] | Main CB 4P 150A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A |  |  |  |  | X | OFF
1T-1-3 | O | OFF |  |  |  |  | 3P 30A | #03 | CF상면 | . | #04 | 3P 30A |  |  |  |  | O | OFF | 1T-4-3
1T-1-6 | O | OFF |  |  |  |  | 3P 30A | #05 | CF상면 | . | #06 | 3P 30A |  |  |  |  | O | OFF | 1T-4-6
1T-1A9 | O | OFF |  |  |  |  | 3P 30A | #07 | . | . | #08 | 3P 30A |  |  |  |  | O | OFF | 1T-4-9
1T-1-12 | O | OFF |  |  |  |  | 3P 30A | #09 | Google상면 | . | #10 | 3P 30A |  |  |  |  | O | OFF | 1T-4-12
1T-2-3 | O | OFF |  |  |  |  | 3P 30A | #11 | CF상면 | . | #12 | 3P 20A |  |  |  |  | O | OFF | 1T-5-3
1T-2-6 | O | OFF |  |  |  |  | 3P 20A | #13 | . | . | #14 | 3P 20A |  |  |  |  | O | OFF | 1T-5-6
1T-2-9 | O | OFF |  |  |  |  | 3P 20A | #15 | . | . | #16 | 3P 20A |  |  |  |  | O | OFF | 1T-5-9
1T-2-12 | O | OFF |  |  |  |  | 3P 20A | #17 | Google상면 | . | #18 | 3P 20A |  |  |  |  | O | OFF | 1T-5-12
1T-3-3 | O | OFF |  |  |  |  | 3P 20A | #19 | . | . | #20 | 3P 20A |  |  |  |  | O | OFF | 1T-6-2
1T-3-6 | O | OFF |  |  |  |  | 3P 20A | #21 | . | . | #22 | 3P 20A |  |  |  |  | O | OFF | 1T-6-4
1T-3-9 | O | OFF |  |  |  |  | 3P 20A | #23 | . | . | #24 | 3P 20A |  |  |  |  | X | OFF
1T-3-12 | O | OFF |  |  |  |  | 3P 20A | #25 | . | . | #26 | 3P 20A |  |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-05 |  | PDU : SEL1 - 5-1 - A3 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  | 0 |  | 2P 30A | #01 |  |  | #02 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #03 |  |  | #04 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #13 |  |  | #14 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #19 |  |  | #20 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-2
| X | OFF |  | 0 |  |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-3
| X | OFF |  |  | 0 |  | 2P 30A | #25 |  |  | #26 | 2P 30A |  |  | 0 |  | O | OFF | 3A-12-3T
| X | OFF | 0 |  |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-4
| X | OFF |  | 0 |  |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-5
| X | OFF |  |  | 0 |  | 2P 30A | #31 |  |  | #32 | 2P 30A |  |  | 0 |  | O | OFF | 3A-12-6
| X | OFF | 0 |  |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-7
| X | OFF |  | 0 |  |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-8
| X | OFF |  |  | 0 |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #43 |  |  | #44 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-06 |  | PDU : SEL1 - 5-1 - B3 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  | 0 |  | 2P 30A | #01 |  |  | #02 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #03 |  |  | #04 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #13 |  |  | #14 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #19 |  |  | #20 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A | 0 |  |  |  | O | OFF | 3B-12-2
| X | OFF |  | 0 |  |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  | 0 |  |  | O | OFF | 3B-12-3
| X | OFF |  |  | 0 |  | 2P 30A | #25 |  |  | #26 | 2P 30A |  |  | 0 |  | O | OFF | 3B-12-4
| X | OFF | 0 |  |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A | 0 |  |  |  | O | OFF | 3B-12-5
| X | OFF |  | 0 |  |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  | 0 |  |  | O | OFF | 3B-12-6
| X | OFF |  |  | 0 |  | 2P 30A | #31 |  |  | #32 | 2P 30A |  |  | 3.59 |  | O | OFF | 3B-12-6T
| X | OFF | 0 |  |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A | 3.61 |  |  |  | O | OFF | 3B-12-7
| X | OFF |  | 0 |  |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  | 3.46 |  |  | O | OFF | 3B-12-8
| X | OFF |  |  | 0.22 |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  |  | 5.37 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A | 5.22 |  |  |  | X | OFF
| X | OFF |  | 0.21 |  |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  | 5.68 |  |  | X | OFF
| X | OFF |  |  | 0.3 |  | 2P 30A | #43 |  |  | #44 | 2P 30A |  |  | 7.91 |  | X | OFF
| X | OFF | 0.3 |  |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A | 0.5 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  | 0.54 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  |  | 0.84 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A | 0.74 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  | 0.75 |  |  | X | OFF
[12 empty] | 합계: | 10.37 | 10.64 | 18.23
5-DaHall 1-PDU-07 |  | PDU : SEL1 - 5-1 - A4 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 8.6 | 1.1 | 0.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
9A-1-5 (PCCW) /5F-A-14 | O | ON | 7.93 |  |  |  | 3P 30A | #01 | PCCW | 센츄리링크코리아 | #02 | 3P 30A | 1.32 |  |  |  | O | ON | 9A-1-8 / 5F-A-17
9A-1-6 / 5F-A-15 | O | ON |  | 1.44 |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A |  | 0 |  |  | O | ON | 9A-1-9 / 5F-A-18
9A-1-7 / 5F-A-16 | O | ON |  |  | 0.4 |  | 3P 30A | #05 | PCCW | 세종 인터넷(IES.YSM.S51) | #06 | 3P 30A |  |  | 0.4 |  | O | ON | 9A-1-10 / 5F-A-19
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #09 |  |  | #10 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 1.07 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0.44 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 10.32 | 1.88 | 0.8
5-DaHall 1-PDU-09 |  | PDU : SEL1 - 5-1 - A5 | [6 empty] | Main CB 4P 200A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #03 |  |  | #04 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #09 |  |  | #10 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #37 |  |  | #38 | 3P 20A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-08 |  | PDU : SEL1 - 5-1 - B4 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 6.5 | 1.4 | 1.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01 | 코로케션 | 센츄리링크코리아 | #02 | 3P 30A | 1.54 |  |  |  | O | ON | 9B-1-8 / 5F-A-17
9B-1-6 / 5F-A-15 | O | ON |  | 1.55 |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A |  | 5.49 |  |  | O | ON | 9B-1-9 / 5F-A-18
9B-1-7 / 5F-A-16 | O | ON |  |  | 0 |  | 3P 30A | #05 | PCCW | 세종 인터넷(IES.YSM.S51) | #06 | 3P 30A |  |  | 1.39 |  | O | ON | 9B-1-10 / 5F-A-19
9B-1-5 (PCCW)/5F-A-14 | O | ON | 5.49 |  |  |  | 3P 30A | #07 | PCCW |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #09 |  |  | #10 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 1.25 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 1.39 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| O | ON |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 8.28 | 8.43 | 1.39
5-DaHall 1-PDU-10 |  | PDU : SEL1 - 5-1 - B5 | [6 empty] | Main CB 4P 200A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #03 |  |  | #04 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #09 |  |  | #10 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #37 |  |  | #38 | 3P 20A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-11 |  | PDU : SEL1 - 5-1 - A6 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 15.3 | 10.2 | 9.9 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
1A-1-1 / 5F-A-10 | O | ON | 0 |  |  |  | 3P 30A | #03 | 코로케션 |  | #04 | 3P 30A | 0 |  |  |  | O | OFF | A1-3-2
1A-1-2 / 5F-A-11 | O | ON |  | 5.31 |  |  | 3P 30A | #05 | 코로케션 | 코로케션 | #06 | 3P 30A |  | 2.01 |  |  | O | ON | A1-3-3
1A-1-2(2) | O | ON |  |  | 2 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 20A |  |  | 0 |  | O | ON | A1-3-4
1A-1-3 / 5F-A-12 | O | ON | 5.29 |  |  |  | 3P 30A | #09 | PCCW | 코로케션 | #10 | 3P 20A | 0 |  |  |  | O | ON | A1-3-5
1A-1-4 / 5F-A-13 | O | ON |  | 2.69 |  |  | 3P 30A | #11 | PCCW | 코로케션 | #12 | 3P 20A |  | 5.7 |  |  | O | ON | A1-3-6
1A-1-4(2) / 5F-A-13 (2) | O | ON |  |  | 1.99 |  | 3P 30A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 2.76 |  | O | ON | A1-3-7
A1-2-1 / 5F-B-10 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 0 |  |  |  | O | ON | A1-3-8
A1-2-2 / 5F-B-11 | O | ON |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 3.54 |  |  | O | ON | A1-3-9
A1-2-3 / 5F-B-12 | O | OFF |  |  | 2.02 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 3.36 |  | O | ON | A1-3-10
A1-2-4 / 5F-B-13 | O | ON | 2.68 |  |  |  | 3P 20A | #21 | 다코스 |  | #22 | 3P 20A | 0 |  |  |  | O | ON | A807 / 5F-D-16 / A1-4-7(2)
A1-2-5 / A605 (A) | O | ON |  | 5.71 |  |  | 3P 20A | #23 | 이비즈네트웍스 | PCCW | #24 | 3P 20A |  | 0 |  |  | O | ON | A1-5-10(2) / 5F-E-19
A1-2-6 / 5F-B-15 | O | ON |  |  | 3.61 |  | 3P 20A | #25 | 다코스 & NTT | PCCW | #26 | 3P 20A |  |  | 5.53 |  | O | ON | A1-1-3(2) / 5F-A-12(2)
A1-2-7 / 5F-B-16 | O | ON | 2.69 |  |  |  | 3P 20A | #27 | 제우스네트웍스 |  | #28 | 3P 20A | 5.62 |  |  |  | O | ON | A1-1-8(2) / 5F-A-17 (2)
A1-2-8 / 5F-B-17 | O | ON |  | 5.55 |  |  | 3P 20A | #29 | COLT |  | #30 | 3P 20A |  | 5.73 |  |  | O | ON | 5F-D-18 임시
A1-3-1 | O | OFF |  |  | 0 |  | 3P 20A | #31 |  | 코로케션 | #32 | 3P 20A |  |  | 0 |  | O | ON
[12 empty] | 합계: | 16.28 | 36.24 | 21.27
5-DaHall 1-PDU-13 |  | PDU : SEL1 - 5-1 - A7 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 12 | 18.7 | 14.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
A2-2-9 / 5F-B-18 | O | ON | 6.43 |  |  |  | 3P 30A | #03 | 코로케션 | 코로케션 | #04 | 3P 30A | 0 |  |  |  | O | ON | A2-5-4
A2-2-10 / 5F-B-19 | O | ON |  | 3.98 |  |  | 3P 30A | #05 | PCCW | 코로케션 | #06 | 3P 30A |  | 6.32 |  |  | O | ON | A2-5-5
A2-4-1 | O | ON |  |  | 0.73 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 4.67 |  | O | ON | A2-5-6
A2-4-2 | O | ON | 0 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 30A | 5.99 |  |  |  | O | ON | A2-5-7
A2-4-3 | O | ON |  | 3.32 |  |  | 3P 20A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 10.08 |  |  | O | ON | A2-5-8
A2-4-4 | O | ON |  |  | 2.6 |  | 3P 20A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 0 |  | O | ON | A2-5-9
A2-4-5 / 5F-D-14 | O | ON | 0 |  |  |  | 3P 20A | #15 | PCCW | PCCW | #16 | 3P 20A | 3.95 |  |  |  | O | ON | A2-5-10 / 5F-E-19
A2-4-6 / 5F-D-15 | O | ON |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 0 |  |  | O | OFF | A2-6-1
A2-4-7 | O | ON |  |  | 6.36 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 4.4 |  | O | OFF | A2-6-2
A2-4-8 | O | ON | 3.33 |  |  |  | 3P 20A | #21 | 코로케션 | 코로케션 | #22 | 3P 20A | 0 |  |  |  | O | OFF | A2-6-3
A2-4-9 | O | ON |  | 10.11 |  |  | 3P 20A | #23 | 코로케션 | 코로케션 | #24 | 3P 20A |  | 3.96 |  |  | O | OFF | A2-6-4
A2-4-10 | O | ON |  |  | 2.57 |  | 3P 20A | #25 | 코로케션 | 코로케션 | #26 | 3P 20A |  |  | 2.1 |  | O | ON | A2-6-5 / F-14
A2-5-1 | O | ON | 0 |  |  |  | 3P 20A | #27 | 코로케션 | 코로케션 | #28 | 3P 20A | 0 |  |  |  | O | OFF | A2-6-6 / F-15
A2-5-2 | O | ON |  | 2.05 |  |  | 3P 20A | #29 | 코로케션 | 코로케션 | #30 | 3P 20A |  | 0 |  |  | O | OFF | A2-6-7 / F-16
A2-5-3 | O | ON |  |  | 0 |  | 3P 20A | #31 | 코로케션 | 코로케션 | #32 | 3P 20A |  |  | 0 |  | O | ON | A2-6-8 / F-17
[12 empty] | 합계: | 19.7 | 39.82 | 23.43
5-DaHall 1-PDU-15 |  | PDU : SEL1 - 5-1 - A8 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 19.1 | 6.2 | 14.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
AC PDU-3#A | O | ON | 6.1 | 1.29 | 8.28 |  | 3P 50A | #01(3상) | 텔스트라 | 텔스트라 | #02(3상) | 3P 50A | 3.43 | 2.84 | 6.34 |  | O | ON | TO:PDU(A)-3A
| X | OFF | 0 | 0 | 0 |  | 3P 50A | #03(3상) |  | Singtel-1 | #04(3상) | 3P 50A | 0 | 0 | 0 |  | X | OFF | DC정류기A
TRANSDUSER | O | OFF | 0 | 0 | 0 |  | 3P 30A | #05(3상) |  |  | #06(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF | customer con
PUD(A)-3-07 / 5F-B-17 (2) | O | ON | 3.98 |  |  |  | 3P 30A | #07 | COLT |  | #08 | 3P 30A | 4.36 |  |  |  | O | ON | A1007 / 5F-F-16
PUD(A)-3-09 / 5F-B-17 (3) | O | ON |  | 1.77 |  |  | 3P 30A | #09 | COLT |  | #10 | 3P 30A |  | 9.05 |  |  | O | OFF | A1006 / 5F-F-15
A603 / Colt, A-1 (23/08/23 On) | O | ON |  |  | 0.22 |  | 3P 30A | #11 |  | CMI | #12 | 3P 30A |  |  | 2.37 |  | O | ON | D-15랙(CMI)-A ('21.09.29 투입)
P여(A)-3 싱텔 SKB CWDM A전원 | O | ON | 0.78 |  |  |  | 3P 30A | #13 |  |  | #14 | 3P 30A | 1.6 |  |  |  | O | ON | A603 / Colt, 정류기A (23/08/23 On)
PUD(A)-2-15 | X | OFF |  | 0.37 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 8.38 |  |  | X | OFF
PUD(A)-2-17 | X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
PUD(A)-2-19 | X | OFF | 4.37 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 7.49 |  |  |  | X | OFF
PUD(A)-2-21 | X | OFF |  | 2.34 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 1.59 |  |  | X | OFF
PUD(A)-2-23 | O | ON |  |  | 2.34 |  | 3P 20A | #23 | Singtel-2 |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
DACOM EOS | X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
PUD(A)-2-27 | X | OFF |  | 0 |  |  | 3P 20A | #27 |  | 다코스 & NTT | #28 | 3P 20A |  | 0.72 |  |  | O | ON | A3-2-6(2) / 5F-B-15 (2)
PUD(A)-2-29 | O | ON |  |  | 0.72 |  | 3P 20A | #29 | Singtel-2 |  | #30 | 3P 20A |  |  | 0 |  | X | OFF | TNSI A
[12 empty] | 합계: | 32.11 | 28.35 | 20.27
5-DaHall 1-PDU-12 |  | PDU : SEL1 - 5-1 - B6 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 20.1 | 13.1 | 14 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
1B-1-1 / 5F-A-10 | O | ON | 0 |  |  |  | 3P 30A | #03 | 코로케션 | 코로케션 | #04 | 3P 30A | 1.92 |  |  |  | O | ON | B1-3-3
1B-1-2 / 5F-A-11 | O | ON |  | 2.98 |  |  | 3P 30A | #05 | PCCW | 코로케션 | #06 | 3P 30A |  | 0 |  |  | O | ON | B1-3-4
| X | OFF |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 0 |  | O | ON | B1-3-5
1B-1-4 / 5F-A-13 | O | ON | 2.96 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 20A | 3.15 |  |  |  | O | ON | B1-3-6
1B-1-4(2) / 5F-A-13 (2) | O | ON |  | 5.49 |  |  | 3P 30A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | B1-3-7
B1-2-1 / 5F-B-10 | O | ON |  |  | 3.64 |  | 3P 20A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 0 |  | O | ON | B1-3-8
B1-2-2 / 5F-B-11 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 6.66 |  |  |  | O | ON | B1-3-9
B1-2-3 / 5F-B-12 | O | OFF |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 3.55 |  |  | O | ON | B1-3-10
B1-2-4 / 5F-B-13 | O | ON |  |  | 3.07 |  | 3P 20A | #19 | 다코스 |  | #20 | 3P 20A |  |  | 0 |  | X | OFF
B1-2-5 / A605 (B) | O | ON | 5.36 |  |  |  | 3P 20A | #21 | 이비즈네트웍스 |  | #22 | 3P 20A | 0 |  |  |  | X | OFF | A807 / 5F-D-16 / B1-4-7(2)
B1-2-6 / 5F-B-15 | O | ON |  | 0 |  |  | 3P 20A | #23 | 다코스 & NTT | PCCW | #24 | 3P 20A |  | 6.74 |  |  | O | ON | B1-5-10(2) / 5F-E-19
B1-2-7 / 5F-B-16 | O | ON |  |  | 3.54 |  | 3P 20A | #25 | 제우스네트웍스 | PCCW | #26 | 3P 20A |  |  | 5.03 |  | O | ON | 1B-1-3 / 5F-A-12
B1-2-8 / 5F-B-17 | O | ON | 0 |  |  |  | 3P 20A | #27 | COLT |  | #28 | 3P 20A | 6 |  |  |  | O | ON | B1-1-8(2) / 5F-A-17 (2)
B1-3-1 | O | ON |  | 5.05 |  |  | 3P 20A | #29 | 코로케션 | PCCW | #30 | 3P 20A |  | 6.54 |  |  | X | ON | B1-1-3(2) / 5F-A-12 (2)
B1-3-2 | O | OFF |  |  | 6.57 |  | 3P 20A | #31 | 코로케션 | 코로케션 | #32 | 3P 20A |  |  | 3.48 |  | O | ON | B1-2-9 / 5F-B-18
[12 empty] | 합계: | 26.05 | 30.35 | 25.33
5-DaHall 1-PDU-14 |  | PDU : SEL1 - 5-1 - B7 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 13.4 | 11.6 | 7.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
B2-2-10 / 5F-B-19 | O | ON | 3.28 |  |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A | 7.85 |  |  |  | O | ON | B2-5-5
B2-4-1 | O | ON |  | 0 |  |  | 3P 30A | #05 | 코로케션 | 코로케션 | #06 | 3P 30A |  | 3.16 |  |  | O | ON | B2-5-6
B2-4-2 | O | ON |  |  | 1.83 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 0 |  | O | ON | B2-5-7
B2-4-3 | O | OFF | 1.07 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 30A | 2.69 |  |  |  | O | ON | B2-5-8
B2-4-4 | O | ON |  | 3.6 |  |  | 3P 20A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 2.67 |  |  | O | ON | B2-5-9
B2-4-5 / 5F-D-14 | O | ON |  |  | 1.83 |  | 3P 20A | #13 | PCCW | PCCW | #14 | 3P 20A |  |  | 3.24 |  | O | ON | B2-5-10 / 5F-E-19
B2-4-6 / 5F-D-15 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 0 |  |  |  | O | OFF | B2-6-1
B2-4-7 | O | ON |  | 1.07 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 7.93 |  |  | O | OFF | B2-6-2
B2-4-8 | O | ON |  |  | 3.15 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 0 |  | O | OFF | B2-6-3
B2-4-9 | O | ON | 3.58 |  |  |  | 3P 20A | #21 | 코로케션 | 코로케션 | #22 | 3P 20A | 0 |  |  |  | O | OFF | B2-6-4
B2-4-10 | O | ON |  | 3.25 |  |  | 3P 20A | #23 | 코로케션 | 코로케션 | #24 | 3P 20A |  | 5.7 |  |  | O | ON | B2-6-5 / F-14
B2-5-1 | O | ON |  |  | 0 |  | 3P 20A | #25 | 코로케션 | 코로케션 | #26 | 3P 20A |  |  | 0 |  | O | OFF | B2-6-6 / F-15
B2-5-2 | O | ON | 0 |  |  |  | 3P 20A | #27 | 코로케션 | 코로케션 | #28 | 3P 20A | 5.56 |  |  |  | O | OFF | B2-6-7 / F-16
B2-5-3 | O | ON |  | 0 |  |  | 3P 20A | #29 | 코로케션 | 코로케션 | #30 | 3P 20A |  | 1.21 |  |  | O | ON | B2-6-8 / F-17
B2-5-4 | O | ON |  |  | 0 |  | 3P 20A | #31 | 코로케션 |  | #32 | 3P 20A |  |  | 1.25 |  | O | ON | FMS 5층 메인전원
[12 empty] | 합계: | 24.03 | 28.59 | 11.3
5-DaHall 1-PDU-16 |  | PDU : SEL1 - 5-1 - B8 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 20.1 | 11.1 | 16 | <- 실측값 |  |  | <- 디스플래이값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
AC PDU-3#B | O | ON | 4.77 | 1.37 | 6.16 |  | 3P 50A | #01(3상) | 텔스트라 | 텔스트라 | #02(3상) | 3P 50A | 3.19 | 3.18 | 2.06 |  | O | ON | TO:PDU(B)-3A
| X | OFF | 0 | 0 | 0 |  | 3P 50A | #03(3상) |  | Singtel-1 | #04(3상) | 3P 50A | 0 | 0 | 0 |  | X | OFF | DC정류기B
TRANSDUSER | X | OFF | 0 | 0 | 0 |  | 3P 30A | #05(3상) |  |  | #06(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF | customer con
PUD(B)-3-07 / 5F-B-17 (2) | O | ON | 4.18 |  |  |  | 3P 30A | #07 | COLT |  | #08 | 3P 30A | 5.18 |  |  |  | O | ON | A1007 / 5F-F-16
PUD(B)-3-09 / 5F-B-17 (3) | O | ON |  | 3.73 |  |  | 3P 30A | #09 | COLT |  | #10 | 3P 30A |  | 1.02 |  |  | X | OFF | A1006 / 5F-F-15
A603 / Colt, B-1 (23/08/23 On) | O | ON |  |  | 0.73 |  | 3P 30A | #11 |  | CMI | #12 | 3P 30A |  |  | 2.63 |  | O | ON | D-15랙(CMI)-B ('21.09.29 투입)
P여(B)-3 싱텔 SKB CWDM B전원 | O | ON | 1.63 |  |  |  | 3P 30A | #13 |  |  | #14 | 3P 30A | 1.74 |  |  |  | O | ON | A603 / Colt, 정류기B (23/08/23 On)
KT Rack #2 (소형 임시정류기) | O | ON |  | 2.46 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 8.25 |  |  | X | OFF
KT Rack #3 (소형 임시정류기) | O | ON |  |  | 1.6 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
KT Rack #4 (소형 임시정류기) | O | ON | 4.91 |  |  |  | 3P 20A | #19 |  | 4F BMS | #20 | 3P 20A | 1.03 |  |  |  | O | ON | 신규 BMS(4F TPS실) Rack
텔스트라 CCTV 모니터링PC 및 시스템 박스 | O | ON |  | 2.6 |  |  | 3P 20A | #21 |  | 5F BMS | #22 | 3P 20A |  | 1.73 |  |  | O | ON | 신규 BMS(5F TPS실) Rack
DACOM EOS | O | ON |  |  | 0 |  | 3P 20A | #23 | Singtel-2 | Singtel-2 | #24 | 3P 20A |  |  | 1.54 |  | O | ON | kt mspp 전원
| O | ON | 0.61 |  |  |  | 3P 20A | #25 | Singtel-2 |  | #26 | 3P 20A | 0.61 |  |  |  | X | OFF
SKB2.5G전용 PDU B3 27 | O | ON |  | 3.69 |  |  | 3P 20A | #27 | Singtel-2 | 다코스 & NTT | #28 | 3P 20A |  | 0.31 |  |  | O | ON | B3-2-6(2) / 5F-B-15 (2)
데이콤 AC전원 | O | ON |  |  | 2.23 |  | 3P 20A | #29 | Singtel-2 | Singtel-2 | #30 | 3P 20A |  |  | 0.53 |  | O | ON | TNSI A
[12 empty] | 합계: | 27.85 | 28.34 | 17.48
PDU(C) | [8 empty] | Main CB 4P 50A
[12 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  |  |  | 3P 50A | #01(3상) |  |  | #02(3상) | 3P 50A |  |  |  |  | X | OFF
라우터룸 System box | O | ON |  |  |  |  | 3P 30A | #03(3상) | Singtel-2 |  | #04(3상) | 3P 30A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  |  |  | X | OFF
SYSTEM BOX | X | OFF |  |  |  |  | 3P 30A | #07 |  | Singtel-2 | #08 | 3P 30A |  |  |  |  | O | ON | SYSTEM BOX
customer con | X | OFF |  |  |  |  | 3P 20A | #09 |  | Singtel-2 | #10 | 3P 20A |  |  |  |  | O | ON | SYSTEM BOX
SYSTEM BOX | O | ON |  |  |  |  | 3P 20A | #11 | Singtel-2 |  | #12 | 3P 20A |  |  |  |  | X | OFF | customer con
| O | OFF |  |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A |  |  |  |  | X | OFF | customer con
M/S 단파 | O | ON |  |  |  |  | 3P 20A | #15 | Singtel-2 |  | #16 | 3P 20A |  |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-17 |  | PDU : SEL1 - 5-1 - A9 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 5.5 | 7.2 | 2.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RT-07 | ○ | ON | 0.76 |  |  |  | 2P 30A | #01 | U08-A-01 | U08-A-02 | #02 | 2P 30A | 0.85 |  |  |  | ○ | ON | RT-08
RT-09 | ○ | ON |  | 0 |  |  | 2P 30A | #03 | U08-A-03 | U08-A-04 | #04 | 2P 30A |  | 0 |  |  | ○ | ON | RT-10
RT-11 | ○ | ON |  |  | 7.31 |  | 2P 30A | #05 | U08-A-05 | U08-A-06 | #06 | 2P 30A |  |  | 0.54 |  | ○ | ON | RT-12
RT-13 | ○ | ON | 0 |  |  |  | 2P 30A | #07 | U08-A-07 | U08-A-08 | #08 | 2P 30A | 2.45 |  |  |  | ○ | ON | RT-14
RT-15 | ○ | ON |  | 7.31 |  |  | 2P 30A | #09 | U08-A-09 | U08-A-10 | #10 | 2P 30A |  | 0 |  |  | ○ | ON | RT-16
RT-17 | ○ | ON |  |  | 0.55 |  | 2P 30A | #11 | U08-A-11 | U08-A-12 | #12 | 2P 30A |  |  | 1.15 |  | ○ | ON | RT-18
RT-19 | ○ | ON | 1.84 |  |  |  | 2P 30A | #13 | U08-A-13 | U08-A-14 | #14 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-01
LSP-02 | ○ | OFF |  | 0 |  |  | 2P 30A | #15 | U08-A-15 | U08-A-16 | #16 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-03
LSP-04 | ○ | ON |  |  | 0.8 |  | 2P 30A | #17 | U08-A-17 | U08-A-18 | #18 | 2P 30A |  |  | 0.85 |  | ○ | OFF | LSP-05
LSP-06 | ○ | OFF | 0 |  |  |  | 2P 30A | #19 | U08-A-19 | U08-A-20 | #20 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-07
LSP-08 | ○ | OFF |  | 2.45 |  |  | 2P 30A | #21 | U08-A-21 | U08-A-22 | #22 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-09
LSP-10 | ○ | OFF |  |  | 1.15 |  | 2P 30A | #23 | U08-A-23 | U08-A-24 | #24 | 2P 30A |  |  | 0 |  | ○ | ON | MT-06
RT-08 정류기 | ○ | ON | 1.84 |  |  |  | 2P 30A | #25 | U08-A-25 |  | #26 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 7.74 | 9.76 | 12.35
5-DaHall 1-PDU-18 |  | PDU : SEL1 - 5-1 - B9 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 4.6 | 5 | 1.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RT-07 | ○ | ON | 1.12 |  |  |  | 2P 30A | #01 | U08-B-01 | U08-B-02 | #02 | 2P 30A | 0.79 |  |  |  | ○ | ON | RT-08
RT-09 | ○ | ON |  | 0 |  |  | 2P 30A | #03 | U08-B-03 | U08-B-04 | #04 | 2P 30A |  | 0 |  |  | ○ | ON | RT-10
RT-11 | ○ | ON |  |  | 5 |  | 2P 30A | #05 | U08-B-05 | U08-B-06 | #06 | 2P 30A |  |  | 0.42 |  | ○ | ON | RT-12
RT-13 | ○ | ON | 0 |  |  |  | 2P 30A | #07 | U08-B-07 | U08-B-08 | #08 | 2P 30A | 2.3 |  |  |  | ○ | ON | RT-14
RT-15 | ○ | ON |  | 5.02 |  |  | 2P 30A | #09 | U08-B-09 | U08-B-10 | #10 | 2P 30A |  | 0 |  |  | ○ | ON | RT-16
RT-17 | ○ | ON |  |  | 0.42 |  | 2P 30A | #11 | U08-B-11 | U08-B-12 | #12 | 2P 30A |  |  | 1.08 |  | ○ | ON | RT-18
RT-19 | ○ | ON | 1.01 |  |  |  | 2P 30A | #13 | U08-B-13 | U08-B-14 | #14 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-01
LSP-02 | ○ | OFF |  | 0 |  |  | 2P 30A | #15 | U08-B-15 | U08-B-16 | #16 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-03
LSP-04 | ○ | OFF |  |  | 0 |  | 2P 30A | #17 | U08-B-17 | U08-B-18 | #18 | 2P 30A |  |  | 0.8 |  | ○ | OFF | LSP-05
LSP-06 | ○ | OFF | 0 |  |  |  | 2P 30A | #19 | U08-B-19 | U08-B-20 | #20 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-07
LSP-08 | ○ | OFF |  | 2.32 |  |  | 2P 30A | #21 | U08-B-21 | U08-B-22 | #22 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-09
LSP-10 | ○ | OFF |  |  | 1.07 |  | 2P 30A | #23 | U08-B-23 | U08-B-24 | #24 | 2P 30A |  |  | 0 |  | ○ | ON | 시로코팬
RT-08 정류기 | ○ | ON | 1.02 |  |  |  | 2P 30A | #25 | U08-B-25 |  | #26 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 6.24 | 7.34 | 8.79
5-DaHall 1-PDU-19 |  | PDU : SEL1 - 5-1 - A10 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 35.1 | 38.9 | 22.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-1 | ○ | ON | 9.4 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 8.6 |  |  |  | ○ | ON | RTX Rack#8, R3-1-1
RTX Rack#2, R1-2-1 | ○ | ON |  | 7.55 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 9.47 |  |  | ○ | ON | RTX Rack#9, R3-2-1
RTX Rack#3, R1-3-1 | ○ | ON |  |  | 8.62 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 5.56 |  | ○ | ON | NW/Mgmt Rack, R3-3-1
RTX Rack#4, R2-1-1 | ○ | ON | 10.37 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 10.83 |  |  |  | ○ | ON | A40 Rack#1, R4-1-1
RTX Rack#5, R2-2-1 | ○ | ON |  | 9.94 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 8.24 |  |  | ○ | ON | A40 Rack#2, R4-2-1
RTX Rack#6, R2-3-1 | ○ | ON |  |  | 13.25 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 4.7 |  | ○ | ON | NetApp FAS#1, R4-3-1
RTX Rack#7, R2-4-1 | ○ | ON | 12.45 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 3.11 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-1
DGX Rack#1, R5-1-1 | ○ | ON |  | 10.73 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 14.87 |  |  | ○ | OFF | 예비Rack#1, R6-1-1
DGX Rack#2, R5-2-1 | ○ | ON |  |  | 6.06 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 11.12 |  | ○ | OFF | 예비Rack#2, R6-2-1
DGX Rack#3, R5-3-1 | ○ | ON | 6.15 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 12.03 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-1
| X | OFF |  | 10.29 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 10.5 |  |  | ○ | OFF | 예비Rack#4, R6-4-1
| X | OFF |  |  | 11.63 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 72.94 | 81.59 | 60.94
5-DaHall 1-PDU-20 |  | PDU : SEL1 - 5-1 - B10 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 28.1 | 32.6 | 23.1 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-2 | ○ | ON | 9.39 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 9.55 |  |  |  | ○ | ON | RTX Rack#8, R3-1-2
RTX Rack#2, R1-2-2 | ○ | ON |  | 7.21 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 9.22 |  |  | ○ | ON | RTX Rack#9, R3-2-2
RTX Rack#3, R1-3-2 | ○ | ON |  |  | 8.53 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 4.71 |  | ○ | ON | NW/Mgmt Rack, R3-3-2
RTX Rack#4, R2-1-2 | ○ | ON | 10.53 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 11.41 |  |  |  | ○ | ON | A40 Rack#1, R4-1-2
RTX Rack#5, R2-2-2 | ○ | ON |  | 9.61 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 8.46 |  |  | ○ | ON | A40 Rack#2, R4-2-2
RTX Rack#6, R2-3-2 | ○ | ON |  |  | 12.9 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 4.64 |  | ○ | ON | NetApp FAS#1, R4-3-2
RTX Rack#7, R2-4-2 | ○ | ON | 11.93 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 3.04 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-2
DGX Rack#1, R5-1-2 | ○ | ON |  | 11.38 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 15.05 |  |  | ○ | OFF | 예비Rack#1, R6-1-2
DGX Rack#2, R5-2-2 | ○ | ON |  |  | 5.93 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 10.57 |  | ○ | OFF | 예비Rack#2, R6-2-2
DGX Rack#3, R5-3-2 | ○ | ON | 6.55 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 12.25 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-2
| X | OFF |  | 9.97 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 5.87 |  |  | ○ | OFF | 예비Rack#4, R6-4-2
| X | OFF |  |  | 5.96 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 74.65 | 76.77 | 53.24
5-DaHall 1-PDU-21 |  | PDU : SEL1 - 5-1 - A11 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 41.9 | 33.6 | 29.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-3 | ○ | ON | 10.18 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 8.77 |  |  |  | ○ | ON | RTX Rack#8, R3-1-3
RTX Rack#2, R1-2-3 | ○ | ON |  | 8.9 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 6.56 |  |  | ○ | ON | RTX Rack#9, R3-2-3
RTX Rack#3, R1-3-3 | ○ | ON |  |  | 9.09 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 8.58 |  | ○ | ON | NW/Mgmt Rack, R3-3-3
RTX Rack#4, R2-1-3 | ○ | ON | 10.69 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 9.12 |  |  |  | ○ | ON | A40 Rack#1, R4-1-3
RTX Rack#5, R2-2-3 | ○ | ON |  | 10.61 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 11.74 |  |  | ○ | ON | A40 Rack#2, R4-2-3
RTX Rack#6, R2-3-3 | ○ | ON |  |  | 9.63 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 2.9 |  | ○ | ON | NetApp FAS#1, R4-3-3
RTX Rack#7, R2-4-3 | ○ | ON | 12.81 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 3.4 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-3
DGX Rack#1, R5-1-3 | ○ | ON |  | 8.91 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 14.46 |  |  | ○ | OFF | 예비Rack#1, R6-1-3
DGX Rack#2, R5-2-3 | ○ | ON |  |  | 9.81 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 7.45 |  | ○ | OFF | 예비Rack#2, R6-2-3
DGX Rack#3, R5-3-3 | ○ | ON | 5.14 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 11.51 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-3
| X | OFF |  | 9.99 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 9.89 |  |  | ○ | OFF | 예비Rack#4, R6-4-3
| X | OFF |  |  | 11.6 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 71.62 | 81.06 | 59.06
5-DaHall 1-PDU-22 |  | PDU : SEL1 - 5-1 - B11 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 37 | 27.7 | 24 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-4 | ○ | ON | 10.5 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 8.71 |  |  |  | ○ | ON | RTX Rack#8, R3-1-4
RTX Rack#2, R1-2-4 | ○ | ON |  | 8.7 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 5.8 |  |  | ○ | ON | RTX Rack#9, R3-2-4
RTX Rack#3, R1-3-4 | ○ | ON |  |  | 8.58 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 8.87 |  | ○ | ON | NW/Mgmt Rack, R3-3-4
RTX Rack#4, R2-1-4 | ○ | ON | 10.21 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 9.65 |  |  |  | ○ | ON | A40 Rack#1, R4-1-4
RTX Rack#5, R2-2-4 | ○ | ON |  | 10.56 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 12.02 |  |  | ○ | ON | A40 Rack#2, R4-2-4
RTX Rack#6, R2-3-4 | ○ | ON |  |  | 10.01 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 2.98 |  | ○ | ON | NetApp FAS#1, R4-3-4
RTX Rack#7, R2-4-4 | ○ | ON | 13.02 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 3.02 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-4
DGX Rack#1, R5-1-4 | ○ | ON |  | 9.5 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 14.77 |  |  | ○ | OFF | 예비Rack#1, R6-1-4
DGX Rack#2, R5-2-4 | ○ | ON |  |  | 9.32 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 7.27 |  | ○ | OFF | 예비Rack#2, R6-2-4
DGX Rack#3, R5-3-4 | ○ | ON | 5.75 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 11.85 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-4
| X | OFF |  | 9.77 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 5.69 |  |  | ○ | OFF | 예비Rack#4, R6-4-4
| X | OFF |  |  | 8.88 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 72.71 | 76.81 | 55.91
5층 TR룸
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
PDU-8 (A) | O | ON | 5.6 | 7.2 | 2.3 | 3.8 | 3P 200A | #08 | Singtel | Singtel | #08 | 3P 200A | 4.6 | 5 | 1.5 | 2.7 | O | ON | PDU-8 (B)
텔스트라 정류기 A1 | O | ON | 8.4 | 19.2 | 9.2 | 10.7 | 3P 30A | #03 | C2C | C2C | #04 | 3P 30A | 8.6 | 8.4 | 9 | 2.1 | O | ON | 텔스트라 정류기 A2
텔스트라 정류기 B1 | O | ON | 11.2 | 8 | 11.6 | 4 | 3P 30A | #05 | C2C | C2C | #06 | 3P 30A | 11.7 | 11.5 | 11.5 | 1.8 | O | ON | 텔스트라 정류기 B2
|  |  | 사용량 | 배분
| IDC |  | 785.21 | 41.82% | [7 empty] | 5-1-A1 | 39.42 | 43.26 | 31.73
| 텔스트라 |  | 51.61 | 2.749% | [7 empty] | 5-1-B1 | 38.63 | 40.33 | 30.19
| 텔스트라 정류기 |  | 128.3 | 6.833% | [7 empty] | 5-1-A2 | 34.31 | 22.77 | 21.08
| singtel PDU-8-A |  | 29.85 | 1.59% | [7 empty] | 6-1-B2 | 32.11 | 20.77 | 20.58
| singtel PDU-8-B |  | 22.37 | 1.191% | =>합계 | 2.781% | [5 empty] | 5-1-A3 | 0 | 0 | 0
| singtel (기타) |  | 23.04 | 1.227% | [7 empty] | 5-1-B3 | 10.37 | 10.64 | 18.23
| LG CNS |  | 837.3 | 44.59% | [7 empty] | 5-1-A4 | 10.32 | 1.88 | 0.8
함계 | IDC |  | 1877.68 | 100% | [7 empty] | 5-1-B4 | 8.28 | 8.43 | 1.39
[12 empty] | 5-1-A5 | 0 | 0 | 0
[12 empty] | 5-1-B5 | 0 | 0 | 0
[12 empty] | 5-1-A6 | 16.28 | 36.24 | 21.27
[12 empty] | 5-1-B6 | 26.05 | 30.35 | 25.33
[12 empty] | 5-1-A7 | 19.7 | 39.82 | 23.43
| C2C | [10 empty] | 5-1-B7 | 24.03 | 28.59 | 11.3
[12 empty] | 5-1-A8 | 32.11 | 28.35 | 20.27
[12 empty] | 5-1-B8 | 27.85 | 28.34 | 17.48
[12 empty] | 5-1-A9 | 7.74 | 9.76 | 12.35 | 29.85
[12 empty] | 5-1-B9 | 6.24 | 7.34 | 8.79 | 22.37
[12 empty] | 5-1-A10 | 72.94 | 81.59 | 60.94
|  |  |  | 복도 | [7 empty] | 5-1-B10 | 74.65 | 76.77 | 53.24
[12 empty] | 5-1-A11 | 71.62 | 81.06 | 59.06
[12 empty] | 5-1-B11 | 72.71 | 76.81 | 55.91 |  | 837.3
|  |  |  | ▼ | [8 empty] | 625.36 | 673.1 | 493.37 | 1791.83
128.3
1920.13
[5 empty] | Singtel-1 |  | Singtel-2 |  | Pacnet
Note on A226: 이현상: 계약전류 10A/랙 ? 초과시 AM연락 필요! (임영호팀장/장우창M/장태영M)
Note on A274: 이현상: 계약전류 10A/랙 ? 초과시 AM연락 필요 (임영호팀장/장우창M/장태영M)

## 5층_부하량(월간_AVG)
Date : 2023-11-01 ~ 2023-11-30
5-DaHall 1-CEP-05 | [8 empty] | Main CB 4P 350A
[12 empty] | MAIN 계측값 : | 62.2 | 67 | 61.8 | <- 실측값 |  |  | -1
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
5-DaHall 1-CRAC-16 보조 5F-2호기(구글) | O | ON | 0 | 0 | 0 |  | 4P 50A | #01 | . | . | #02 | 4P 50A | 0 | 0 | 0 |  | O | ON | 5-DaHall 1-CRAC-15 보조 5F-1호기(구글)
5-DaHall 1-CRAC-01 LG CRAC #01 | O | ON | 0.078948 | 0.079611 | 0.078611 |  | 4P 50A | #03 | . | . | #04 | 4P 50A | 18.1523 | 18.2569 | 17.9319 |  | O | ON | 5-DaHall 1-CRAC-02 LG CRAC #02
5-DaHall 1-CRAC-03 LG CRAC #03 | O | ON | 0.14982 | 0.15172 | 0.14853 |  | 4P 50A | #05 | . | . | #06 | 4P 50A | 19.7905 | 19.3812 | 19.7072 |  | O | ON | 5-DaHall 1-CRAC-04 LG CRAC #04
5-DaHall 1-CRAC-05 LG CRAC #05 | O | ON | 14.9237 | 14.9132 | 14.6659 |  | 4P 50A | #07 | . | . | #08 | 4P 50A | 11.6908 | 11.7958 | 11.6839 |  | O | ON | 5-DaHall 1-CRAC-06 LG CRAC #06
5-DaHall 1-CRAC-07 LG CRAC #07 | O | ON | 0.12239 | 0.12429 | 0.12132 |  | 4P 50A | #09 | . | . | #10 | 4P 50A | 0.13355 | 0.13661 | 0.13361 |  | O | ON | 5-DaHall 1-CRAC-08 LG CRAC #08
5-DaHall 1-CRAC-09 LG CRAC #09 | O | ON | 16.2531 | 16.3563 | 16.1459 |  | 4P 50A | #11 | . | . | #12 | 4P 50A | 16.8723 | 16.5479 | 16.899 |  | O | ON | 5-DaHall 1-CRAC-13 CF CRAC #01
spare | X | OFF | 24.7097 |  |  |  | 2P 30A | #13 | . | . | #14 | 2P 30A | 0 |  |  |  | X | OFF | spare
spare | X | OFF |  | 0 |  |  | 2P 30A | #15 | . | . | #16 | 2P 50A |  | 12.8713 |  |  | O | ON | 5-DaHall 1-EH (5층 가습기 Main)
spare | X | OFF |  |  | 12.3129 |  | 2P 30A | #17 | . | . | #18 | 2P 50A |  |  | 9.8507 |  | O | ON | 4-DaHall 1-EH (4층 가습기 Main)
[12 empty] | 합계: | 122.8771 | 110.6148 | 119.6794
5-DaHall 1-CEP-06 | [8 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 0.7 | 0 | 0.7 | <- 실측값
[10 empty] | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
[10 empty] | . | #01 | 4P 60A | 0.24228 | 0.057747 | 0.24644 |  | O | ON | LG CRAC #10 (수냉식)
[10 empty] | . | #02 | 4P 60A | 0.24257 | 0.060039 | 0.24744 |  | O | ON | LG CRAC #11 (수냉식)
[10 empty] | . | #03 | 4P 60A | 0.2434 | 0.063805 | 0.23459 |  | O | ON | LG CRAC #12 (수냉식)
[10 empty] | . | #04 | 4P 60A | 0 | 0 | 0 |  | X | OFF | spare
[12 empty] | 합계: | 0.72824 | 0.18159 | 0.72847
5-DaHall 1-PDU-01 |  | PDU : SEL1 - 5-1 - A1 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 34.6 | 37.8 | 27.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0.58996 | 0.74371 |  | O | ON | 보다폰정류기-A
1A-1-1 | O | ON | 0 |  |  |  | 2P 30A | #01 | CF상면 |  | #02 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-21 / 1A-2-11
1A-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | CF상면 | 구글202-A | #04 | 2P 30A |  | 0 |  |  | O | ON | 1A-2-12
1A-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | CF상면 | 구글201-A | #06 | 2P 30A |  |  | 1.5294 |  | O | ON | 1A-2-13
1A-1-4 | O | OFF | 0 |  |  |  | 2P 30A | #07 | CF상면 |  | #08 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-24 / 1A-2-14
G1101 (1A-1-5) | O | ON |  | 13.8976 |  |  | 2P 30A | #09 | cloudflare | 구글 시스템박스 | #10 | 2P 30A |  | 0 |  |  | O | ON | 1A-2-15
G1102 (1A-1-6) | O | ON |  |  | 11.3149 |  | 2P 30A | #11 | cloudflare | 철거필요 | #12 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-1
G1103 (1A-1-7) | O | ON | 13.7686 |  |  |  | 2P 30A | #13 | cloudflare | 철거필요 | #14 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-2
G1104 (1A-1-8) | O | ON |  | 0 |  |  | 2P 30A | #15 | cloudflare | 철거필요 | #16 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-3
G1105 (1A-1-9) | O | ON |  |  | 0 |  | 2P 30A | #17 | cloudflare | 철거필요 | #18 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-4
1A-1-10 | O | ON | 1.0405 |  |  |  | 2P 30A | #19 | 구글104-A | 철거필요 | #20 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-5
1A-1-11 | O | ON |  | 1.4766 |  |  | 2P 30A | #21 | 구글103-A | 철거필요 | #22 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-6
1A-1-12 | O | ON |  |  | 1.5398 |  | 2P 30A | #23 | 구글102-A | 철거필요 | #24 | 2P 30A |  |  | 0 |  | O | OFF | 1A-3-7
1A-1-13 | O | ON | 0 |  |  |  | 2P 30A | #25 | 구글101-A | 철거필요 | #26 | 2P 30A | 0 |  |  |  | O | OFF | 1A-3-8
1A-1-14 | O | OFF |  | 0 |  |  | 2P 30A | #27 |  | 철거필요 | #28 | 2P 30A |  | 0 |  |  | O | OFF | 1A-3-9
1A-1-15 | O | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | O | OFF | 5F-P-20 / 1A-3-10
G1201 (1A-2-1) | O | ON | 11.0998 |  |  |  | 2P 30A | #31 | cloudflare |  | #32 | 2P 30A | 0 |  |  |  | O | OFF | 5F-P-21 / 1A-3-11
G1202 (1A-2-2) | O | ON |  | 9.9455 |  |  | 2P 30A | #33 | cloudflare |  | #34 | 2P 30A |  | 0 |  |  | O | OFF | 5F-P-22 / 1A-3-12
G1203 (1A-2-3) | O | ON |  |  | 11.6982 |  | 2P 30A | #35 | cloudflare |  | #36 | 2P 30A |  |  | 0 |  | O | OFF | 5F-P-23 / 1A-3-13
G1204 (1A-2-4) | O | ON | 9.5055 |  |  |  | 2P 30A | #37 | cloudflare |  | #38 | 2P 30A | 0 |  |  |  | O | OFF | 5F-P-24 / 1A-3-14
G1205 (1A-2-5) | O | ON |  | 11.8317 |  |  | 2P 30A | #39 | cloudflare | ?? | #40 | 2P 30A |  | 0 |  |  | X | OFF
1A-2-6 | O | OFF |  |  | 0 |  | 2P 30A | #41 | CF상면 | 보다폰 케이지 안쪽 | #42 | 2P 30A |  |  | 0 |  | O | OFF | 1A-4-1
1A-2-7 | O | OFF | 0 |  |  |  | 2P 30A | #43 | CF상면 | 보다폰 케이지 안쪽 | #44 | 2P 30A | 0 |  |  |  | O | OFF | 1A-4-2
1A-2-8 | O | OFF |  | 0 |  |  | 2P 30A | #45 | CF상면 | 보다폰 케이지 안쪽 | #46 | 2P 30A |  | 0.61537 |  |  | O | ON | 1A-4-3
1A-2-9 | O | OFF |  |  | 0 |  | 2P 30A | #47 | CF상면 | Vodafone | #48 | 2P 30A |  |  | 1.7392 |  | O | ON | VF Rack#1-상
5F-Q-20 | O | OFF | 0 |  |  |  | 2P 30A | #49 |  | Vodafone | #50 | 2P 30A | 0 |  |  |  | O | ON | VF Rack#2-상
[12 empty] | 합계: | 35.4144 | 38.3568 | 28.5652
5-DaHall 1-PDU-02 |  | PDU : SEL1 - 5-1 - B1 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 34.6 | 35.2 | 26.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0.66516 | 0.74062 |  | O | ON | 보다폰정류기-B
1B-1-1 | O | OFF | 0 |  |  |  | 2P 30A | #01 | CF상면 |  | #02 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-21 / 1B-2-11
1B-1-2 | O | OFF |  | 0 |  |  | 2P 30A | #03 | CF상면 | 구글202-A | #04 | 2P 30A |  | 0 |  |  | O | ON | 1B-2-12
1B-1-3 | O | OFF |  |  | 0 |  | 2P 30A | #05 | CF상면 | 구글201-A | #06 | 2P 30A |  |  | 1.252 |  | O | ON | 1B-2-13
1B-1-4 | O | OFF | 0 |  |  |  | 2P 30A | #07 | CF상면 |  | #08 | 2P 30A | 0 |  |  |  | O | OFF | 5F-Q-24 / 1B-2-14
G1101 (1B-1-5) | O | ON |  | 11.6589 |  |  | 2P 30A | #09 | cloudflare | 구글Cage 지문인식기 | #10 | 2P 30A |  | 0 |  |  | O | ON | 1B-2-15
G1102 (1B-1-6) | O | ON |  |  | 12.8737 |  | 2P 30A | #11 | cloudflare |  | #12 | 2P 30A |  |  | 0 |  | O | OFF | 1B-3-1
G1103 (1B-1-7) | O | ON | 11.4483 |  |  |  | 2P 30A | #13 | cloudflare |  | #14 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-2
G1104 (1B-1-8) | O | ON |  | 0 |  |  | 2P 30A | #15 | cloudflare |  | #16 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-3
G1105 (1B-1-9) | O | ON |  |  | 0 |  | 2P 30A | #17 | cloudflare |  | #18 | 2P 30A |  |  | 0 |  | O | ON | 1B-3-4
1B-1-10 | O | ON | 0 |  |  |  | 2P 30A | #19 | 구글104-A |  | #20 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-5
1B-1-11 | O | ON |  | 1.6313 |  |  | 2P 30A | #21 | 구글103-A |  | #22 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-6
1B-1-12 | O | ON |  |  | 1.3209 |  | 2P 30A | #23 | 구글102-A |  | #24 | 2P 30A |  |  | 0 |  | O | ON | 1B-3-7
1B-1-13 | O | ON | 0 |  |  |  | 2P 30A | #25 | 구글101-A |  | #26 | 2P 30A | 0 |  |  |  | O | ON | 1B-3-8
1B-1-14 | O | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | O | ON | 1B-3-9
1B-1-15 | O | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | O | ON | 5F-P-20 / 1B-3-10
G1201 (1A-2-1) | O | ON | 11.4642 |  |  |  | 2P 30A | #31 | cloudflare |  | #32 | 2P 30A | 0 |  |  |  | O | ON | 5F-P-21 / 1B-3-11
G1202 (1B-2-2) | O | ON |  | 11.5709 |  |  | 2P 30A | #33 | cloudflare |  | #34 | 2P 30A |  | 0 |  |  | O | ON | 5F-P-22 / 1B-3-12
G1203 (1B-2-3) | O | ON |  |  | 9.7301 |  | 2P 30A | #35 | cloudflare |  | #36 | 2P 30A |  |  | 0 |  | O | ON | 5F-P-23 / 1B-3-13
G1204 (1B-2-4) | O | ON | 11.348 |  |  |  | 2P 30A | #37 | cloudflare |  | #38 | 2P 30A | 0 |  |  |  | O | ON | 5F-P-24 / 1B-3-14
G1205 (1B-2-5) | O | ON |  | 9.5155 |  |  | 2P 30A | #39 | cloudflare |  | #40 | 2P 30A |  | 0 |  |  | O | OFF | 5F-P-25 / 1B-3-15
1B-2-6 | O | OFF |  |  | 0 |  | 2P 30A | #41 | CF상면 | ?? | #42 | 2P 30A |  |  | 0 |  | O | OFF | 1B-7-1(2)
1B-2-7 | O | OFF | 0 |  |  |  | 2P 30A | #43 | CF상면 |  | #44 | 2P 30A | 0 |  |  |  | O | OFF | 1B-4-2
1B-2-8 | O | OFF |  | 0 |  |  | 2P 30A | #45 | CF상면 | 보다폰 케이지 안쪽 | #46 | 2P 30A |  | 0.65748 |  |  | O | ON | 1B-4-3
1B-2-9 | O | OFF |  |  | 0 |  | 2P 30A | #47 | CF상면 | Vodafone | #48 | 2P 30A |  |  | 1.1049 |  | O | ON | VF Rack#1-하
5F-Q-20 | O | OFF | 0 |  |  |  | 2P 30A | #49 |  | Vodafone | #50 | 2P 30A | 0 |  |  |  | O | ON | VF Rack#2-하
[12 empty] | 합계: | 34.2605 | 35.6993 | 27.0223
5-DaHall 1-PDU-03 |  | PDU : SEL1 - 5-1 - A2 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 26.8 | 15.9 | 18 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0 | 0 |  | X | OFF
5F-O-16 / 2A-4-6 | O | ON | 0 |  |  |  | 2P 30A | #01 |  | KG이니시스 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B221 (R13)-1
5F-O-17 / 2A-4-7 | O | ON |  | 0 |  |  | 2P 30A | #03 |  | KG이니시스 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B221 (R13)-2
5F-O-18 | O | ON |  |  | 0 |  | 2P 30A | #05 |  | KG이니시스 | #06 | 2P 30A |  |  | 0.56815 |  | O | ON | B222 (R14)-1
5F-O-19 | O | ON | 0 |  |  |  | 2P 30A | #07 |  | KG이니시스 | #08 | 2P 30A | 1.4133 |  |  |  | O | ON | B222 (R14)-2
5F-O-20 | O | ON |  | 0 |  |  | 2P 30A | #09 |  | KG이니시스 | #10 | 2P 30A |  | 3.5687 |  |  | O | ON | B316 (R15)-1
5F-O-21 | O | ON |  |  | 0 |  | 2P 30A | #11 |  | KG이니시스 | #12 | 2P 30A |  |  | 1.7762 |  | O | ON | B316 (R15)-2
5F-O-22 | O | ON | 0 |  |  |  | 2P 30A | #13 |  | KG이니시스 | #14 | 2P 30A | 0.35629 |  |  |  | O | ON | B317 (R16)-1
5F-O-23 | O | ON |  | 0 |  |  | 2P 30A | #15 |  | KG이니시스 | #16 | 2P 30A |  | 3.8993 |  |  | O | ON | B318 (R17)-1
5F-O-24 | O | ON |  |  | 0 |  | 2P 30A | #17 |  | KG이니시스 | #18 | 2P 30A |  |  | 4.6474 |  | O | ON | B319 (R18)
2A-7-2(2) | X | OFF | 0 |  |  |  | 2P 30A | #19 | ?? | KG이니시스 | #20 | 2P 30A | 2.8041 |  |  |  | O | ON | B320 (R19)
2A-5-1 | O | OFF |  | 0 |  |  | 2P 30A | #21 | 보다폰상면 | KG이니시스 | #22 | 2P 30A |  | 3.3989 |  |  | O | ON | B321 (R20)
2A-5-2 | O | ON |  |  | 0 |  | 2P 30A | #23 | 보다폰상면 | KG이니시스 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B322 (R21)
2A-5-3 | O | ON | 0 |  |  |  | 2P 30A | #25 | 보다폰상면 | KG이니시스 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B416 (R22)
2A-5-4 | O | ON |  | 0 |  |  | 2P 30A | #27 | 보다폰상면 | KG이니시스 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B417 (R23)
2A-5-5 | O | ON |  |  | 0 |  | 2P 30A | #29 |  | KG이니시스 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B418 (R24)
5-1-A2-31 | X | OFF | 0 |  |  |  | 2P 30A | #31 |  | KG이니시스 | #32 | 2P 30A | 2.4898 |  |  |  | O | ON | B116 (R12)
5-1-A2-33 | X | OFF |  | 0 |  |  | 2P 30A | #33 |  | KG이니시스 | #34 | 2P 30A |  | 2.1696 |  |  | O | ON | B117 (R11)
5-1-A2-35 | X | OFF |  |  | 0 |  | 2P 30A | #35 |  | KG이니시스 | #36 | 2P 30A |  |  | 2.17 |  | O | ON | B118 (R10)
B317 (R16)-2 | O | ON | 3.3377 |  |  |  | 2P 30A | #37 | KG이니시스 | KG이니시스 | #38 | 2P 30A | 2.435 |  |  |  | O | ON | B119 (R9)
B318 (R17)-2 | O | ON |  | 1.3727 |  |  | 2P 30A | #39 | KG이니시스 | KG이니시스 | #40 | 2P 30A |  | 1.3683 |  |  | O | ON | B120 (R8)
B221 (R13)-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | KG이니시스 | KG이니시스 | #42 | 2P 30A |  |  | 1.7892 |  | O | ON | B121 (R7)
B222 (R14)-3 | O | ON | 2.4187 |  |  |  | 2P 30A | #43 | KG이니시스 | KG이니시스 | #44 | 2P 30A | 2.9436 |  |  |  | O | ON | B122 (R6)
B316 (R15)-3 | O | ON |  | 0 |  |  | 2P 30A | #45 | KG이니시스 | KG이니시스 | #46 | 2P 30A |  | 2.912 |  |  | O | ON | B216 (R5)
B219 (R2) | O | ON |  |  | 4.0462 |  | 2P 30A | #47 | KG이니시스 | KG이니시스 | #48 | 2P 30A |  |  | 3.7191 |  | O | ON | B217 (R4)
B220 (R1) | O | ON | 5.699 |  |  |  | 2P 30A | #49 | KG이니시스 | KG이니시스 | #50 | 2P 30A | 4.1031 |  |  |  | O | ON | B218 (R3)
[12 empty] | 합계: | 28.0007 | 18.6894 | 18.7163
5-DaHall 1-PDU-04 |  | PDU : SEL1 - 5-1 - B2 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 25.1 | 15.5 | 18.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| O | OFF | 0 | 0 | 0 |  | 3P 60A | #3P-01 |  |  | #3P-02 | 3P 60A | 0 | 0 | 0 |  | O | OFF
5F-O-16 / 2B-4-6 | O | ON | 0 |  |  |  | 2P 30A | #01 | 철거가능 | KG이니시스 | #02 | 2P 30A | 0 |  |  |  | O | OFF | B221 (R13)-1
5F-O-17 / 2B-4-7 | O | ON |  | 0 |  |  | 2P 30A | #03 | 철거가능 | KG이니시스 | #04 | 2P 30A |  | 0 |  |  | O | OFF | B221 (R13)-2
5F-O-18 | O | ON |  |  | 0 |  | 2P 30A | #05 | 철거가능 | KG이니시스 | #06 | 2P 30A |  |  | 0.56831 |  | O | ON | B222 (R14)-1
5F-O-19 | O | ON | 0 |  |  |  | 2P 30A | #07 | 철거가능 | KG이니시스 | #08 | 2P 30A | 1.7195 |  |  |  | O | ON | B222 (R14)-2
5F-O-20 | O | ON |  | 0 |  |  | 2P 30A | #09 | 철거가능 | KG이니시스 | #10 | 2P 30A |  | 3.5462 |  |  | O | ON | B316 (R15)-1
5F-O-21 | O | ON |  |  | 0 |  | 2P 30A | #11 | 철거가능 | KG이니시스 | #12 | 2P 30A |  |  | 1.8162 |  | O | ON | B316 (R15)-2
5F-O-22 | O | ON | 0 |  |  |  | 2P 30A | #13 | 철거가능 | KG이니시스 | #14 | 2P 30A | 0.64036 |  |  |  | O | ON | B317 (R16)-1
5F-O-23 | O | ON |  | 0 |  |  | 2P 30A | #15 | 철거가능 | KG이니시스 | #16 | 2P 30A |  | 3.8896 |  |  | O | ON | B318 (R17)-1
5F-O-24 | O | ON |  |  | 0 |  | 2P 30A | #17 | 철거가능 | KG이니시스 | #18 | 2P 30A |  |  | 4.4966 |  | O | ON | B319 (R18)
2B-7-2(2) | O | OFF | 0 |  |  |  | 2P 30A | #19 | ?? | KG이니시스 | #20 | 2P 30A | 1.8441 |  |  |  | O | ON | B320 (R19)
2B-5-1 | O | OFF |  | 0 |  |  | 2P 30A | #21 | 보다폰상면 | KG이니시스 | #22 | 2P 30A |  | 4.7166 |  |  | O | ON | B321 (R20)
2B-5-2 | O | ON |  |  | 0 |  | 2P 30A | #23 | 보다폰상면 | KG이니시스 | #24 | 2P 30A |  |  | 0 |  | O | OFF | B322 (R21)
2B-5-3 | O | ON | 0 |  |  |  | 2P 30A | #25 | 보다폰상면 | KG이니시스 | #26 | 2P 30A | 0 |  |  |  | O | OFF | B416 (R22)
2B-5-4 | O | ON |  | 0 |  |  | 2P 30A | #27 | 보다폰상면 | KG이니시스 | #28 | 2P 30A |  | 0 |  |  | O | OFF | B417 (R23)
2B-5-5 | O | ON |  |  | 0 |  | 2P 30A | #29 | 철거필요 | KG이니시스 | #30 | 2P 30A |  |  | 0 |  | O | OFF | B418 (R24)
| X | OFF | 0 |  |  |  | 2P 30A | #31 | 철거필요 | KG이니시스 | #32 | 2P 30A | 0.27074 |  |  |  | O | ON | B116 (R12)
| X | OFF |  | 0 |  |  | 2P 30A | #33 | 철거필요 | KG이니시스 | #34 | 2P 30A |  | 0.28991 |  |  | O | ON | B117 (R11)
| X | OFF |  |  | 0 |  | 2P 30A | #35 | 철거가능 | KG이니시스 | #36 | 2P 30A |  |  | 2.2939 |  | O | ON | B118 (R10)
B317 (R16)-2 | O | ON | 3.86 |  |  |  | 2P 30A | #37 | KG이니시스 | KG이니시스 | #38 | 2P 30A | 2.5978 |  |  |  | O | ON | B119 (R9)
B318 (R17)-2 | O | ON |  | 0.91329 |  |  | 2P 30A | #39 | KG이니시스 | KG이니시스 | #40 | 2P 30A |  | 1.4562 |  |  | O | ON | B120 (R8)
B221 (R13)-3 | O | OFF |  |  | 0 |  | 2P 30A | #41 | KG이니시스 | KG이니시스 | #42 | 2P 30A |  |  | 1.5857 |  | O | ON | B121 (R7)
B222 (R14)-3 | O | ON | 2.494 |  |  |  | 2P 30A | #43 | KG이니시스 | KG이니시스 | #44 | 2P 30A | 2.3215 |  |  |  | O | ON | B122 (R6)
B316 (R15)-3 | O | ON |  | 0 |  |  | 2P 30A | #45 | KG이니시스 | KG이니시스 | #46 | 2P 30A |  | 2.3525 |  |  | O | ON | B216 (R5)
B219 (R2) | O | ON |  |  | 4.3953 |  | 2P 30A | #47 | KG이니시스 | KG이니시스 | #48 | 2P 30A |  |  | 3.1823 |  | O | ON | B217 (R4)
B220 (R1) | O | ON | 5.4287 |  |  |  | 2P 30A | #49 | KG이니시스 | KG이니시스 | #50 | 2P 30A | 3.9494 |  |  |  | O | ON | B218 (R3)
[12 empty] | 합계: | 25.1261 | 17.1644 | 18.3382
PDU6B-1T |  | PDU : | [6 empty] | Main CB 4P 150A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A |  |  |  |  | X | OFF
1T-1-3 | O | OFF |  |  |  |  | 3P 30A | #03 | CF상면 | . | #04 | 3P 30A |  |  |  |  | O | OFF | 1T-4-3
1T-1-6 | O | OFF |  |  |  |  | 3P 30A | #05 | CF상면 | . | #06 | 3P 30A |  |  |  |  | O | OFF | 1T-4-6
1T-1A9 | O | OFF |  |  |  |  | 3P 30A | #07 | . | . | #08 | 3P 30A |  |  |  |  | O | OFF | 1T-4-9
1T-1-12 | O | OFF |  |  |  |  | 3P 30A | #09 | Google상면 | . | #10 | 3P 30A |  |  |  |  | O | OFF | 1T-4-12
1T-2-3 | O | OFF |  |  |  |  | 3P 30A | #11 | CF상면 | . | #12 | 3P 20A |  |  |  |  | O | OFF | 1T-5-3
1T-2-6 | O | OFF |  |  |  |  | 3P 20A | #13 | . | . | #14 | 3P 20A |  |  |  |  | O | OFF | 1T-5-6
1T-2-9 | O | OFF |  |  |  |  | 3P 20A | #15 | . | . | #16 | 3P 20A |  |  |  |  | O | OFF | 1T-5-9
1T-2-12 | O | OFF |  |  |  |  | 3P 20A | #17 | Google상면 | . | #18 | 3P 20A |  |  |  |  | O | OFF | 1T-5-12
1T-3-3 | O | OFF |  |  |  |  | 3P 20A | #19 | . | . | #20 | 3P 20A |  |  |  |  | O | OFF | 1T-6-2
1T-3-6 | O | OFF |  |  |  |  | 3P 20A | #21 | . | . | #22 | 3P 20A |  |  |  |  | O | OFF | 1T-6-4
1T-3-9 | O | OFF |  |  |  |  | 3P 20A | #23 | . | . | #24 | 3P 20A |  |  |  |  | X | OFF
1T-3-12 | O | OFF |  |  |  |  | 3P 20A | #25 | . | . | #26 | 3P 20A |  |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-05 |  | PDU : SEL1 - 5-1 - A3 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  | 0 |  | 2P 30A | #01 |  |  | #02 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #03 |  |  | #04 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #13 |  |  | #14 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #19 |  |  | #20 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-2
| X | OFF |  | 0 |  |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-3
| X | OFF |  |  | 0 |  | 2P 30A | #25 |  |  | #26 | 2P 30A |  |  | 0 |  | O | OFF | 3A-12-3T
| X | OFF | 0 |  |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-4
| X | OFF |  | 0 |  |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-5
| X | OFF |  |  | 0 |  | 2P 30A | #31 |  |  | #32 | 2P 30A |  |  | 0 |  | O | OFF | 3A-12-6
| X | OFF | 0 |  |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A | 0 |  |  |  | O | OFF | 3A-12-7
| X | OFF |  | 0 |  |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  | 0 |  |  | O | OFF | 3A-12-8
| X | OFF |  |  | 0 |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #43 |  |  | #44 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-06 |  | PDU : SEL1 - 5-1 - B3 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  | 0 |  | 2P 30A | #01 |  |  | #02 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #03 |  |  | #04 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #05 |  |  | #06 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #07 |  |  | #08 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #09 |  |  | #10 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #11 |  |  | #12 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #13 |  |  | #14 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #15 |  |  | #16 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #17 |  |  | #18 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #19 |  |  | #20 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #21 |  |  | #22 | 2P 30A | 0 |  |  |  | O | OFF | 3B-12-2
| X | OFF |  | 0 |  |  | 2P 30A | #23 |  |  | #24 | 2P 30A |  | 0 |  |  | O | OFF | 3B-12-3
| X | OFF |  |  | 0 |  | 2P 30A | #25 |  |  | #26 | 2P 30A |  |  | 0 |  | O | OFF | 3B-12-4
| X | OFF | 0 |  |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A | 0 |  |  |  | O | OFF | 3B-12-5
| X | OFF |  | 0 |  |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  | 0 |  |  | O | OFF | 3B-12-6
| X | OFF |  |  | 0 |  | 2P 30A | #31 |  |  | #32 | 2P 30A |  |  | 0.00082146 |  | O | OFF | 3B-12-6T
| X | OFF | 0 |  |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A | 0.00082609 |  |  |  | O | OFF | 3B-12-7
| X | OFF |  | 0 |  |  | 2P 30A | #35 |  |  | #36 | 2P 30A |  | 0.00040088 |  |  | O | OFF | 3B-12-8
| X | OFF |  |  | 4.9826e-05 |  | 2P 30A | #37 |  |  | #38 | 2P 30A |  |  | 0.0006221 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #39 |  |  | #40 | 2P 30A | 0.00060473 |  |  |  | X | OFF
| X | OFF |  | 2.4334e-05 |  |  | 2P 30A | #41 |  |  | #42 | 2P 30A |  | 0.00065817 |  |  | X | OFF
| X | OFF |  |  | 3.4758e-05 |  | 2P 30A | #43 |  |  | #44 | 2P 30A |  |  | 0.00097439 |  | X | OFF
| X | OFF | 3.4758e-05 |  |  |  | 2P 30A | #45 |  |  | #46 | 2P 30A | 0.00011239 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #47 |  |  | #48 | 2P 30A |  | 0.00012165 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #49 |  |  | #50 | 2P 30A |  |  | 0.00019233 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #51 |  |  | #52 | 2P 30A | 8.5737e-05 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #53 |  |  | #54 | 2P 30A |  | 8.6896e-05 |  |  | X | OFF
[12 empty] | 합계: | 0.0016637 | 0.0012919 | 0.0026949
5-DaHall 1-PDU-07 |  | PDU : SEL1 - 5-1 - A4 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 8.6 | 1.1 | 0.7 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
9A-1-5 (PCCW) /5F-A-14 | O | ON | 7.7743 |  |  |  | 3P 30A | #01 | PCCW | 센츄리링크코리아 | #02 | 3P 30A | 1.0427 |  |  |  | O | ON | 9A-1-8 / 5F-A-17
9A-1-6 / 5F-A-15 | O | ON |  | 1.0896 |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A |  | 0 |  |  | O | ON | 9A-1-9 / 5F-A-18
9A-1-7 / 5F-A-16 | O | ON |  |  | 0.39038 |  | 3P 30A | #05 | PCCW | 세종 인터넷(IES.YSM.S51) | #06 | 3P 30A |  |  | 0.3788 |  | O | ON | 9A-1-10 / 5F-A-19
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #09 |  |  | #10 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0.94028 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0.36241 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 9.7574 | 1.452 | 0.76918
5-DaHall 1-PDU-09 |  | PDU : SEL1 - 5-1 - A5 | [6 empty] | Main CB 4P 200A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #03 |  |  | #04 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #09 |  |  | #10 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #37 |  |  | #38 | 3P 20A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-08 |  | PDU : SEL1 - 5-1 - B4 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 6.5 | 1.4 | 1.4 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01 | 코로케션 | 센츄리링크코리아 | #02 | 3P 30A | 1.2448 |  |  |  | O | ON | 9B-1-8 / 5F-A-17
9B-1-6 / 5F-A-15 | O | ON |  | 1.3681 |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A |  | 5.2088 |  |  | O | ON | 9B-1-9 / 5F-A-18
9B-1-7 / 5F-A-16 | O | ON |  |  | 0 |  | 3P 30A | #05 | PCCW | 세종 인터넷(IES.YSM.S51) | #06 | 3P 30A |  |  | 1.328 |  | O | ON | 9B-1-10 / 5F-A-19
9B-1-5 (PCCW)/5F-A-14 | O | ON | 5.2714 |  |  |  | 3P 30A | #07 | PCCW |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #09 |  |  | #10 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 1.1226 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 1.3098 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| O | ON |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 7.6387 | 7.8867 | 1.328
5-DaHall 1-PDU-10 |  | PDU : SEL1 - 5-1 - B5 | [6 empty] | Main CB 4P 200A |  |  | <= MAIN OFF
[12 empty] | MAIN 계측값 : |  |  |  | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 |  |  |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #03 |  |  | #04 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 30A | #07 |  |  | #08 | 3P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 30A | #09 |  |  | #10 | 3P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #11 |  |  | #12 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #23 |  |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #27 |  |  | #28 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #29 |  |  | #30 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #31 |  |  | #32 | 3P 20A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 3P 20A | #33 |  |  | #34 | 3P 20A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 3P 20A | #35 |  |  | #36 | 3P 20A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 3P 20A | #37 |  |  | #38 | 3P 20A | 0 |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-11 |  | PDU : SEL1 - 5-1 - A6 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 15.3 | 10.2 | 9.9 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
1A-1-1 / 5F-A-10 | O | ON | 0 |  |  |  | 3P 30A | #03 | 코로케션 |  | #04 | 3P 30A | 0 |  |  |  | O | OFF | A1-3-2
1A-1-2 / 5F-A-11 | O | ON |  | 4.9924 |  |  | 3P 30A | #05 | 코로케션 | 코로케션 | #06 | 3P 30A |  | 1.9354 |  |  | O | ON | A1-3-3
1A-1-2(2) | O | ON |  |  | 1.8655 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 20A |  |  | 0 |  | O | ON | A1-3-4
1A-1-3 / 5F-A-12 | O | ON | 5.0854 |  |  |  | 3P 30A | #09 | PCCW | 코로케션 | #10 | 3P 20A | 0 |  |  |  | O | ON | A1-3-5
1A-1-4 / 5F-A-13 | O | ON |  | 2.4235 |  |  | 3P 30A | #11 | PCCW | 코로케션 | #12 | 3P 20A |  | 4.7449 |  |  | O | ON | A1-3-6
1A-1-4(2) / 5F-A-13 (2) | O | ON |  |  | 1.8986 |  | 3P 30A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 2.4231 |  | O | ON | A1-3-7
A1-2-1 / 5F-B-10 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 0 |  |  |  | O | ON | A1-3-8
A1-2-2 / 5F-B-11 | O | ON |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 3.0066 |  |  | O | ON | A1-3-9
A1-2-3 / 5F-B-12 | O | OFF |  |  | 1.9028 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 2.9667 |  | O | ON | A1-3-10
A1-2-4 / 5F-B-13 | O | ON | 2.4821 |  |  |  | 3P 20A | #21 | 다코스 |  | #22 | 3P 20A | 0 |  |  |  | O | ON | A807 / 5F-D-16 / A1-4-7(2)
A1-2-5 / A605 (A) | O | ON |  | 4.7745 |  |  | 3P 20A | #23 | 이비즈네트웍스 | PCCW | #24 | 3P 20A |  | 0 |  |  | O | ON | A1-5-10(2) / 5F-E-19
A1-2-6 / 5F-B-15 | O | ON |  |  | 2.8546 |  | 3P 20A | #25 | 다코스 & NTT | PCCW | #26 | 3P 20A |  |  | 4.9259 |  | O | ON | A1-1-3(2) / 5F-A-12(2)
A1-2-7 / 5F-B-16 | O | ON | 2.4187 |  |  |  | 3P 20A | #27 | 제우스네트웍스 |  | #28 | 3P 20A | 5.279 |  |  |  | O | ON | A1-1-8(2) / 5F-A-17 (2)
A1-2-8 / 5F-B-17 | O | ON |  | 5.2037 |  |  | 3P 20A | #29 | COLT |  | #30 | 3P 20A |  | 5.2394 |  |  | O | ON | 5F-D-18 임시
A1-3-1 | O | OFF |  |  | 0 |  | 3P 20A | #31 |  | 코로케션 | #32 | 3P 20A |  |  | 0 |  | O | ON
[12 empty] | 합계: | 15.2651 | 32.3204 | 18.8374
5-DaHall 1-PDU-13 |  | PDU : SEL1 - 5-1 - A7 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 12 | 18.7 | 14.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
A2-2-9 / 5F-B-18 | O | ON | 5.2809 |  |  |  | 3P 30A | #03 | 코로케션 | 코로케션 | #04 | 3P 30A | 0 |  |  |  | O | ON | A2-5-4
A2-2-10 / 5F-B-19 | O | ON |  | 3.8315 |  |  | 3P 30A | #05 | PCCW | 코로케션 | #06 | 3P 30A |  | 5.7186 |  |  | O | ON | A2-5-5
A2-4-1 | O | ON |  |  | 0.68093 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 4.1143 |  | O | ON | A2-5-6
A2-4-2 | O | ON | 0 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 30A | 5.4351 |  |  |  | O | ON | A2-5-7
A2-4-3 | O | ON |  | 3.0406 |  |  | 3P 20A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 8.8344 |  |  | O | ON | A2-5-8
A2-4-4 | O | ON |  |  | 1.1149 |  | 3P 20A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 0 |  | O | ON | A2-5-9
A2-4-5 / 5F-D-14 | O | ON | 0 |  |  |  | 3P 20A | #15 | PCCW | PCCW | #16 | 3P 20A | 3.7659 |  |  |  | O | ON | A2-5-10 / 5F-E-19
A2-4-6 / 5F-D-15 | O | ON |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 0 |  |  | O | OFF | A2-6-1
A2-4-7 | O | ON |  |  | 5.5747 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 4.044 |  | O | OFF | A2-6-2
A2-4-8 | O | ON | 3.0988 |  |  |  | 3P 20A | #21 | 코로케션 | 코로케션 | #22 | 3P 20A | 0 |  |  |  | O | OFF | A2-6-3
A2-4-9 | O | ON |  | 8.95 |  |  | 3P 20A | #23 | 코로케션 | 코로케션 | #24 | 3P 20A |  | 3.7088 |  |  | O | OFF | A2-6-4
A2-4-10 | O | ON |  |  | 2.4387 |  | 3P 20A | #25 | 코로케션 | 코로케션 | #26 | 3P 20A |  |  | 1.8314 |  | O | ON | A2-6-5 / F-14
A2-5-1 | O | ON | 0 |  |  |  | 3P 20A | #27 | 코로케션 | 코로케션 | #28 | 3P 20A | 0 |  |  |  | O | OFF | A2-6-6 / F-15
A2-5-2 | O | ON |  | 1.8121 |  |  | 3P 20A | #29 | 코로케션 | 코로케션 | #30 | 3P 20A |  | 0 |  |  | O | OFF | A2-6-7 / F-16
A2-5-3 | O | ON |  |  | 0 |  | 3P 20A | #31 | 코로케션 | 코로케션 | #32 | 3P 20A |  |  | 0 |  | O | ON | A2-6-8 / F-17
[12 empty] | 합계: | 17.5807 | 35.8959 | 19.7989
5-DaHall 1-PDU-15 |  | PDU : SEL1 - 5-1 - A8 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 19.1 | 6.2 | 14.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
AC PDU-3#A | O | ON | 6.0279 | 1.253 | 7.9728 |  | 3P 50A | #01(3상) | 텔스트라 | 텔스트라 | #02(3상) | 3P 50A | 3.2897 | 2.7182 | 1.997 |  | O | ON | TO:PDU(A)-3A
| X | OFF | 0 | 0 | 0 |  | 3P 50A | #03(3상) |  | Singtel-1 | #04(3상) | 3P 50A | 0 | 0 | 0 |  | X | OFF | DC정류기A
TRANSDUSER | O | OFF | 0 | 0 | 0 |  | 3P 30A | #05(3상) |  |  | #06(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF | customer con
PUD(A)-3-07 / 5F-B-17 (2) | O | ON | 3.1077 |  |  |  | 3P 30A | #07 | COLT |  | #08 | 3P 30A | 4.1937 |  |  |  | O | ON | A1007 / 5F-F-16
PUD(A)-3-09 / 5F-B-17 (3) | O | ON |  | 1.7053 |  |  | 3P 30A | #09 | COLT |  | #10 | 3P 30A |  | 6.5942 |  |  | O | OFF | A1006 / 5F-F-15
A603 / Colt, A-1 (23/08/23 On) | O | ON |  |  | 0.0031944 |  | 3P 30A | #11 |  | CMI | #12 | 3P 30A |  |  | 2.3146 |  | O | ON | D-15랙(CMI)-A ('21.09.29 투입)
P여(A)-3 싱텔 SKB CWDM A전원 | O | ON | 0.65398 |  |  |  | 3P 30A | #13 |  |  | #14 | 3P 30A | 1.5309 |  |  |  | O | ON | A603 / Colt, 정류기A (23/08/23 On)
PUD(A)-2-15 | X | OFF |  | 0.34588 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 7.8789 |  |  | X | OFF
PUD(A)-2-17 | X | OFF |  |  | 0 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
PUD(A)-2-19 | X | OFF | 4.1394 |  |  |  | 3P 20A | #19 |  |  | #20 | 3P 20A | 6.6275 |  |  |  | X | OFF
PUD(A)-2-21 | X | OFF |  | 2.2086 |  |  | 3P 20A | #21 |  |  | #22 | 3P 20A |  | 1.5008 |  |  | X | OFF
PUD(A)-2-23 | O | ON |  |  | 2.246 |  | 3P 20A | #23 | Singtel-2 |  | #24 | 3P 20A |  |  | 0 |  | X | OFF
DACOM EOS | X | OFF | 0 |  |  |  | 3P 20A | #25 |  |  | #26 | 3P 20A | 0 |  |  |  | X | OFF
PUD(A)-2-27 | X | OFF |  | 0 |  |  | 3P 20A | #27 |  | 다코스 & NTT | #28 | 3P 20A |  | 0.69019 |  |  | O | ON | A3-2-6(2) / 5F-B-15 (2)
PUD(A)-2-29 | O | ON |  |  | 0.44294 |  | 3P 20A | #29 | Singtel-2 |  | #30 | 3P 20A |  |  | 0 |  | X | OFF | TNSI A
[12 empty] | 합계: | 29.5709 | 24.8951 | 14.9766
5-DaHall 1-PDU-12 |  | PDU : SEL1 - 5-1 - B6 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 20.1 | 13.1 | 14 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
1B-1-1 / 5F-A-10 | O | ON | 0 |  |  |  | 3P 30A | #03 | 코로케션 | 코로케션 | #04 | 3P 30A | 1.852 |  |  |  | O | ON | B1-3-3
1B-1-2 / 5F-A-11 | O | ON |  | 2.7999 |  |  | 3P 30A | #05 | PCCW | 코로케션 | #06 | 3P 30A |  | 0 |  |  | O | ON | B1-3-4
| X | OFF |  |  | 0 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 0 |  | O | ON | B1-3-5
1B-1-4 / 5F-A-13 | O | ON | 2.8494 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 20A | 2.824 |  |  |  | O | ON | B1-3-6
1B-1-4(2) / 5F-A-13 (2) | O | ON |  | 4.4011 |  |  | 3P 30A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 0 |  |  | O | ON | B1-3-7
B1-2-1 / 5F-B-10 | O | ON |  |  | 3.1179 |  | 3P 20A | #13 | 코로케션 | 코로케션 | #14 | 3P 20A |  |  | 0 |  | O | ON | B1-3-8
B1-2-2 / 5F-B-11 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 5.9409 |  |  |  | O | ON | B1-3-9
B1-2-3 / 5F-B-12 | O | OFF |  | 0 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 3.1234 |  |  | O | ON | B1-3-10
B1-2-4 / 5F-B-13 | O | ON |  |  | 2.8563 |  | 3P 20A | #19 | 다코스 |  | #20 | 3P 20A |  |  | 0 |  | X | OFF
B1-2-5 / A605 (B) | O | ON | 4.4338 |  |  |  | 3P 20A | #21 | 이비즈네트웍스 |  | #22 | 3P 20A | 0 |  |  |  | X | OFF | A807 / 5F-D-16 / B1-4-7(2)
B1-2-6 / 5F-B-15 | O | ON |  | 0 |  |  | 3P 20A | #23 | 다코스 & NTT | PCCW | #24 | 3P 20A |  | 4.113 |  |  | O | ON | B1-5-10(2) / 5F-E-19
B1-2-7 / 5F-B-16 | O | ON |  |  | 3.2839 |  | 3P 20A | #25 | 제우스네트웍스 | PCCW | #26 | 3P 20A |  |  | 4.8527 |  | O | ON | 1B-1-3 / 5F-A-12
B1-2-8 / 5F-B-17 | O | ON | 0 |  |  |  | 3P 20A | #27 | COLT |  | #28 | 3P 20A | 5.2757 |  |  |  | O | ON | B1-1-8(2) / 5F-A-17 (2)
B1-3-1 | O | ON |  | 4.7545 |  |  | 3P 20A | #29 | 코로케션 | PCCW | #30 | 3P 20A |  | 6.3531 |  |  | X | ON | B1-1-3(2) / 5F-A-12 (2)
B1-3-2 | O | OFF |  |  | 6.2081 |  | 3P 20A | #31 | 코로케션 | 코로케션 | #32 | 3P 20A |  |  | 3.2036 |  | O | ON | B1-2-9 / 5F-B-18
[12 empty] | 합계: | 23.1758 | 25.545 | 23.5226
5-DaHall 1-PDU-14 |  | PDU : SEL1 - 5-1 - B7 | [6 empty] | Main CB 4P 150A
[12 empty] | MAIN 계측값 : | 13.4 | 11.6 | 7.6 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF | 0 | 0 | 0 |  | 3P 30A | #01(3상) |  |  | #02(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF
B2-2-10 / 5F-B-19 | O | ON | 3.1702 |  |  |  | 3P 30A | #03 | PCCW | 코로케션 | #04 | 3P 30A | 6.784 |  |  |  | O | ON | B2-5-5
B2-4-1 | O | ON |  | 0 |  |  | 3P 30A | #05 | 코로케션 | 코로케션 | #06 | 3P 30A |  | 2.7567 |  |  | O | ON | B2-5-6
B2-4-2 | O | ON |  |  | 1.6507 |  | 3P 30A | #07 | 코로케션 | 코로케션 | #08 | 3P 30A |  |  | 0 |  | O | ON | B2-5-7
B2-4-3 | O | OFF | 0.91896 |  |  |  | 3P 30A | #09 | 코로케션 | 코로케션 | #10 | 3P 30A | 2.4612 |  |  |  | O | ON | B2-5-8
B2-4-4 | O | ON |  | 3.2292 |  |  | 3P 20A | #11 | 코로케션 | 코로케션 | #12 | 3P 20A |  | 2.4455 |  |  | O | ON | B2-5-9
B2-4-5 / 5F-D-14 | O | ON |  |  | 1.6831 |  | 3P 20A | #13 | PCCW | PCCW | #14 | 3P 20A |  |  | 3.1126 |  | O | ON | B2-5-10 / 5F-E-19
B2-4-6 / 5F-D-15 | O | ON | 0 |  |  |  | 3P 20A | #15 | 코로케션 | 코로케션 | #16 | 3P 20A | 0 |  |  |  | O | OFF | B2-6-1
B2-4-7 | O | ON |  | 0.93687 |  |  | 3P 20A | #17 | 코로케션 | 코로케션 | #18 | 3P 20A |  | 6.8537 |  |  | O | OFF | B2-6-2
B2-4-8 | O | ON |  |  | 2.6305 |  | 3P 20A | #19 | 코로케션 | 코로케션 | #20 | 3P 20A |  |  | 0 |  | O | OFF | B2-6-3
B2-4-9 | O | ON | 3.2902 |  |  |  | 3P 20A | #21 | 코로케션 | 코로케션 | #22 | 3P 20A | 0 |  |  |  | O | OFF | B2-6-4
B2-4-10 | O | ON |  | 2.7028 |  |  | 3P 20A | #23 | 코로케션 | 코로케션 | #24 | 3P 20A |  | 5.2254 |  |  | O | ON | B2-6-5 / F-14
B2-5-1 | O | ON |  |  | 0 |  | 3P 20A | #25 | 코로케션 | 코로케션 | #26 | 3P 20A |  |  | 0 |  | O | OFF | B2-6-6 / F-15
B2-5-2 | O | ON | 0 |  |  |  | 3P 20A | #27 | 코로케션 | 코로케션 | #28 | 3P 20A | 5.1566 |  |  |  | O | OFF | B2-6-7 / F-16
B2-5-3 | O | ON |  | 0 |  |  | 3P 20A | #29 | 코로케션 | 코로케션 | #30 | 3P 20A |  | 0.00020326 |  |  | O | ON | B2-6-8 / F-17
B2-5-4 | O | ON |  |  | 0 |  | 3P 20A | #31 | 코로케션 |  | #32 | 3P 20A |  |  | 0.00020998 |  | O | ON | FMS 5층 메인전원
[12 empty] | 합계: | 21.7811 | 24.1504 | 9.0771
5-DaHall 1-PDU-16 |  | PDU : SEL1 - 5-1 - B8 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 20.1 | 11.1 | 16 | <- 실측값 |  |  | <- 디스플래이값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
AC PDU-3#B | O | ON | 4.7036 | 1.3449 | 6.1002 |  | 3P 50A | #01(3상) | 텔스트라 | 텔스트라 | #02(3상) | 3P 50A | 3.058 | 3.0548 | 1.8161 |  | O | ON | TO:PDU(B)-3A
| X | OFF | 0 | 0 | 0 |  | 3P 50A | #03(3상) |  | Singtel-1 | #04(3상) | 3P 50A | 0 | 0 | 0 |  | X | OFF | DC정류기B
TRANSDUSER | X | OFF | 0 | 0 | 0 |  | 3P 30A | #05(3상) |  |  | #06(3상) | 3P 30A | 0 | 0 | 0 |  | X | OFF | customer con
PUD(B)-3-07 / 5F-B-17 (2) | O | ON | 3.4715 |  |  |  | 3P 30A | #07 | COLT |  | #08 | 3P 30A | 4.3362 |  |  |  | O | ON | A1007 / 5F-F-16
PUD(B)-3-09 / 5F-B-17 (3) | O | ON |  | 1.7549 |  |  | 3P 30A | #09 | COLT |  | #10 | 3P 30A |  | 0.9712 |  |  | X | OFF | A1006 / 5F-F-15
A603 / Colt, B-1 (23/08/23 On) | O | ON |  |  | 0.40296 |  | 3P 30A | #11 |  | CMI | #12 | 3P 30A |  |  | 2.4929 |  | O | ON | D-15랙(CMI)-B ('21.09.29 투입)
P여(B)-3 싱텔 SKB CWDM B전원 | O | ON | 1.3404 |  |  |  | 3P 30A | #13 |  |  | #14 | 3P 30A | 1.6695 |  |  |  | O | ON | A603 / Colt, 정류기B (23/08/23 On)
KT Rack #2 (소형 임시정류기) | O | ON |  | 2.3945 |  |  | 3P 20A | #15 |  |  | #16 | 3P 20A |  | 7.8338 |  |  | X | OFF
KT Rack #3 (소형 임시정류기) | O | ON |  |  | 1.5462 |  | 3P 20A | #17 |  |  | #18 | 3P 20A |  |  | 0 |  | X | OFF
KT Rack #4 (소형 임시정류기) | O | ON | 4.52 |  |  |  | 3P 20A | #19 |  | 4F BMS | #20 | 3P 20A | 0.68925 |  |  |  | O | ON | 신규 BMS(4F TPS실) Rack
텔스트라 CCTV 모니터링PC 및 시스템 박스 | O | ON |  | 0.96691 |  |  | 3P 20A | #21 |  | 5F BMS | #22 | 3P 20A |  | 0.84193 |  |  | O | ON | 신규 BMS(5F TPS실) Rack
DACOM EOS | O | ON |  |  | 0 |  | 3P 20A | #23 | Singtel-2 | Singtel-2 | #24 | 3P 20A |  |  | 1.4455 |  | O | ON | kt mspp 전원
| O | ON | 0.46351 |  |  |  | 3P 20A | #25 | Singtel-2 |  | #26 | 3P 20A | 0.57227 |  |  |  | X | OFF
SKB2.5G전용 PDU B3 27 | O | ON |  | 1.4893 |  |  | 3P 20A | #27 | Singtel-2 | 다코스 & NTT | #28 | 3P 20A |  | 0.29024 |  |  | O | ON | B3-2-6(2) / 5F-B-15 (2)
데이콤 AC전원 | O | ON |  |  | 1.7927 |  | 3P 20A | #29 | Singtel-2 | Singtel-2 | #30 | 3P 20A |  |  | 0.49895 |  | O | ON | TNSI A
[12 empty] | 합계: | 24.8244 | 20.9426 | 16.0955
PDU(C) | [8 empty] | Main CB 4P 50A
[12 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
| X | OFF |  |  |  |  | 3P 50A | #01(3상) |  |  | #02(3상) | 3P 50A |  |  |  |  | X | OFF
라우터룸 System box | O | ON |  |  |  |  | 3P 30A | #03(3상) | Singtel-2 |  | #04(3상) | 3P 30A |  |  |  |  | X | OFF
| X | OFF |  |  |  |  | 3P 30A | #05 |  |  | #06 | 3P 30A |  |  |  |  | X | OFF
SYSTEM BOX | X | OFF |  |  |  |  | 3P 30A | #07 |  | Singtel-2 | #08 | 3P 30A |  |  |  |  | O | ON | SYSTEM BOX
customer con | X | OFF |  |  |  |  | 3P 20A | #09 |  | Singtel-2 | #10 | 3P 20A |  |  |  |  | O | ON | SYSTEM BOX
SYSTEM BOX | O | ON |  |  |  |  | 3P 20A | #11 | Singtel-2 |  | #12 | 3P 20A |  |  |  |  | X | OFF | customer con
| O | OFF |  |  |  |  | 3P 20A | #13 |  |  | #14 | 3P 20A |  |  |  |  | X | OFF | customer con
M/S 단파 | O | ON |  |  |  |  | 3P 20A | #15 | Singtel-2 |  | #16 | 3P 20A |  |  |  |  | X | OFF
[12 empty] | 합계: | 0 | 0 | 0
5-DaHall 1-PDU-17 |  | PDU : SEL1 - 5-1 - A9 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 5.5 | 7.2 | 2.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RT-07 | ○ | ON | 0.72242 |  |  |  | 2P 30A | #01 | U08-A-01 | U08-A-02 | #02 | 2P 30A | 0.81744 |  |  |  | ○ | ON | RT-08
RT-09 | ○ | ON |  | 0 |  |  | 2P 30A | #03 | U08-A-03 | U08-A-04 | #04 | 2P 30A |  | 0 |  |  | ○ | ON | RT-10
RT-11 | ○ | ON |  |  | 6.7267 |  | 2P 30A | #05 | U08-A-05 | U08-A-06 | #06 | 2P 30A |  |  | 0.50001 |  | ○ | ON | RT-12
RT-13 | ○ | ON | 0 |  |  |  | 2P 30A | #07 | U08-A-07 | U08-A-08 | #08 | 2P 30A | 2.2208 |  |  |  | ○ | ON | RT-14
RT-15 | ○ | ON |  | 5.7682 |  |  | 2P 30A | #09 | U08-A-09 | U08-A-10 | #10 | 2P 30A |  | 0 |  |  | ○ | ON | RT-16
RT-17 | ○ | ON |  |  | 0.52003 |  | 2P 30A | #11 | U08-A-11 | U08-A-12 | #12 | 2P 30A |  |  | 1.1064 |  | ○ | ON | RT-18
RT-19 | ○ | ON | 1.71 |  |  |  | 2P 30A | #13 | U08-A-13 | U08-A-14 | #14 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-01
LSP-02 | ○ | OFF |  | 0 |  |  | 2P 30A | #15 | U08-A-15 | U08-A-16 | #16 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-03
LSP-04 | ○ | ON |  |  | 0.7421 |  | 2P 30A | #17 | U08-A-17 | U08-A-18 | #18 | 2P 30A |  |  | 0.78661 |  | ○ | OFF | LSP-05
LSP-06 | ○ | OFF | 0 |  |  |  | 2P 30A | #19 | U08-A-19 | U08-A-20 | #20 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-07
LSP-08 | ○ | OFF |  | 2.1382 |  |  | 2P 30A | #21 | U08-A-21 | U08-A-22 | #22 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-09
LSP-10 | ○ | OFF |  |  | 1.065 |  | 2P 30A | #23 | U08-A-23 | U08-A-24 | #24 | 2P 30A |  |  | 0 |  | ○ | ON | MT-06
RT-08 정류기 | ○ | ON | 1.7783 |  |  |  | 2P 30A | #25 | U08-A-25 |  | #26 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 7.249 | 7.9064 | 11.4468
5-DaHall 1-PDU-18 |  | PDU : SEL1 - 5-1 - B9 | [6 empty] | Main CB 4P 200A
[12 empty] | MAIN 계측값 : | 4.6 | 5 | 1.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RT-07 | ○ | ON | 0.82545 |  |  |  | 2P 30A | #01 | U08-B-01 | U08-B-02 | #02 | 2P 30A | 0.7625 |  |  |  | ○ | ON | RT-08
RT-09 | ○ | ON |  | 0 |  |  | 2P 30A | #03 | U08-B-03 | U08-B-04 | #04 | 2P 30A |  | 0 |  |  | ○ | ON | RT-10
RT-11 | ○ | ON |  |  | 4.645 |  | 2P 30A | #05 | U08-B-05 | U08-B-06 | #06 | 2P 30A |  |  | 0.39283 |  | ○ | ON | RT-12
RT-13 | ○ | ON | 0 |  |  |  | 2P 30A | #07 | U08-B-07 | U08-B-08 | #08 | 2P 30A | 2.1394 |  |  |  | ○ | ON | RT-14
RT-15 | ○ | ON |  | 4.8339 |  |  | 2P 30A | #09 | U08-B-09 | U08-B-10 | #10 | 2P 30A |  | 0 |  |  | ○ | ON | RT-16
RT-17 | ○ | ON |  |  | 0.40911 |  | 2P 30A | #11 | U08-B-11 | U08-B-12 | #12 | 2P 30A |  |  | 1.0356 |  | ○ | ON | RT-18
RT-19 | ○ | ON | 0.9383 |  |  |  | 2P 30A | #13 | U08-B-13 | U08-B-14 | #14 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-01
LSP-02 | ○ | OFF |  | 0 |  |  | 2P 30A | #15 | U08-B-15 | U08-B-16 | #16 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-03
LSP-04 | ○ | OFF |  |  | 0 |  | 2P 30A | #17 | U08-B-17 | U08-B-18 | #18 | 2P 30A |  |  | 0.73835 |  | ○ | OFF | LSP-05
LSP-06 | ○ | OFF | 0 |  |  |  | 2P 30A | #19 | U08-B-19 | U08-B-20 | #20 | 2P 30A | 0 |  |  |  | ○ | OFF | LSP-07
LSP-08 | ○ | OFF |  | 2.0598 |  |  | 2P 30A | #21 | U08-B-21 | U08-B-22 | #22 | 2P 30A |  | 0 |  |  | ○ | OFF | LSP-09
LSP-10 | ○ | OFF |  |  | 0.99228 |  | 2P 30A | #23 | U08-B-23 | U08-B-24 | #24 | 2P 30A |  |  | 0 |  | ○ | ON | 시로코팬
RT-08 정류기 | ○ | ON | 0.98612 |  |  |  | 2P 30A | #25 | U08-B-25 |  | #26 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #27 |  |  | #28 | 2P 30A |  | 0 |  |  | X | OFF
| X | OFF |  |  | 0 |  | 2P 30A | #29 |  |  | #30 | 2P 30A |  |  | 0 |  | X | OFF
| X | OFF | 0 |  |  |  | 2P 30A | #31 |  |  | #32 | 2P 30A | 0 |  |  |  | X | OFF
| X | OFF |  | 0 |  |  | 2P 30A | #33 |  |  | #34 | 2P 30A |  | 0 |  |  | X | OFF
[12 empty] | 합계: | 5.6518 | 6.8937 | 8.2133
5-DaHall 1-PDU-19 |  | PDU : SEL1 - 5-1 - A10 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 35.1 | 38.9 | 22.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-1 | ○ | ON | 4.3555 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 3.1937 |  |  |  | ○ | ON | RTX Rack#8, R3-1-1
RTX Rack#2, R1-2-1 | ○ | ON |  | 4.0838 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 3.4714 |  |  | ○ | ON | RTX Rack#9, R3-2-1
RTX Rack#3, R1-3-1 | ○ | ON |  |  | 3.6577 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 3.1371 |  | ○ | ON | NW/Mgmt Rack, R3-3-1
RTX Rack#4, R2-1-1 | ○ | ON | 5.0432 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 5.3781 |  |  |  | ○ | ON | A40 Rack#1, R4-1-1
RTX Rack#5, R2-2-1 | ○ | ON |  | 3.6832 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 5.0353 |  |  | ○ | ON | A40 Rack#2, R4-2-1
RTX Rack#6, R2-3-1 | ○ | ON |  |  | 3.2033 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 3.927 |  | ○ | ON | NetApp FAS#1, R4-3-1
RTX Rack#7, R2-4-1 | ○ | ON | 4.3621 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 1.7822 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-1
DGX Rack#1, R5-1-1 | ○ | ON |  | 5.495 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 6.3267 |  |  | ○ | OFF | 예비Rack#1, R6-1-1
DGX Rack#2, R5-2-1 | ○ | ON |  |  | 4.0167 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 5.046 |  | ○ | OFF | 예비Rack#2, R6-2-1
DGX Rack#3, R5-3-1 | ○ | ON | 3.009 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 7.1291 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-1
| X | OFF |  | 6.9643 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 8.1055 |  |  | ○ | OFF | 예비Rack#4, R6-4-1
| X | OFF |  |  | 8.9514 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 34.2529 | 43.1652 | 31.9392
5-DaHall 1-PDU-20 |  | PDU : SEL1 - 5-1 - B10 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 28.1 | 32.6 | 23.1 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-2 | ○ | ON | 4.388 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 3.8187 |  |  |  | ○ | ON | RTX Rack#8, R3-1-2
RTX Rack#2, R1-2-2 | ○ | ON |  | 3.9414 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 3.4008 |  |  | ○ | ON | RTX Rack#9, R3-2-2
RTX Rack#3, R1-3-2 | ○ | ON |  |  | 3.6163 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 2.1512 |  | ○ | ON | NW/Mgmt Rack, R3-3-2
RTX Rack#4, R2-1-2 | ○ | ON | 5.0551 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 5.6127 |  |  |  | ○ | ON | A40 Rack#1, R4-1-2
RTX Rack#5, R2-2-2 | ○ | ON |  | 3.6921 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 5.0004 |  |  | ○ | ON | A40 Rack#2, R4-2-2
RTX Rack#6, R2-3-2 | ○ | ON |  |  | 2.5298 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 3.8241 |  | ○ | ON | NetApp FAS#1, R4-3-2
RTX Rack#7, R2-4-2 | ○ | ON | 4.2581 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 1.6513 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-2
DGX Rack#1, R5-1-2 | ○ | ON |  | 5.6958 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 6.4098 |  |  | ○ | OFF | 예비Rack#1, R6-1-2
DGX Rack#2, R5-2-2 | ○ | ON |  |  | 4.2516 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 4.8746 |  | ○ | OFF | 예비Rack#2, R6-2-2
DGX Rack#3, R5-3-2 | ○ | ON | 3.0109 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 2.7153 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-2
| X | OFF |  | 6.7808 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 2.8347 |  |  | ○ | OFF | 예비Rack#4, R6-4-2
| X | OFF |  |  | 2.5332 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 30.5102 | 37.7558 | 23.7807
5-DaHall 1-PDU-21 |  | PDU : SEL1 - 5-1 - A11 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 41.9 | 33.6 | 29.3 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-3 | ○ | ON | 3.678 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 2.8627 |  |  |  | ○ | ON | RTX Rack#8, R3-1-3
RTX Rack#2, R1-2-3 | ○ | ON |  | 4.8486 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 2.6554 |  |  | ○ | ON | RTX Rack#9, R3-2-3
RTX Rack#3, R1-3-3 | ○ | ON |  |  | 5.59 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 4.3625 |  | ○ | ON | NW/Mgmt Rack, R3-3-3
RTX Rack#4, R2-1-3 | ○ | ON | 4.4081 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 5.3842 |  |  |  | ○ | ON | A40 Rack#1, R4-1-3
RTX Rack#5, R2-2-3 | ○ | ON |  | 4.5618 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 6.742 |  |  | ○ | ON | A40 Rack#2, R4-2-3
RTX Rack#6, R2-3-3 | ○ | ON |  |  | 2.9031 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 1.7161 |  | ○ | ON | NetApp FAS#1, R4-3-3
RTX Rack#7, R2-4-3 | ○ | ON | 4.3279 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 2.3178 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-3
DGX Rack#1, R5-1-3 | ○ | ON |  | 3.663 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 8.1453 |  |  | ○ | OFF | 예비Rack#1, R6-1-3
DGX Rack#2, R5-2-3 | ○ | ON |  |  | 4.7874 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 4.5421 |  | ○ | OFF | 예비Rack#2, R6-2-3
DGX Rack#3, R5-3-3 | ○ | ON | 3.3129 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 7.7999 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-3
| X | OFF |  | 5.0671 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 7.3646 |  |  | ○ | OFF | 예비Rack#4, R6-4-3
| X | OFF |  |  | 7.7807 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 34.0915 | 43.0478 | 31.682
5-DaHall 1-PDU-22 |  | PDU : SEL1 - 5-1 - B11 | [6 empty] | Main CB 4P 300A
[12 empty] | MAIN 계측값 : | 37 | 27.7 | 24 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
RTX Rack#1, R1-1-4 | ○ | ON | 4.0021 |  |  |  | 2P 50A | #01 |  |  | #02 | 2P 50A | 2.823 |  |  |  | ○ | ON | RTX Rack#8, R3-1-4
RTX Rack#2, R1-2-4 | ○ | ON |  | 4.7818 |  |  | 2P 50A | #03 |  |  | #04 | 2P 50A |  | 2.3563 |  |  | ○ | ON | RTX Rack#9, R3-2-4
RTX Rack#3, R1-3-4 | ○ | ON |  |  | 5.1268 |  | 2P 50A | #05 |  |  | #06 | 2P 30A |  |  | 2.9584 |  | ○ | ON | NW/Mgmt Rack, R3-3-4
RTX Rack#4, R2-1-4 | ○ | ON | 4.2732 |  |  |  | 2P 50A | #07 |  |  | #08 | 2P 50A | 5.8281 |  |  |  | ○ | ON | A40 Rack#1, R4-1-4
RTX Rack#5, R2-2-4 | ○ | ON |  | 4.368 |  |  | 2P 50A | #09 |  |  | #10 | 2P 50A |  | 6.497 |  |  | ○ | ON | A40 Rack#2, R4-2-4
RTX Rack#6, R2-3-4 | ○ | ON |  |  | 3.0905 |  | 2P 50A | #11 |  |  | #12 | 2P 30A |  |  | 1.7404 |  | ○ | ON | NetApp FAS#1, R4-3-4
RTX Rack#7, R2-4-4 | ○ | ON | 4.0657 |  |  |  | 2P 50A | #13 |  |  | #14 | 2P 30A | 2.34 |  |  |  | ○ | ON | NetApp AFF#2, R4-4-4
DGX Rack#1, R5-1-4 | ○ | ON |  | 3.7615 |  |  | 2P 30A | #15 |  |  | #16 | 2P 50A |  | 8.5137 |  |  | ○ | OFF | 예비Rack#1, R6-1-4
DGX Rack#2, R5-2-4 | ○ | ON |  |  | 4.3797 |  | 2P 30A | #17 |  |  | #18 | 2P 50A |  |  | 4.3303 |  | ○ | OFF | 예비Rack#2, R6-2-4
DGX Rack#3, R5-3-4 | ○ | ON | 3.5231 |  |  |  | 2P 30A | #19 |  |  | #20 | 2P 50A | 3.2377 |  |  |  | ○ | OFF | 예비Rack#3, R6-3-4
| X | OFF |  | 4.8018 |  |  | 2P 50A | #21 |  |  | #22 | 2P 50A |  | 3.2135 |  |  | ○ | OFF | 예비Rack#4, R6-4-4
| X | OFF |  |  | 4.6486 |  | 2P 50A | #23 |  |  | #24 | 2P 50A |  |  | 0 |  | X | OFF
[12 empty] | 합계: | 30.0929 | 38.2937 | 26.2746
5층 TR룸
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | NO. |  | CB 용량 | R | S | T | N | 배선연결 | ON/OFF | 부하명
PDU-8 (A) | O | ON | 5.6 | 7.2 | 2.3 | 3.8 | 3P 200A | #08 | Singtel | Singtel | #08 | 3P 200A | 4.6 | 5 | 1.5 | 2.7 | O | ON | PDU-8 (B)
텔스트라 정류기 A1 | O | ON | 8.4 | 19.2 | 9.2 | 10.7 | 3P 30A | #03 | C2C | C2C | #04 | 3P 30A | 8.6 | 8.4 | 9 | 2.1 | O | ON | 텔스트라 정류기 A2
텔스트라 정류기 B1 | O | ON | 11.2 | 8 | 11.6 | 4 | 3P 30A | #05 | C2C | C2C | #06 | 3P 30A | 11.7 | 11.5 | 11.5 | 1.8 | O | ON | 텔스트라 정류기 B2
|  |  | 사용량 | 배분
| IDC |  | 651.6081 | 50.31% | [7 empty] | 5-1-A1 | 35.4144 | 38.3568 | 28.5652
| 텔스트라 |  | 44.3033 | 3.42% | [7 empty] | 5-1-B1 | 34.2605 | 35.6993 | 27.0223
| 텔스트라 정류기 |  | 128.3 | 9.905% | [7 empty] | 5-1-A2 | 28.0007 | 18.6894 | 18.7163
| singtel PDU-8-A |  | 26.6021 | 2.054% | [7 empty] | 6-1-B2 | 25.1261 | 17.1644 | 18.3382
| singtel PDU-8-B |  | 20.7587 | 1.603% | =>합계 | 3.656% | [5 empty] | 5-1-A3 | 0 | 0 | 0
| singtel (기타) |  | 18.834 | 1.454% | [7 empty] | 5-1-B3 | 0.0016637 | 0.0012919 | 0.0026949
| LG CNS |  | 404.8864 | 31.26% | [7 empty] | 5-1-A4 | 9.7574 | 1.452 | 0.76918
함계 | IDC |  | 1295.2926 | 100% | [7 empty] | 5-1-B4 | 7.6387 | 7.8867 | 1.328
[12 empty] | 5-1-A5 | 0 | 0 | 0
[12 empty] | 5-1-B5 | 0 | 0 | 0
[12 empty] | 5-1-A6 | 15.2651 | 32.3204 | 18.8374
[12 empty] | 5-1-B6 | 23.1758 | 25.545 | 23.5226
[12 empty] | 5-1-A7 | 17.5807 | 35.8959 | 19.7989
| C2C | [10 empty] | 5-1-B7 | 21.7811 | 24.1504 | 9.0771
[12 empty] | 5-1-A8 | 29.5709 | 24.8951 | 14.9766
[12 empty] | 5-1-B8 | 24.8244 | 20.9426 | 16.0955
[12 empty] | 5-1-A9 | 7.249 | 7.9064 | 11.4468 | 26.6021
[12 empty] | 5-1-B9 | 5.6518 | 6.8937 | 8.2133 | 20.7587
[12 empty] | 5-1-A10 | 34.2529 | 43.1652 | 31.9392
|  |  |  | 복도 | [7 empty] | 5-1-B10 | 30.5102 | 37.7558 | 23.7807
[12 empty] | 5-1-A11 | 34.0915 | 43.0478 | 31.682
[12 empty] | 5-1-B11 | 30.0929 | 38.2937 | 26.2746 |  | 404.8864
|  |  |  | ▼ | [8 empty] | 414.2458 | 460.0618 | 330.3865 | 1204.6941
128.3
1332.9941
[5 empty] | Singtel-1 |  | Singtel-2 |  | Pacnet
Note on A226: 이현상: 계약전류 10A/랙 ? 초과시 AM연락 필요! (임영호팀장/장우창M/장태영M)
Note on A274: 이현상: 계약전류 10A/랙 ? 초과시 AM연락 필요 (임영호팀장/장우창M/장태영M)

## 4층_부하량(월간_MIN)
Date : 2023-11-01 ~ 2023-11-30
4-DaHall 1-PDU-02 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B1 |  |  |  | 4-DaHall 1-PDU-04 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B2
|  | MAIN 계측값 : | 73.5 | 46 | 65.4 | <- 실측값 | [5 empty] | MAIN 계측값 : | 70.2 | 42.2 | 22.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
정류기 1호기 | O | ON | 0.62 | 0.54 | 0.78 |  | 4P 100A | #01 | 코어룸 |  | X | OFF | 0 | 0 | 0 |  | 4P 100A | #01
POP E(상) | O | ON | 34.8 |  |  |  | 2P 100A | #02 | 코어룸 | POP F(상) | O | ON | 38.63 |  |  |  | 2P 100A | #02 | 코어룸
POP B(상) | O | ON |  | 32.08 |  |  | 2P 100A | #03 | 코어룸 | IDC 1구역 B(상) | O | ON |  | 26.4 |  |  | 2P 100A | #03 | 코어룸
POP C(상) | O | ON |  |  | 30.36 |  | 2P 100A | #04 | 코어룸 | IDC 1구역 C(상) | X | OFF |  |  | 0 |  | 2P 100A | #04 | 코어룸
POP D(상) | O | ON | 40.4 |  |  |  | 2P 100A | #05 | 코어룸 | IDC 1구역 D(상) | O | ON | 9.47 |  |  |  | 2P 100A | #05 | 코로케션
IDC 2구역 I(상) | O | ON |  | 12.15 |  |  | 2P 100A | #06 | 코로케션 | IDC 1구역 E(상) | O | ON |  | 14.21 |  |  | 2P 100A | #06 | 코로케션
IDC 2구역 H(상) | O | ON |  |  | 28.37 |  | 2P 100A | #07 | 코로케션 | IDC 1구역 F(상) | O | ON |  |  | 21.53 |  | 2P 100A | #07 | 코로케션
| X | OFF | 0 |  |  |  | 2P 100A | #08 |  | IDC 1구역 G(상) | O | ON | 21.3 |  |  |  | 2P 100A | #08 | 코로케션
| X | OFF |  | 0 |  |  | 2P 100A | #09 |  |  | X | OFF |  | 0 |  |  | 2P 100A | #09
|  | 합계: | 75.82 | 44.77 | 59.51 | [6 empty] | 합계: | 69.4 | 40.61 | 21.53
4-DaHall 1-PDU-06 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B3 |  |  |  | 4-DaHall 1-PDU-08 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B4
|  | MAIN 계측값 : | 67 | 32.4 | 27 | <- 실측값 | [5 empty] | MAIN 계측값 : | 44.8 | 68.4 | 18 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
IDC 2구역 J(상) | O | ON | 9.83 |  |  |  | 2P 100A | #01 | 코로케션 | K 2-1-상 | O | ON | 22.18 |  |  |  | 2P 100A | #01 | 세틀뱅크(구 시스케어)
IDC 2구역 K(상) | O | ON |  | 0 |  |  | 2P 100A | #02 | 코로케션 | K 3-1 상 | O | ON |  | 32.62 |  |  | 2P 100A | #02 | 미디어꾼(구)윈텔)
IDC 2구역 L(상) | O | ON |  |  | 7.81 |  | 2P 100A | #03 | 코로케션 | K 2-2-상 | O | ON |  |  | 5.29 |  | 2P 100A | #03 | 세틀뱅크(구 시스케어)
IDC 2구역 M(상) | O | ON | 6.86 |  |  |  | 2P 100A | #04 | 코로케션 | K 3-2 상 | O | ON | 9.06 |  |  |  | 2P 100A | #04 | 미디어꾼(구)윈텔)
IDC 3구역 N(상) | O | ON |  | 0 |  |  | 2P 100A | #05 | 코로케션 | K 2-3-상 | O | ON |  | 7.32 |  |  | 2P 100A | #05 | 세틀뱅크(구 시스케어)
IDC 3구역 O(상) | O | ON |  |  | 0 |  | 2P 100A | #06 | 코로케션 | K 3-3 상 | O | ON |  |  | 11.08 |  | 2P 100A | #06 | 미디어꾼(구)윈텔)
IDC 3구역 P(상) | O | ON | 8.09 |  |  |  | 2P 100A | #07 | 코로케션 | K 2-4 상 | O | ON | 12.98 |  |  |  | 2P 100A | #07 | 세틀뱅크(구 시스케어)
IDC 3구역 Q(상) | O | ON |  | 13.5 |  |  | 2P 100A | #08 | 코로케션 | K 3-4 상 | O | ON |  | 23.81 |  |  | 2P 100A | #08 | 미디어꾼(구)윈텔)
IDC 3구역 R(상) | O | OFF |  |  | 0 |  | 2P 100A | #09 | 코로케션 | K 1-1 상 | O | ON |  |  | 0 |  | 2P 100A | #09 | BMW
IDC 3구역 S(상) | O | ON | 36.52 |  |  |  | 2P 100A | #10 | 코로케션 | K 1-2 상 | O | ON | 0 |  |  |  | 2P 100A | #10 | 세종시스템케이지
| X | OFF |  | 0 |  |  | 2P 100A | #11 |  |  | X | OFF |  | 0 |  |  | 2P 100A | #11
| X | OFF |  |  | 0 |  | 2P 100A | #12 |  |  | X | OFF |  |  | 0 |  | 2P 100A | #12
|  | 합계: | 61.3 | 13.5 | 7.81 | [6 empty] | 합계: | 44.22 | 63.75 | 16.37
4-DaHall 1-PDU-10 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B5 |  |  |  | 4-DaHall 1-PDU-01 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A1
|  | MAIN 계측값 : | 46.5 | 43.9 | 43.5 | <- 실측값 | [5 empty] | MAIN 계측값 : | 77.6 | 59.1 | 50.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
라온 - 철거 | O | OFF | 0 | 0 | 0 |  | 4P 200A | #01 |  | 정류기 2호기 | O | ON | 1.13 | 0.89 | 1.33 |  | 4P 100A | #01 | 코어룸
CRAC 4E-1호기(20RT) | O | ON | 28.97 | 26.42 | 27.99 |  | 4P 200A | #02 | 항온 | POP E(하) | O | ON | 37.09 |  |  |  | 2P 100A | #02 | 코어룸
CRAC 4E-2호기(20RT) | O | ON | 2.95 | 2.66 | 3.22 |  | 4P 200A | #03 | 항온 | POP B(하) | O | ON |  | 33.54 |  |  | 2P 100A | #03 | 코어룸
|  | 합계: | 31.92 | 29.08 | 31.21 | 0 |  |  |  | POP C(하) | O | ON |  |  | 31.18 |  | 2P 100A | #04 | 코어룸
[10 empty] | POP D(하) | O | ON | 40.91 |  |  |  | 2P 100A | #05 | 코어룸
[10 empty] | IDC 2구역 I(하) | O | ON |  | 22.9 |  |  | 2P 100A | #06 | 코로케션
[10 empty] | IDC 2구역 H(하) | O | ON |  |  | 12.44 |  | 2P 100A | #07 | 코로케션
[11 empty] | X | OFF | 0 |  |  |  | 2P 100A | #08
[11 empty] | X | OFF |  | 0 |  |  | 2P 100A | #09
[12 empty] | 합계: | 79.13 | 57.33 | 44.95
4-DaHall 1-PDU-03 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A2 |  |  |  | 4-DaHall 1-PDU-05 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A3
|  | MAIN 계측값 : | 57.4 | 38.8 | 25.4 | <- 실측값 | [5 empty] | MAIN 계측값 : | 59.5 | 27.6 | 25.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
| X | OFF | 0 | 0 | 0 |  | 4P 100A | #01 |  | IDC 2구역 J(하) | O | ON | 8.38 |  |  |  | 2P 100A | #01 | 코로케션
POP F(하) | O | ON | 31.81 |  |  |  | 2P 100A | #02 | 코어룸 | IDC 2구역 K(하) | O | ON |  | 0 |  |  | 2P 100A | #02 | 코로케션
IDC 1구역 B(하) | O | ON |  | 26.71 |  |  | 2P 100A | #03 | 코어룸 | IDC 2구역 L(하) | O | ON |  |  | 6.39 |  | 2P 100A | #03 | 코로케션
IDC 1구역 C(하) | X | OFF |  |  | 0 |  | 2P 100A | #04 | 코어룸 | IDC 2구역 M(하) | O | ON | 7.15 |  |  |  | 2P 100A | #04 | 코로케션
IDC 1구역 D(하) | O | ON | 6.14 |  |  |  | 2P 100A | #05 | 코로케션 | IDC 3구역 N(하) | O | ON |  | 0 |  |  | 2P 100A | #05 | 코로케션
IDC 1구역 E(하) | O | ON |  | 10.15 |  |  | 2P 100A | #06 | 코로케션 | IDC 3구역 O(하) | O | ON |  |  | 12.68 |  | 2P 100A | #06 | 코로케션
IDC 1구역 F(하) | O | ON |  |  | 16.11 |  | 2P 100A | #07 | 코로케션 | IDC 3구역 P(하) | O | ON | 6.06 |  |  |  | 2P 100A | #07 | 코로케션
IDC 1구역 G(하) | O | ON | 17.56 |  |  |  | 2P 100A | #08 | 코로케션 | IDC 3구역 Q(하) | O | ON |  | 10.2 |  |  | 2P 100A | #08 | 코로케션
| X | OFF |  | 0 |  |  | 2P 100A | #09 |  | IDC 3구역 R(하) | O | OFF |  |  | 0 |  | 2P 100A | #09 | 코로케션
|  | 합계: | 55.51 | 36.86 | 16.11 |  |  |  |  | IDC 3구역 S(하) | O | ON | 31.56 |  |  |  | 2P 100A | #10 | 코로케션
[11 empty] | X | OFF |  | 0 |  |  | 2P 100A | #11
[11 empty] | X | OFF |  |  | 0 |  | 2P 100A | #12
[12 empty] | 합계: | 53.15 | 10.2 | 19.07
4-DaHall 1-PDU-07 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A4 |  |  |  | 4-DaHall 1-PDU-09 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A5
|  | MAIN 계측값 : | 44.7 | 76.7 | 22 | <- 실측값 | [5 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 2-1-하 | O | ON | 19.95 |  |  |  | 2P 100A | #01 | 세틀뱅크(구 시스케어) | 라온(상)- 철거 | X | OFF | 0 | 0 | 0 |  | 4P 200A | #01
K 3-1-하 | O | ON |  | 32.86 |  |  | 2P 100A | #02 | 미디어꾼(구)윈텔) |  | X | OFF | 0 | 0 | 0 |  | 4P 200A | #02
K 2-2-하 | O | ON |  |  | 5.2 |  | 2P 100A | #03 | 세틀뱅크(구 시스케어) |  | X | OFF | 0 | 0 | 0 |  | 4P 200A | #03
K 3-2-하 | O | ON | 10.17 |  |  |  | 2P 100A | #04 | 미디어꾼(구)윈텔) |  |  | 합계: | 0 | 0 | 0
K 2-3-하 | O | ON |  | 5.88 |  |  | 2P 100A | #05 | 세틀뱅크(구 시스케어) | TR Room A,B
K 3-3-하 | O | ON |  |  | 14.26 |  | 2P 100A | #06 | 미디어꾼(구)윈텔) | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 2-4-하 | O | ON | 13.74 |  |  |  | 2P 100A | #07 | 세틀뱅크(구 시스케어) | KB증권 DR(A) - 철거 | X | OFF |  |  |  |  | 4P 320A | #07
K 3-4-하 | O | ON |  | 30.44 |  |  | 2P 100A | #08 | 미디어꾼(구)윈텔)
K 1-1-하 | O | ON |  |  | 0 |  | 2P 100A | #09 | BMW | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 1-2-하 | O | ON | 0 |  |  |  | 2P 100A | #10 | 세종시스템케이지 | KB증권 DR(B) - 철거 | X | OFF |  |  |  |  | 4P 320A | #07
| X | OFF |  | 0 |  |  | 2P 100A | #11
| X | OFF |  |  | 0 |  | 2P 100A | #12
|  | 합계: | 43.86 | 69.18 | 19.46
|  |  |  | 사용량 | 층당 분배
4층 | IDC | IDC |  | 614.2 | 60.02%
| IP | 세종 시스템 |  | 0 | 0%
| 공통 | 세종 시스템
| IP | core room |  | 409.2 | 39.98%
총합 |  |  |  | 1023.4 | 100%
4층 항온항습기 비상 (4층 5RT x 3대, 10RT x 1대) | [8 empty] | Main CB 3P 150A
[11 empty] | MAIN 계측값 : | 24.1 | 22 | 21.9 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | 부하명 | CB 용량 | R | S | T | N | 배선연결 | ON/OFF |  | NO.
4-1 호 | O | ON |  |  |  |  | 3P 50A |  |  | 4-4호 | 3P 50A |  |  |  |  | O | ON
4-2 호 | O | ON |  |  |  | 0 | 3P 50A |  |  |  | 3P 50A |  |  |  |  | X | OFF
4-3 호 | O | ON |  |  |  | 0.1 | 3P 50A |  |  |  | 3P 50A |  |  |  |  | X | OFF
[11 empty] | 합계: | 0 | 0 | 0

## 4층_부하량(월간_MAX)
Date : 2023-11-01 ~ 2023-11-30
4-DaHall 1-PDU-02 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B1 |  |  |  | 4-DaHall 1-PDU-04 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B2
|  | MAIN 계측값 : | 73.5 | 46 | 65.4 | <- 실측값 | [5 empty] | MAIN 계측값 : | 70.2 | 42.2 | 22.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
정류기 1호기 | O | ON | 1.04 | 0.78 | 1.19 |  | 4P 100A | #01 | 코어룸 |  | X | OFF | 0 | 0 | 0 |  | 4P 100A | #01
POP E(상) | O | ON | 35.48 |  |  |  | 2P 100A | #02 | 코어룸 | POP F(상) | O | ON | 40.17 |  |  |  | 2P 100A | #02 | 코어룸
POP B(상) | O | ON |  | 33.16 |  |  | 2P 100A | #03 | 코어룸 | IDC 1구역 B(상) | O | ON |  | 31.32 |  |  | 2P 100A | #03 | 코어룸
POP C(상) | O | ON |  |  | 36.38 |  | 2P 100A | #04 | 코어룸 | IDC 1구역 C(상) | X | OFF |  |  | 0 |  | 2P 100A | #04 | 코어룸
POP D(상) | O | ON | 42.16 |  |  |  | 2P 100A | #05 | 코어룸 | IDC 1구역 D(상) | O | ON | 9.99 |  |  |  | 2P 100A | #05 | 코로케션
IDC 2구역 I(상) | O | ON |  | 12.63 |  |  | 2P 100A | #06 | 코로케션 | IDC 1구역 E(상) | O | ON |  | 15.47 |  |  | 2P 100A | #06 | 코로케션
IDC 2구역 H(상) | O | ON |  |  | 29.89 |  | 2P 100A | #07 | 코로케션 | IDC 1구역 F(상) | O | ON |  |  | 25.82 |  | 2P 100A | #07 | 코로케션
| X | OFF | 0 |  |  |  | 2P 100A | #08 |  | IDC 1구역 G(상) | O | ON | 23.67 |  |  |  | 2P 100A | #08 | 코로케션
| X | OFF |  | 0 |  |  | 2P 100A | #09 |  |  | X | OFF |  | 0 |  |  | 2P 100A | #09
|  | 합계: | 78.68 | 46.57 | 67.46 | [6 empty] | 합계: | 73.83 | 46.79 | 25.82
4-DaHall 1-PDU-06 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B3 |  |  |  | 4-DaHall 1-PDU-08 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B4
|  | MAIN 계측값 : | 67 | 32.4 | 27 | <- 실측값 | [5 empty] | MAIN 계측값 : | 44.8 | 68.4 | 18 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
IDC 2구역 J(상) | O | ON | 11.61 |  |  |  | 2P 100A | #01 | 코로케션 | K 2-1-상 | O | ON | 24.58 |  |  |  | 2P 100A | #01 | 세틀뱅크(구 시스케어)
IDC 2구역 K(상) | O | ON |  | 0 |  |  | 2P 100A | #02 | 코로케션 | K 3-1 상 | O | ON |  | 35.23 |  |  | 2P 100A | #02 | 미디어꾼(구)윈텔)
IDC 2구역 L(상) | O | ON |  |  | 9.17 |  | 2P 100A | #03 | 코로케션 | K 2-2-상 | O | ON |  |  | 5.63 |  | 2P 100A | #03 | 세틀뱅크(구 시스케어)
IDC 2구역 M(상) | O | ON | 7.56 |  |  |  | 2P 100A | #04 | 코로케션 | K 3-2 상 | O | ON | 9.95 |  |  |  | 2P 100A | #04 | 미디어꾼(구)윈텔)
IDC 3구역 N(상) | O | ON |  | 0 |  |  | 2P 100A | #05 | 코로케션 | K 2-3-상 | O | ON |  | 7.95 |  |  | 2P 100A | #05 | 세틀뱅크(구 시스케어)
IDC 3구역 O(상) | O | ON |  |  | 0 |  | 2P 100A | #06 | 코로케션 | K 3-3 상 | O | ON |  |  | 13.64 |  | 2P 100A | #06 | 미디어꾼(구)윈텔)
IDC 3구역 P(상) | O | ON | 9.74 |  |  |  | 2P 100A | #07 | 코로케션 | K 2-4 상 | O | ON | 13.16 |  |  |  | 2P 100A | #07 | 세틀뱅크(구 시스케어)
IDC 3구역 Q(상) | O | ON |  | 15.4 |  |  | 2P 100A | #08 | 코로케션 | K 3-4 상 | O | ON |  | 34.73 |  |  | 2P 100A | #08 | 미디어꾼(구)윈텔)
IDC 3구역 R(상) | O | OFF |  |  | 0 |  | 2P 100A | #09 | 코로케션 | K 1-1 상 | O | ON |  |  | 0 |  | 2P 100A | #09 | BMW
IDC 3구역 S(상) | O | ON | 41.48 |  |  |  | 2P 100A | #10 | 코로케션 | K 1-2 상 | O | ON | 0 |  |  |  | 2P 100A | #10 | 세종시스템케이지
| X | OFF |  | 0 |  |  | 2P 100A | #11 |  |  | X | OFF |  | 0 |  |  | 2P 100A | #11
| X | OFF |  |  | 0 |  | 2P 100A | #12 |  |  | X | OFF |  |  | 0 |  | 2P 100A | #12
|  | 합계: | 70.39 | 15.4 | 9.17 | [6 empty] | 합계: | 47.69 | 77.91 | 19.27
4-DaHall 1-PDU-10 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B5 |  |  |  | 4-DaHall 1-PDU-01 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A1
|  | MAIN 계측값 : | 46.5 | 43.9 | 43.5 | <- 실측값 | [5 empty] | MAIN 계측값 : | 77.6 | 59.1 | 50.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
라온 - 철거 | O | OFF | 0 | 0 | 0 |  | 4P 200A | #01 |  | 정류기 2호기 | O | ON | 1.47 | 1.19 | 1.65 |  | 4P 100A | #01 | 코어룸
CRAC 4E-1호기(20RT) | O | ON | 32.43 | 29.91 | 31.28 |  | 4P 200A | #02 | 항온 | POP E(하) | O | ON | 37.9 |  |  |  | 2P 100A | #02 | 코어룸
CRAC 4E-2호기(20RT) | O | ON | 27.88 | 27.19 | 26.8 |  | 4P 200A | #03 | 항온 | POP B(하) | O | ON |  | 34.95 |  |  | 2P 100A | #03 | 코어룸
|  | 합계: | 60.31 | 57.1 | 58.08 | 0 |  |  |  | POP C(하) | O | ON |  |  | 37.59 |  | 2P 100A | #04 | 코어룸
[10 empty] | POP D(하) | O | ON | 42.43 |  |  |  | 2P 100A | #05 | 코어룸
[10 empty] | IDC 2구역 I(하) | O | ON |  | 24.59 |  |  | 2P 100A | #06 | 코로케션
[10 empty] | IDC 2구역 H(하) | O | ON |  |  | 12.96 |  | 2P 100A | #07 | 코로케션
[11 empty] | X | OFF | 0 |  |  |  | 2P 100A | #08
[11 empty] | X | OFF |  | 0 |  |  | 2P 100A | #09
[12 empty] | 합계: | 81.8 | 60.73 | 52.2
4-DaHall 1-PDU-03 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A2 |  |  |  | 4-DaHall 1-PDU-05 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A3
|  | MAIN 계측값 : | 57.4 | 38.8 | 25.4 | <- 실측값 | [5 empty] | MAIN 계측값 : | 59.5 | 27.6 | 25.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
| X | OFF | 0 | 0 | 0 |  | 4P 100A | #01 |  | IDC 2구역 J(하) | O | ON | 9.72 |  |  |  | 2P 100A | #01 | 코로케션
POP F(하) | O | ON | 33.51 |  |  |  | 2P 100A | #02 | 코어룸 | IDC 2구역 K(하) | O | ON |  | 0 |  |  | 2P 100A | #02 | 코로케션
IDC 1구역 B(하) | O | ON |  | 30.46 |  |  | 2P 100A | #03 | 코어룸 | IDC 2구역 L(하) | O | ON |  |  | 7.8 |  | 2P 100A | #03 | 코로케션
IDC 1구역 C(하) | X | OFF |  |  | 0 |  | 2P 100A | #04 | 코어룸 | IDC 2구역 M(하) | O | ON | 7.54 |  |  |  | 2P 100A | #04 | 코로케션
IDC 1구역 D(하) | O | ON | 6.62 |  |  |  | 2P 100A | #05 | 코로케션 | IDC 3구역 N(하) | O | ON |  | 0 |  |  | 2P 100A | #05 | 코로케션
IDC 1구역 E(하) | O | ON |  | 10.92 |  |  | 2P 100A | #06 | 코로케션 | IDC 3구역 O(하) | O | ON |  |  | 13.18 |  | 2P 100A | #06 | 코로케션
IDC 1구역 F(하) | O | ON |  |  | 29.63 |  | 2P 100A | #07 | 코로케션 | IDC 3구역 P(하) | O | ON | 7.61 |  |  |  | 2P 100A | #07 | 코로케션
IDC 1구역 G(하) | O | ON | 19.89 |  |  |  | 2P 100A | #08 | 코로케션 | IDC 3구역 Q(하) | O | ON |  | 13.85 |  |  | 2P 100A | #08 | 코로케션
| X | OFF |  | 0 |  |  | 2P 100A | #09 |  | IDC 3구역 R(하) | O | OFF |  |  | 0 |  | 2P 100A | #09 | 코로케션
|  | 합계: | 60.02 | 41.38 | 29.63 |  |  |  |  | IDC 3구역 S(하) | O | ON | 37.17 |  |  |  | 2P 100A | #10 | 코로케션
[11 empty] | X | OFF |  | 0 |  |  | 2P 100A | #11
[11 empty] | X | OFF |  |  | 0 |  | 2P 100A | #12
[12 empty] | 합계: | 62.04 | 13.85 | 20.98
4-DaHall 1-PDU-07 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A4 |  |  |  | 4-DaHall 1-PDU-09 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A5
|  | MAIN 계측값 : | 44.7 | 76.7 | 22 | <- 실측값 | [5 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 2-1-하 | O | ON | 21.93 |  |  |  | 2P 100A | #01 | 세틀뱅크(구 시스케어) | 라온(상)- 철거 | X | OFF | 0 | 0 | 0 |  | 4P 200A | #01
K 3-1-하 | O | ON |  | 35.56 |  |  | 2P 100A | #02 | 미디어꾼(구)윈텔) |  | X | OFF | 0 | 0 | 0 |  | 4P 200A | #02
K 2-2-하 | O | ON |  |  | 5.56 |  | 2P 100A | #03 | 세틀뱅크(구 시스케어) |  | X | OFF | 0 | 0 | 0 |  | 4P 200A | #03
K 3-2-하 | O | ON | 10.88 |  |  |  | 2P 100A | #04 | 미디어꾼(구)윈텔) |  |  | 합계: | 0 | 0 | 0
K 2-3-하 | O | ON |  | 6.47 |  |  | 2P 100A | #05 | 세틀뱅크(구 시스케어) | TR Room A,B
K 3-3-하 | O | ON |  |  | 17.09 |  | 2P 100A | #06 | 미디어꾼(구)윈텔) | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 2-4-하 | O | ON | 13.97 |  |  |  | 2P 100A | #07 | 세틀뱅크(구 시스케어) | KB증권 DR(A) - 철거 | X | OFF |  |  |  |  | 4P 320A | #07
K 3-4-하 | O | ON |  | 37.85 |  |  | 2P 100A | #08 | 미디어꾼(구)윈텔)
K 1-1-하 | O | ON |  |  | 0 |  | 2P 100A | #09 | BMW | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 1-2-하 | O | ON | 0 |  |  |  | 2P 100A | #10 | 세종시스템케이지 | KB증권 DR(B) - 철거 | X | OFF |  |  |  |  | 4P 320A | #07
| X | OFF |  | 0 |  |  | 2P 100A | #11
| X | OFF |  |  | 0 |  | 2P 100A | #12
|  | 합계: | 46.78 | 79.88 | 22.65
|  |  |  | 사용량 | 층당 분배
4층 | IDC | IDC |  | 708.09 | 61.52%
| IP | 세종 시스템 |  | 0 | 0%
| 공통 | 세종 시스템
| IP | core room |  | 442.83 | 38.48%
총합 |  |  |  | 1150.92 | 100%
4층 항온항습기 비상 (4층 5RT x 3대, 10RT x 1대) | [8 empty] | Main CB 3P 150A
[11 empty] | MAIN 계측값 : | 24.1 | 22 | 21.9 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | 부하명 | CB 용량 | R | S | T | N | 배선연결 | ON/OFF |  | NO.
4-1 호 | O | ON |  |  |  |  | 3P 50A |  |  | 4-4호 | 3P 50A |  |  |  |  | O | ON
4-2 호 | O | ON |  |  |  | 0 | 3P 50A |  |  |  | 3P 50A |  |  |  |  | X | OFF
4-3 호 | O | ON |  |  |  | 0.1 | 3P 50A |  |  |  | 3P 50A |  |  |  |  | X | OFF
[11 empty] | 합계: | 0 | 0 | 0

## 4층_부하량(월간_AVG)
Date : 2023-11-01 ~ 2023-11-30
4-DaHall 1-PDU-02 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B1 |  |  |  | 4-DaHall 1-PDU-04 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B2
|  | MAIN 계측값 : | 73.5 | 46 | 65.4 | <- 실측값 | [5 empty] | MAIN 계측값 : | 70.2 | 42.2 | 22.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
정류기 1호기 | O | ON | 0.88309 | 0.69963 | 1.0559 |  | 4P 100A | #01 | 코어룸 |  | X | OFF | 0 | 0 | 0 |  | 4P 100A | #01
POP E(상) | O | ON | 35.2048 |  |  |  | 2P 100A | #02 | 코어룸 | POP F(상) | O | ON | 39.4635 |  |  |  | 2P 100A | #02 | 코어룸
POP B(상) | O | ON |  | 32.4976 |  |  | 2P 100A | #03 | 코어룸 | IDC 1구역 B(상) | O | ON |  | 28.2948 |  |  | 2P 100A | #03 | 코어룸
POP C(상) | O | ON |  |  | 36.0017 |  | 2P 100A | #04 | 코어룸 | IDC 1구역 C(상) | X | OFF |  |  | 0 |  | 2P 100A | #04 | 코어룸
POP D(상) | O | ON | 40.9562 |  |  |  | 2P 100A | #05 | 코어룸 | IDC 1구역 D(상) | O | ON | 9.6382 |  |  |  | 2P 100A | #05 | 코로케션
IDC 2구역 I(상) | O | ON |  | 12.3198 |  |  | 2P 100A | #06 | 코로케션 | IDC 1구역 E(상) | O | ON |  | 14.5532 |  |  | 2P 100A | #06 | 코로케션
IDC 2구역 H(상) | O | ON |  |  | 28.991 |  | 2P 100A | #07 | 코로케션 | IDC 1구역 F(상) | O | ON |  |  | 22.2232 |  | 2P 100A | #07 | 코로케션
| X | OFF | 0 |  |  |  | 2P 100A | #08 |  | IDC 1구역 G(상) | O | ON | 22.3842 |  |  |  | 2P 100A | #08 | 코로케션
| X | OFF |  | 0 |  |  | 2P 100A | #09 |  |  | X | OFF |  | 0 |  |  | 2P 100A | #09
|  | 합계: | 77.044 | 45.517 | 66.0486 | [6 empty] | 합계: | 71.4859 | 42.8479 | 22.2232
4-DaHall 1-PDU-06 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B3 |  |  |  | 4-DaHall 1-PDU-08 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B4
|  | MAIN 계측값 : | 67 | 32.4 | 27 | <- 실측값 | [5 empty] | MAIN 계측값 : | 44.8 | 68.4 | 18 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
IDC 2구역 J(상) | O | ON | 10.6138 |  |  |  | 2P 100A | #01 | 코로케션 | K 2-1-상 | O | ON | 22.6604 |  |  |  | 2P 100A | #01 | 세틀뱅크(구 시스케어)
IDC 2구역 K(상) | O | ON |  | 0 |  |  | 2P 100A | #02 | 코로케션 | K 3-1 상 | O | ON |  | 33.2791 |  |  | 2P 100A | #02 | 미디어꾼(구)윈텔)
IDC 2구역 L(상) | O | ON |  |  | 8.9534 |  | 2P 100A | #03 | 코로케션 | K 2-2-상 | O | ON |  |  | 5.4024 |  | 2P 100A | #03 | 세틀뱅크(구 시스케어)
IDC 2구역 M(상) | O | ON | 6.9284 |  |  |  | 2P 100A | #04 | 코로케션 | K 3-2 상 | O | ON | 9.4718 |  |  |  | 2P 100A | #04 | 미디어꾼(구)윈텔)
IDC 3구역 N(상) | O | ON |  | 0 |  |  | 2P 100A | #05 | 코로케션 | K 2-3-상 | O | ON |  | 7.4679 |  |  | 2P 100A | #05 | 세틀뱅크(구 시스케어)
IDC 3구역 O(상) | O | ON |  |  | 0 |  | 2P 100A | #06 | 코로케션 | K 3-3 상 | O | ON |  |  | 12.24 |  | 2P 100A | #06 | 미디어꾼(구)윈텔)
IDC 3구역 P(상) | O | ON | 8.3674 |  |  |  | 2P 100A | #07 | 코로케션 | K 2-4 상 | O | ON | 13.0529 |  |  |  | 2P 100A | #07 | 세틀뱅크(구 시스케어)
IDC 3구역 Q(상) | O | ON |  | 14.0982 |  |  | 2P 100A | #08 | 코로케션 | K 3-4 상 | O | ON |  | 27.0223 |  |  | 2P 100A | #08 | 미디어꾼(구)윈텔)
IDC 3구역 R(상) | O | OFF |  |  | 0 |  | 2P 100A | #09 | 코로케션 | K 1-1 상 | O | ON |  |  | 0 |  | 2P 100A | #09 | BMW
IDC 3구역 S(상) | O | ON | 39.6661 |  |  |  | 2P 100A | #10 | 코로케션 | K 1-2 상 | O | ON | 0 |  |  |  | 2P 100A | #10 | 세종시스템케이지
| X | OFF |  | 0 |  |  | 2P 100A | #11 |  |  | X | OFF |  | 0 |  |  | 2P 100A | #11
| X | OFF |  |  | 0 |  | 2P 100A | #12 |  |  | X | OFF |  |  | 0 |  | 2P 100A | #12
|  | 합계: | 65.5757 | 14.0982 | 8.9534 | [6 empty] | 합계: | 45.1851 | 67.7693 | 17.6424
4-DaHall 1-PDU-10 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - B5 |  |  |  | 4-DaHall 1-PDU-01 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A1
|  | MAIN 계측값 : | 46.5 | 43.9 | 43.5 | <- 실측값 | [5 empty] | MAIN 계측값 : | 77.6 | 59.1 | 50.5 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
라온 - 철거 | O | OFF | 0 | 0 | 0 |  | 4P 200A | #01 |  | 정류기 2호기 | O | ON | 1.2633 | 1.0083 | 1.47 |  | 4P 100A | #01 | 코어룸
CRAC 4E-1호기(20RT) | O | ON | 30.5636 | 27.9705 | 29.4858 |  | 4P 200A | #02 | 항온 | POP E(하) | O | ON | 37.4998 |  |  |  | 2P 100A | #02 | 코어룸
CRAC 4E-2호기(20RT) | O | ON | 15.1943 | 14.7978 | 14.6503 |  | 4P 200A | #03 | 항온 | POP B(하) | O | ON |  | 34.2678 |  |  | 2P 100A | #03 | 코어룸
|  | 합계: | 45.7579 | 42.7684 | 44.136 | 0 |  |  |  | POP C(하) | O | ON |  |  | 37.2639 |  | 2P 100A | #04 | 코어룸
[10 empty] | POP D(하) | O | ON | 41.4804 |  |  |  | 2P 100A | #05 | 코어룸
[10 empty] | IDC 2구역 I(하) | O | ON |  | 23.5345 |  |  | 2P 100A | #06 | 코로케션
[10 empty] | IDC 2구역 H(하) | O | ON |  |  | 12.608 |  | 2P 100A | #07 | 코로케션
[11 empty] | X | OFF | 0 |  |  |  | 2P 100A | #08
[11 empty] | X | OFF |  | 0 |  |  | 2P 100A | #09
[12 empty] | 합계: | 80.2434 | 58.8105 | 51.3418
4-DaHall 1-PDU-03 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A2 |  |  |  | 4-DaHall 1-PDU-05 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A3
|  | MAIN 계측값 : | 57.4 | 38.8 | 25.4 | <- 실측값 | [5 empty] | MAIN 계측값 : | 59.5 | 27.6 | 25.2 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
| X | OFF | 0 | 0 | 0 |  | 4P 100A | #01 |  | IDC 2구역 J(하) | O | ON | 8.9695 |  |  |  | 2P 100A | #01 | 코로케션
POP F(하) | O | ON | 32.2199 |  |  |  | 2P 100A | #02 | 코어룸 | IDC 2구역 K(하) | O | ON |  | 0 |  |  | 2P 100A | #02 | 코로케션
IDC 1구역 B(하) | O | ON |  | 28.4408 |  |  | 2P 100A | #03 | 코어룸 | IDC 2구역 L(하) | O | ON |  |  | 7.7355 |  | 2P 100A | #03 | 코로케션
IDC 1구역 C(하) | X | OFF |  |  | 0 |  | 2P 100A | #04 | 코어룸 | IDC 2구역 M(하) | O | ON | 7.2205 |  |  |  | 2P 100A | #04 | 코로케션
IDC 1구역 D(하) | O | ON | 6.3018 |  |  |  | 2P 100A | #05 | 코로케션 | IDC 3구역 N(하) | O | ON |  | 0 |  |  | 2P 100A | #05 | 코로케션
IDC 1구역 E(하) | O | ON |  | 10.3842 |  |  | 2P 100A | #06 | 코로케션 | IDC 3구역 O(하) | O | ON |  |  | 12.8628 |  | 2P 100A | #06 | 코로케션
IDC 1구역 F(하) | O | ON |  |  | 28.4161 |  | 2P 100A | #07 | 코로케션 | IDC 3구역 P(하) | O | ON | 6.5082 |  |  |  | 2P 100A | #07 | 코로케션
IDC 1구역 G(하) | O | ON | 18.5092 |  |  |  | 2P 100A | #08 | 코로케션 | IDC 3구역 Q(하) | O | ON |  | 11.8335 |  |  | 2P 100A | #08 | 코로케션
| X | OFF |  | 0 |  |  | 2P 100A | #09 |  | IDC 3구역 R(하) | O | OFF |  |  | 0 |  | 2P 100A | #09 | 코로케션
|  | 합계: | 57.0308 | 38.8249 | 28.4161 |  |  |  |  | IDC 3구역 S(하) | O | ON | 34.7027 |  |  |  | 2P 100A | #10 | 코로케션
[11 empty] | X | OFF |  | 0 |  |  | 2P 100A | #11
[11 empty] | X | OFF |  |  | 0 |  | 2P 100A | #12
[12 empty] | 합계: | 57.401 | 11.8335 | 20.5983
4-DaHall 1-PDU-07 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A4 |  |  |  | 4-DaHall 1-PDU-09 |  |  | Main CB 4P 300A |  |  | PDU : SEL1 - 4-1 - A5
|  | MAIN 계측값 : | 44.7 | 76.7 | 22 | <- 실측값 | [5 empty] | MAIN 계측값 : | 0 | 0 | 0 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고 | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 2-1-하 | O | ON | 20.3838 |  |  |  | 2P 100A | #01 | 세틀뱅크(구 시스케어) | 라온(상)- 철거 | X | OFF | 0 | 0 | 0 |  | 4P 200A | #01
K 3-1-하 | O | ON |  | 33.5635 |  |  | 2P 100A | #02 | 미디어꾼(구)윈텔) |  | X | OFF | 0 | 0 | 0 |  | 4P 200A | #02
K 2-2-하 | O | ON |  |  | 5.3006 |  | 2P 100A | #03 | 세틀뱅크(구 시스케어) |  | X | OFF | 0 | 0 | 0 |  | 4P 200A | #03
K 3-2-하 | O | ON | 10.3767 |  |  |  | 2P 100A | #04 | 미디어꾼(구)윈텔) |  |  | 합계: | 0 | 0 | 0
K 2-3-하 | O | ON |  | 6.0186 |  |  | 2P 100A | #05 | 세틀뱅크(구 시스케어) | TR Room A,B
K 3-3-하 | O | ON |  |  | 15.6783 |  | 2P 100A | #06 | 미디어꾼(구)윈텔) | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 2-4-하 | O | ON | 13.8234 |  |  |  | 2P 100A | #07 | 세틀뱅크(구 시스케어) | KB증권 DR(A) - 철거 | X | OFF |  |  |  |  | 4P 320A | #07
K 3-4-하 | O | ON |  | 34.3054 |  |  | 2P 100A | #08 | 미디어꾼(구)윈텔)
K 1-1-하 | O | ON |  |  | 0 |  | 2P 100A | #09 | BMW | 부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 | CB NO. | 비고
K 1-2-하 | O | ON | 0 |  |  |  | 2P 100A | #10 | 세종시스템케이지 | KB증권 DR(B) - 철거 | X | OFF |  |  |  |  | 4P 320A | #07
| X | OFF |  | 0 |  |  | 2P 100A | #11
| X | OFF |  |  | 0 |  | 2P 100A | #12
|  | 합계: | 44.5839 | 73.8875 | 20.9789
|  |  |  | 사용량 | 층당 분배
4층 | IDC | IDC |  | 658.3703 | 60.49%
| IP | 세종 시스템 |  | 0 | 0%
| 공통 | 세종 시스템
| IP | core room |  | 429.9711 | 39.51%
총합 |  |  |  | 1088.3413 | 100%
4층 항온항습기 비상 (4층 5RT x 3대, 10RT x 1대) | [8 empty] | Main CB 3P 150A
[11 empty] | MAIN 계측값 : | 24.1 | 22 | 21.9 | <- 실측값
부하명 | 배선연결 | ON/OFF | R | S | T | N | CB 용량 |  | NO. | 부하명 | CB 용량 | R | S | T | N | 배선연결 | ON/OFF |  | NO.
4-1 호 | O | ON |  |  |  |  | 3P 50A |  |  | 4-4호 | 3P 50A |  |  |  |  | O | ON
4-2 호 | O | ON |  |  |  | 0 | 3P 50A |  |  |  | 3P 50A |  |  |  |  | X | OFF
4-3 호 | O | ON |  |  |  | 0.1 | 3P 50A |  |  |  | 3P 50A |  |  |  |  | X | OFF
[11 empty] | 합계: | 0 | 0 | 0

## 7층_부하량
장비명 | 분기번호 | MIN |  |  | MAX |  |  | AVG
|  | R | S | T | R | S | T | R | S | T
7-DaHall 1-RPP-01 | 1 | 0 |  |  | 0
7-DaHall 1-RPP-01 | 2 | 0 |  |  | 0
7-DaHall 1-RPP-01 | 3 |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 4 |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 5 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 6 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 7 | 0 |  |  | 0
7-DaHall 1-RPP-01 | 8 | 0 |  |  | 2.51 |  |  | 2.295
7-DaHall 1-RPP-01 | 9 |  | 0 |  |  | 2.68 |  |  | 2.4182
7-DaHall 1-RPP-01 | 10 |  | 0.99 |  |  | 1.69 |  |  | 1.5543
7-DaHall 1-RPP-01 | 11 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 12 |  |  | 1.45 |  |  | 5.48 |  |  | 3.5739
7-DaHall 1-RPP-01 | 13 | 0 |  |  | 1.53 |  |  | 1.4136
7-DaHall 1-RPP-01 | 14 | 3.11 |  |  | 7.19 |  |  | 5.8455
7-DaHall 1-RPP-01 | 15 |  | 0 |  |  | 4.81 |  |  | 4.0936
7-DaHall 1-RPP-01 | 16 |  | 2.5 |  |  | 6.38 |  |  | 3.2014
7-DaHall 1-RPP-01 | 17 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 18 |  |  | 0 |  |  | 2.18 |  |  | 1.4665
7-DaHall 1-RPP-01 | 19 | 0.99 |  |  | 5.38 |  |  | 1.7132
7-DaHall 1-RPP-01 | 20 | 0 |  |  | 1.52 |  |  | 1.4647
7-DaHall 1-RPP-01 | 21 |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 22 |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 23 |  |  | 0 |  |  | 1.5 |  |  | 1.4198
7-DaHall 1-RPP-01 | 24 |  |  | 0 |  |  | 2.29 |  |  | 2.1344
7-DaHall 1-RPP-01 | 25 | 1.5 |  |  | 1.69 |  |  | 1.5435
7-DaHall 1-RPP-01 | 26 | 0 |  |  | 5.08 |  |  | 2.137
7-DaHall 1-RPP-01 | 27 |  | 2.96 |  |  | 7.12 |  |  | 3.8387
7-DaHall 1-RPP-01 | 28 |  | 0.87 |  |  | 4.48 |  |  | 1.8009
7-DaHall 1-RPP-01 | 29 |  |  | 1.29 |  |  | 4.81 |  |  | 3.7843
7-DaHall 1-RPP-01 | 30 |  |  | 1.5 |  |  | 5.98 |  |  | 3.8632
7-DaHall 1-RPP-01 | 31 | 0 |  |  | 6.45 |  |  | 5.6071
7-DaHall 1-RPP-01 | 32 | 0 |  |  | 0
7-DaHall 1-RPP-01 | 33 |  | 0 |  |  | 0
7-DaHall 1-RPP-01 | 34 |  | 0 |  |  | 4.2 |  |  | 1.4248
7-DaHall 1-RPP-01 | 35 |  |  | 0 |  |  | 9.68 |  |  | 4.0589
7-DaHall 1-RPP-01 | 36 |  |  | 0 |  |  | 4.25 |  |  | 3.4252
7-DaHall 1-RPP-01 | 37 | 0 |  |  | 5.39 |  |  | 4.639
7-DaHall 1-RPP-01 | 38 | 0 |  |  | 3.99 |  |  | 2.4542
7-DaHall 1-RPP-01 | 39 |  | 0 |  |  | 2.31 |  |  | 2.0833
7-DaHall 1-RPP-01 | 40 |  | 0 |  |  | 4.99 |  |  | 4.8317
7-DaHall 1-PDU-02 | 1 |  | 0 |  |  | 0
7-DaHall 1-PDU-02 | 2 |  | 0 |  |  | 5.89 |  |  | 5.4828
7-DaHall 1-PDU-02 | 3 |  |  | 0 |  |  | 6.13 |  |  | 5.5322
7-DaHall 1-PDU-02 | 4 |  |  | 0 |  |  | 5.78 |  |  | 5.3789
7-DaHall 1-PDU-02 | 5 | 0 |  |  | 6.05 |  |  | 5.5401
7-DaHall 1-PDU-02 | 6 | 0 |  |  | 5.72 |  |  | 5.3234
7-DaHall 1-PDU-02 | 7 |  | 5.24 |  |  | 5.78 |  |  | 5.6451
7-DaHall 1-PDU-02 | 8 |  | 0 |  |  | 1.09 |  |  | 1.011
7-DaHall 1-PDU-02 | 9 |  |  | 3.26 |  |  | 6.04 |  |  | 5.1452
7-DaHall 1-PDU-02 | 10 |  |  | 2.82 |  |  | 9.39 |  |  | 4.3618
7-DaHall 1-PDU-02 | 11 | 4 |  |  | 5.71 |  |  | 5.4275
7-DaHall 1-PDU-02 | 12 | 0 |  |  | 3.22 |  |  | 2.6773
7-DaHall 1-PDU-02 | 13 |  | 2.33 |  |  | 5.26 |  |  | 4.6923
7-DaHall 1-PDU-02 | 14 |  | 2.97 |  |  | 4.19 |  |  | 3.2196
7-DaHall 1-PDU-02 | 15 |  |  | 1.08 |  |  | 2.49 |  |  | 1.1919
7-DaHall 1-PDU-02 | 16 |  |  | 2.38 |  |  | 3.77 |  |  | 3.0965
7-DaHall 1-PDU-02 | 17 | 3.26 |  |  | 8.53 |  |  | 4.2887
7-DaHall 1-PDU-02 | 18 | 1.74 |  |  | 6.82 |  |  | 2.6467
7-DaHall 1-PDU-02 | 19 |  | 0 |  |  | 9.22 |  |  | 8.6048
7-DaHall 1-PDU-02 | 20 |  | 1.84 |  |  | 3.06 |  |  | 1.9609
7-DaHall 1-PDU-02 | 21 |  |  | 0 |  |  | 4.65 |  |  | 4.0313
7-DaHall 1-PDU-02 | 22 |  |  | 0 |  |  | 1.99 |  |  | 1.9178
7-DaHall 1-PDU-02 | 23 | 0 |  |  | 3.7 |  |  | 2.6238
7-DaHall 1-PDU-02 | 24 | 0 |  |  | 2.41 |  |  | 2.2107
7-DaHall 1-PDU-02 | 25 |  | 0.89 |  |  | 2.35 |  |  | 2.064
7-DaHall 1-PDU-02 | 26 |  | 0.56 |  |  | 3.65 |  |  | 3.0434
7-DaHall 1-PDU-02 | 27 |  |  | 0.23 |  |  | 4.23 |  |  | 3.1066
7-DaHall 1-PDU-02 | 28 |  |  | 0 |  |  | 5.87 |  |  | 5.6621
7-DaHall 1-PDU-02 | 29 | 0 |  |  | 2.49 |  |  | 1.8172
7-DaHall 1-PDU-02 | 30 | 0 |  |  | 0.68 |  |  | 0.5586
7-DaHall 1-PDU-02 | 31 |  | 0 |  |  | 3.76 |  |  | 3.2471
7-DaHall 1-PDU-02 | 32 |  | 1.89 |  |  | 3.54 |  |  | 2.1671
7-DaHall 1-PDU-02 | 33 |  |  | 0 |  |  | 8.58 |  |  | 8.1425
7-DaHall 1-PDU-02 | 34 |  |  | 0 |  |  | 3.22 |  |  | 2.8911
7-DaHall 1-PDU-02 | 35 | 2.92 |  |  | 6.81 |  |  | 5.8439
7-DaHall 1-PDU-02 | 36 | 0 |  |  | 1.77 |  |  | 1.6451
7-DaHall 1-PDU-02 | 37 |  | 0 |  |  | 3.04 |  |  | 1.2372
7-DaHall 1-PDU-02 | 38 |  | 1.91 |  |  | 4.11 |  |  | 3.5214
7-DaHall 1-PDU-02 | 39 |  |  | 1.83 |  |  | 2.4 |  |  | 1.9337
7-DaHall 1-PDU-02 | 40 |  |  | 2.82 |  |  | 3.65 |  |  | 3.0971
7-DaHall 1-PDU-02 | 41 | 0 |  |  | 5.87 |  |  | 5.4582
7-DaHall 1-PDU-02 | 42 | 0.52 |  |  | 5.21 |  |  | 3.9346
7-DaHall 1-PDU-02 | 43 |  | 0 |  |  | 1.91 |  |  | 1.7774
7-DaHall 1-PDU-02 | 44 |  | 0 |  |  | 3.32 |  |  | 1.8154
7-DaHall 1-PDU-02 | 45 |  |  | 0 |  |  | 0
7-DaHall 1-PDU-02 | 46 |  |  | 0 |  |  | 4.03 |  |  | 3.6165
7-DaHall 1-PDU-02 | 47 | 0 |  |  | 3.25 |  |  | 2.7992
7-DaHall 1-PDU-02 | 48 | 1.9 |  |  | 5.27 |  |  | 2.4513
7-DaHall 1-PDU-02 | 49 |  | 0.88 |  |  | 3.26 |  |  | 1.081
7-DaHall 1-PDU-02 | 50 |  | 0 |  |  | 4.01 |  |  | 3.4265
7-DaHall 1-PDU-02 | 51 |  |  | 0.55 |  |  | 1.94 |  |  | 0.81052
7-DaHall 1-PDU-02 | 52 |  |  | 0 |  |  | 3.8 |  |  | 3.2826
7-DaHall 1-PDU-02 | 53 | 0 |  |  | 0.24 |  |  | 0.22466
7-DaHall 1-PDU-02 | 54 | 0 |  |  | 0
7-DaHall 1-PDU-01 | 1 |  | 0 |  |  | 0
7-DaHall 1-PDU-01 | 2 |  | 0 |  |  | 2.53 |  |  | 2.2574
7-DaHall 1-PDU-01 | 3 |  |  | 2.07 |  |  | 5.08 |  |  | 2.954
7-DaHall 1-PDU-01 | 4 |  |  | 0 |  |  | 6.02 |  |  | 5.6083
7-DaHall 1-PDU-01 | 5 | 4.88 |  |  | 7.44 |  |  | 5.2297
7-DaHall 1-PDU-01 | 6 | 0 |  |  | 6.86 |  |  | 6.3779
7-DaHall 1-PDU-01 | 7 |  | 5.95 |  |  | 6.67 |  |  | 6.0984
7-DaHall 1-PDU-01 | 8 |  | 0.79 |  |  | 2.28 |  |  | 1.6519
7-DaHall 1-PDU-01 | 9 |  |  | 2.78 |  |  | 7.46 |  |  | 5.6284
7-DaHall 1-PDU-01 | 10 |  |  | 2.08 |  |  | 4.11 |  |  | 2.8402
7-DaHall 1-PDU-01 | 11 | 4.15 |  |  | 6.88 |  |  | 6.3336
7-DaHall 1-PDU-01 | 12 | 0 |  |  | 2.47 |  |  | 2.0299
7-DaHall 1-PDU-01 | 13 |  | 2.02 |  |  | 6.69 |  |  | 5.7529
7-DaHall 1-PDU-01 | 14 |  | 3.2 |  |  | 4.57 |  |  | 4.0892
7-DaHall 1-PDU-01 | 15 |  |  | 0 |  |  | 0.79 |  |  | 0.7122
7-DaHall 1-PDU-01 | 16 |  |  | 1.65 |  |  | 4.58 |  |  | 2.7079
7-DaHall 1-PDU-01 | 17 | 2.76 |  |  | 8.94 |  |  | 3.9791
7-DaHall 1-PDU-01 | 18 | 1.75 |  |  | 7.17 |  |  | 2.7001
7-DaHall 1-PDU-01 | 19 |  | 0 |  |  | 4.17 |  |  | 3.8195
7-DaHall 1-PDU-01 | 20 |  | 0.9 |  |  | 1.89 |  |  | 1.7184
7-DaHall 1-PDU-01 | 21 |  |  | 1.06 |  |  | 4.44 |  |  | 3.462
7-DaHall 1-PDU-01 | 22 |  |  | 0 |  |  | 1.77 |  |  | 1.6897
7-DaHall 1-PDU-01 | 23 | 0 |  |  | 2.43 |  |  | 1.8628
7-DaHall 1-PDU-01 | 24 | 0 |  |  | 2.83 |  |  | 2.65
7-DaHall 1-PDU-01 | 25 |  | 0 |  |  | 2.24 |  |  | 1.9762
7-DaHall 1-PDU-01 | 26 |  | 0 |  |  | 3.85 |  |  | 3.3292
7-DaHall 1-PDU-01 | 27 |  |  | 0 |  |  | 3.49 |  |  | 3.2123
7-DaHall 1-PDU-01 | 28 |  |  | 0 |  |  | 6.38 |  |  | 5.4264
7-DaHall 1-PDU-01 | 29 | 0 |  |  | 0.38 |  |  | 0.12754
7-DaHall 1-PDU-01 | 30 | 0 |  |  | 0.35 |  |  | 0.34146
7-DaHall 1-PDU-01 | 31 |  | 1.54 |  |  | 4.59 |  |  | 3.983
7-DaHall 1-PDU-01 | 32 |  | 2.1 |  |  | 2.85 |  |  | 2.205
7-DaHall 1-PDU-01 | 33 |  |  | 0 |  |  | 8.88 |  |  | 8.4039
7-DaHall 1-PDU-01 | 34 |  |  | 0 |  |  | 4.58 |  |  | 4.0287
7-DaHall 1-PDU-01 | 35 | 2.27 |  |  | 7.16 |  |  | 5.9127
7-DaHall 1-PDU-01 | 36 | 0 |  |  | 1.78 |  |  | 1.6549
7-DaHall 1-PDU-01 | 37 |  | 0 |  |  | 1.89 |  |  | 1.7538
7-DaHall 1-PDU-01 | 38 |  | 1.71 |  |  | 3.05 |  |  | 2.6066
7-DaHall 1-PDU-01 | 39 |  |  | 1.03 |  |  | 2.78 |  |  | 1.3576
7-DaHall 1-PDU-01 | 40 |  |  | 3.16 |  |  | 3.56 |  |  | 3.3337
7-DaHall 1-PDU-01 | 41 | 1.05 |  |  | 5.61 |  |  | 1.9029
7-DaHall 1-PDU-01 | 42 | 0.35 |  |  | 3.64 |  |  | 2.8907
7-DaHall 1-PDU-01 | 43 |  | 0 |  |  | 2.18 |  |  | 1.9771
7-DaHall 1-PDU-01 | 44 |  | 0 |  |  | 6.82 |  |  | 5.6326
7-DaHall 1-PDU-01 | 45 |  |  | 0 |  |  | 0
7-DaHall 1-PDU-01 | 46 |  |  | 0 |  |  | 2.95 |  |  | 2.6241
7-DaHall 1-PDU-01 | 47 | 0 |  |  | 3.45 |  |  | 3.1056
7-DaHall 1-PDU-01 | 48 | 1.71 |  |  | 3.63 |  |  | 2.0633
7-DaHall 1-PDU-01 | 49 |  | 0 |  |  | 6.66 |  |  | 5.4363
7-DaHall 1-PDU-01 | 50 |  | 0 |  |  | 0
7-DaHall 1-PDU-01 | 51 |  |  | 0 |  |  | 1.74 |  |  | 1.6246
7-DaHall 1-PDU-01 | 52 |  |  | 0 |  |  | 4.06 |  |  | 0.0086132
7-DaHall 1-PDU-01 | 53 | 0 |  |  | 0
7-DaHall 1-PDU-01 | 54 | 0.34 |  |  | 0.35 |  |  | 0.34024
7-DaHall 1-RPP-02 | 1 | 0 |  |  | 0
7-DaHall 1-RPP-02 | 2 | 0.54 |  |  | 3.02 |  |  | 1.6103
7-DaHall 1-RPP-02 | 3 |  | 0 |  |  | 0.56 |  |  | 0.5364
7-DaHall 1-RPP-02 | 4 |  | 0 |  |  | 1.13 |  |  | 1.0467
7-DaHall 1-RPP-02 | 5 |  |  | 0 |  |  | 1.84 |  |  | 1.1637
7-DaHall 1-RPP-02 | 6 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 7 | 1.11 |  |  | 2.86 |  |  | 1.4434
7-DaHall 1-RPP-02 | 8 | 1.76 |  |  | 4.75 |  |  | 3.7722
7-DaHall 1-RPP-02 | 9 |  | 0.84 |  |  | 4.5 |  |  | 1.4678
7-DaHall 1-RPP-02 | 10 |  | 0 |  |  | 0.72 |  |  | 0.65395
7-DaHall 1-RPP-02 | 11 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 12 |  |  | 0 |  |  | 4.72 |  |  | 4.3444
7-DaHall 1-RPP-02 | 13 | 0 |  |  | 2.86 |  |  | 2.7752
7-DaHall 1-RPP-02 | 14 | 5.68 |  |  | 15.79 |  |  | 12.9108
7-DaHall 1-RPP-02 | 15 |  | 0 |  |  | 1.78 |  |  | 1.7234
7-DaHall 1-RPP-02 | 16 |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 17 |  |  | 0 |  |  | 4.52 |  |  | 3.1283
7-DaHall 1-RPP-02 | 18 |  |  | 0 |  |  | 2.91 |  |  | 2.4131
7-DaHall 1-RPP-02 | 19 | 0 |  |  | 6.61 |  |  | 5.5701
7-DaHall 1-RPP-02 | 20 | 0 |  |  | 8.08 |  |  | 2.7515
7-DaHall 1-RPP-02 | 21 |  | 0 |  |  | 2.45 |  |  | 1.5628
7-DaHall 1-RPP-02 | 22 |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 23 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 24 |  |  | 1.44 |  |  | 4.78 |  |  | 2.5932
7-DaHall 1-RPP-02 | 25 | 0 |  |  | 0.72 |  |  | 0.62625
7-DaHall 1-RPP-02 | 26 | 0.3 |  |  | 6.8 |  |  | 1.2034
7-DaHall 1-RPP-02 | 27 |  | 5.63 |  |  | 15.17 |  |  | 7.3389
7-DaHall 1-RPP-02 | 28 |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 29 |  |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 30 |  |  | 0 |  |  | 2.67 |  |  | 1.8933
7-DaHall 1-RPP-02 | 31 | 0 |  |  | 0
7-DaHall 1-RPP-02 | 32 | 1.48 |  |  | 4.18 |  |  | 3.2696
7-DaHall 1-RPP-02 | 33 |  | 0 |  |  | 0.48 |  |  | 0.43786
7-DaHall 1-RPP-02 | 34 |  | 0 |  |  | 0
7-DaHall 1-RPP-02 | 35 |  |  | 1.72 |  |  | 3 |  |  | 2.4571
7-DaHall 1-RPP-02 | 36 |  |  | 3.37 |  |  | 8.03 |  |  | 6.6171
7-DaHall 1-RPP-02 | 37 | 0 |  |  | 6.77 |  |  | 5.8717
7-DaHall 1-RPP-02 | 38 | 4.88 |  |  | 7.94 |  |  | 5.3995
7-DaHall 1-RPP-02 | 39 |  | 2.43 |  |  | 8.07 |  |  | 3.1211
7-DaHall 1-RPP-02 | 40 |  | 0 |  |  | 0
7-DaHall 1-RPP-03 | 1 | 1.17 |  |  | 1.2 |  |  | 1.179
7-DaHall 1-RPP-03 | 2 | 0.94 |  |  | 2.88 |  |  | 1.3236
7-DaHall 1-RPP-03 | 3 |  | 2.75 |  |  | 3.49 |  |  | 2.9106
7-DaHall 1-RPP-03 | 4 |  | 0 |  |  | 2.63 |  |  | 1.9266
7-DaHall 1-RPP-03 | 5 |  |  | 2.73 |  |  | 3.5 |  |  | 3.3004
7-DaHall 1-RPP-03 | 6 |  |  | 0.94 |  |  | 1.77 |  |  | 1.5083
7-DaHall 1-RPP-03 | 7 | 0 |  |  | 2.64 |  |  | 2.437
7-DaHall 1-RPP-03 | 8 | 1.66 |  |  | 2.16 |  |  | 1.9608
7-DaHall 1-RPP-03 | 9 |  | 2.05 |  |  | 2.99 |  |  | 2.6297
7-DaHall 1-RPP-03 | 10 |  | 2.57 |  |  | 2.79 |  |  | 2.6178
7-DaHall 1-RPP-04 | 1 | 1.17 |  |  | 1.19 |  |  | 1.1786
7-DaHall 1-RPP-04 | 2 | 1.47 |  |  | 3.39 |  |  | 2.0054
7-DaHall 1-RPP-04 | 3 |  | 3.33 |  |  | 4.54 |  |  | 3.5632
7-DaHall 1-RPP-04 | 4 |  | 0 |  |  | 5.55 |  |  | 4.3943
7-DaHall 1-RPP-04 | 5 |  |  | 1.61 |  |  | 4.56 |  |  | 3.9282
7-DaHall 1-RPP-04 | 6 |  |  | 1.2 |  |  | 1.84 |  |  | 1.3512
7-DaHall 1-RPP-04 | 7 | 0 |  |  | 5.52 |  |  | 4.0821
7-DaHall 1-RPP-04 | 8 | 1.29 |  |  | 2.16 |  |  | 1.859
7-DaHall 1-RPP-04 | 9 |  | 1.61 |  |  | 2.16 |  |  | 1.7102
7-DaHall 1-RPP-04 | 10 |  | 2.79 |  |  | 3.01 |  |  | 2.8469
7-DaHall 1-PDU-03 | 1 | 23.68 | 12.05 | 17.05 | 27.41 | 15.7 | 28.82 | 25.3735 | 12.9936 | 19.0699
7-DaHall 1-PDU-03 | 2 | 2.37 | 1.8 | 5.06 | 7.09 | 8.25 | 9.83 | 3.5731 | 3.5363 | 7.6977
7-DaHall 1-PDU-03 | 3 | 0 | 0 | 0 | 7.1 | 8.29 | 5.19 | 6.4377 | 7.8114 | 4.8932
7-DaHall 1-PDU-03 | 4 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-03 | 5 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-03 | 6 | 2.41 | 1.92 | 6.64 | 59.06 | 59.71 | 62.09 | 42.4126 | 42.8076 | 45.9105
7-DaHall 1-PDU-03 | 7 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-03 | 8 | 0 | 0 | 0 | 51.81 | 52.37 | 54.75 | 48.1898 | 48.7565 | 50.9272
7-DaHall 1-PDU-03 | 9 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-03 | 10 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-04 | 1 | 39.61 | 40.33 | 42.89 | 47.16 | 47.56 | 50.14 | 45.9711 | 46.8483 | 49.3899
7-DaHall 1-PDU-04 | 2 | 0 | 0 | 0 | 43.78 | 17.88 | 24.36 | 39.3655 | 11.4363 | 20.3818
7-DaHall 1-PDU-04 | 3 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-04 | 4 | 0 | 0 | 0 | 10.47 | 7.93 | 5.85 | 8.7539 | 7.4589 | 5.5276
7-DaHall 1-PDU-04 | 5 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-04 | 6 | 0 | 0 | 0 | 38.99 | 17.76 | 23.97 | 34.8428 | 11.1817 | 19.5182
7-DaHall 1-PDU-04 | 7 | 0 | 0 | 0 | 10.51 | 7.83 | 5.84 | 8.9521 | 7.1636 | 5.4091
7-DaHall 1-PDU-04 | 8 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-04 | 9 | 0 | 0 | 0 | 0 | 0 | 0
7-DaHall 1-PDU-04 | 10 | 0 | 0 | 0 | 0 | 0 | 0

## 6층_부하량
장비명 | 분기번호 | MIN |  |  | MAX |  |  | AVG
|  | R | S | T | R | S | T | R | S | T
6-DaHall 1-CEP-05 | 1 | 0 | 0.75 | 0.67 | 59.42 | 60.51 | 58.78 | 0.17477 | 0.78112 | 0.69841
6-DaHall 1-CEP-05 | 2 | 0 | 0 | 0 | 29.55 | 27.9 | 30.08 | 0.12683 | 0.12305 | 0.13001
6-DaHall 1-CEP-05 | 3 | 0 | 0 | 0 | 0 | 0 | 0
6-DaHall 1-CEP-05 | 4 | 0 | 0 | 0 | 0 | 0 | 0
6-DaHall 1-CEP-05 | 5 | 0 | 0 | 0 | 0 | 0 | 0
6-DaHall 1-CEP-05 | 6 | 0 | 0 | 0 | 0 | 0 | 0
6-DaHall 1-CEP-05 | 7 | 0 | 0 | 0 | 0 | 0 | 0
6-DaHall 1-CEP-05 | 8 | 0 | 0 | 0 | 0 | 0 | 0
6-DaHall 1-CEP-05 | 9 | 0 | 0 | 0 | 0 | 0 | 0
6-DaHall 1-CEP-05 | 10 | 0 | 0 | 0 | 0 | 0 | 0
6-DaHall 1-CEP-05 | 11 | 0 | 0 | 0 | 53.54 | 53.5 | 66.13 | 6.2945 | 6.4056 | 8.1714
6-DaHall 1-CEP-05 | 12 | 0 |  |  | 0
6-DaHall 1-CEP-05 | 13 | 0 |  |  | 0
6-DaHall 1-CEP-05 | 14 |  | 0 |  |  | 48.86 |  |  | 8.5118
6-DaHall 1-CEP-05 | 15 |  | 0 |  |  | 15 |  |  | 10.3192
6-DaHall 1-CEP-05 | 16 |  |  | 0 |  |  | 8 |  |  | 7.4438
6-DaHall 1-CEP-05 | 17 |  |  | 0 |  |  | 13.74 |  |  | 6.3162
6-DaHall 1-PDU-13 | 1 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 2 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 3 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 4 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 5 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 6 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 7 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 8 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 9 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 10 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 11 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 12 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 13 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 14 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 15 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 16 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 17 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 18 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 19 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 20 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 21 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 22 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 23 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 24 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 25 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 26 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 27 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 28 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 29 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 30 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 31 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 32 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 33 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 34 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 35 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 36 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 37 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 38 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 39 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 40 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 41 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 42 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 43 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 44 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 45 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 46 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 47 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 48 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 49 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 50 |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 51 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 52 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-13 | 53 | 0 |  |  | 0
6-DaHall 1-PDU-13 | 54 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 1 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 2 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 3 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 4 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 5 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 6 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 7 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 8 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 9 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 10 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 11 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 12 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 13 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 14 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 15 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 16 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 17 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 18 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 19 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 20 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 21 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 22 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 23 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 24 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 25 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 26 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 27 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 28 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 29 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 30 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 31 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 32 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 33 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 34 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 35 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 36 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 37 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 38 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 39 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 40 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 41 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 42 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 43 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 44 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 45 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 46 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 47 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 48 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 49 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 50 |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 51 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 52 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-14 | 53 | 0 |  |  | 0
6-DaHall 1-PDU-14 | 54 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 1 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 2 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 3 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 4 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 5 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 6 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 7 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 8 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 9 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 10 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 11 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 12 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 13 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 14 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 15 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 16 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 17 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 18 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 19 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 20 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 21 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 22 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 23 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 24 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 25 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 26 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 27 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 28 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 29 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 30 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 31 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 32 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 33 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 34 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 35 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 36 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 37 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 38 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 39 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 40 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 41 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 42 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 43 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 44 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 45 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 46 |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 47 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 48 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-09 | 49 | 0 |  |  | 0
6-DaHall 1-PDU-09 | 50 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 1 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 2 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 3 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 4 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 5 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 6 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 7 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 8 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 9 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 10 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 11 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 12 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 13 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 14 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 15 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 16 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 17 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 18 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 19 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 20 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 21 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 22 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 23 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 24 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 25 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 26 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 27 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 28 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 29 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 30 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 31 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 32 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 33 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 34 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 35 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 36 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 37 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 38 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 39 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 40 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 41 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 42 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 43 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 44 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 45 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 46 |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 47 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 48 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-10 | 49 | 0 |  |  | 0
6-DaHall 1-PDU-10 | 50 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 1 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 2 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 3 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 4 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 5 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 6 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 7 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 8 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 9 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 10 |  | 0 |  |  | 6.01 |  |  | 4.9703
6-DaHall 1-PDU-11 | 11 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 12 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 13 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 14 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 15 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 16 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 17 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 18 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 19 | 0 |  |  | 6.52 |  |  | 5.1988
6-DaHall 1-PDU-11 | 20 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 21 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 22 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 23 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 24 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 25 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 26 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 27 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 28 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 29 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 30 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 31 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 32 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 33 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 34 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 35 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 36 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 37 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 38 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 39 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 40 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 41 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 42 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 43 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 44 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 45 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 46 |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 47 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 48 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-11 | 49 | 0 |  |  | 0
6-DaHall 1-PDU-11 | 50 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 1 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 2 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 3 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 4 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 5 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 6 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 7 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 8 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 9 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 10 |  | 0 |  |  | 6.02 |  |  | 4.9403
6-DaHall 1-PDU-12 | 11 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 12 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 13 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 14 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 15 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 16 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 17 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 18 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 19 | 0 |  |  | 6.54 |  |  | 5.1819
6-DaHall 1-PDU-12 | 20 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 21 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 22 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 23 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 24 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 25 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 26 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 27 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 28 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 29 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 30 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 31 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 32 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 33 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 34 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 35 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 36 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 37 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 38 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 39 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 40 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 41 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 42 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 43 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 44 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 45 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 46 |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 47 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 48 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-12 | 49 | 0 |  |  | 0
6-DaHall 1-PDU-12 | 50 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 1 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 2 | 0 |  |  | 2 |  |  | 1.9073
6-DaHall 1-PDU-01 | 3 |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 4 |  | 0 |  |  | 9.68 |  |  | 3.3293
6-DaHall 1-PDU-01 | 5 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 6 |  |  | 0 |  |  | 3.19 |  |  | 2.9359
6-DaHall 1-PDU-01 | 7 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 8 | 0 |  |  | 4.89 |  |  | 4.6096
6-DaHall 1-PDU-01 | 9 |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 10 |  | 0 |  |  | 9.21 |  |  | 7.6267
6-DaHall 1-PDU-01 | 11 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 12 |  |  | 0 |  |  | 8.41 |  |  | 7.1786
6-DaHall 1-PDU-01 | 13 | 0 |  |  | 2.06 |  |  | 1.8272
6-DaHall 1-PDU-01 | 14 | 2.28 |  |  | 7.06 |  |  | 4.742
6-DaHall 1-PDU-01 | 15 |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 16 |  | 2.19 |  |  | 5.17 |  |  | 4.3582
6-DaHall 1-PDU-01 | 17 |  |  | 0 |  |  | 2.05 |  |  | 1.7175
6-DaHall 1-PDU-01 | 18 |  |  | 0 |  |  | 0.69 |  |  | 0.65398
6-DaHall 1-PDU-01 | 19 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 20 | 0 |  |  | 0.34 |  |  | 0.2262
6-DaHall 1-PDU-01 | 21 |  | 0 |  |  | 0.99 |  |  | 0.77522
6-DaHall 1-PDU-01 | 22 |  | 0 |  |  | 5.78 |  |  | 4.1864
6-DaHall 1-PDU-01 | 23 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 24 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 25 | 0 |  |  | 2.06 |  |  | 1.8536
6-DaHall 1-PDU-01 | 26 | 0 |  |  | 2 |  |  | 1.8658
6-DaHall 1-PDU-01 | 27 |  | 2.28 |  |  | 5.28 |  |  | 2.4816
6-DaHall 1-PDU-01 | 28 |  | 0 |  |  | 3.08 |  |  | 2.8519
6-DaHall 1-PDU-01 | 29 |  |  | 0 |  |  | 4.91 |  |  | 4.5167
6-DaHall 1-PDU-01 | 30 |  |  | 0 |  |  | 9.12 |  |  | 7.4721
6-DaHall 1-PDU-01 | 31 | 1.26 |  |  | 8.36 |  |  | 3.0449
6-DaHall 1-PDU-01 | 32 | 0 |  |  | 7.02 |  |  | 5.0895
6-DaHall 1-PDU-01 | 33 |  | 1.53 |  |  | 5.14 |  |  | 2.3846
6-DaHall 1-PDU-01 | 34 |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 35 |  |  | 0 |  |  | 0.69 |  |  | 0.66837
6-DaHall 1-PDU-01 | 36 |  |  | 0 |  |  | 1.11 |  |  | 1.0053
6-DaHall 1-PDU-01 | 37 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 38 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 39 |  | 0 |  |  | 0.35 |  |  | 0.23171
6-DaHall 1-PDU-01 | 40 |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 41 |  |  | 0 |  |  | 0.99 |  |  | 0.79308
6-DaHall 1-PDU-01 | 42 |  |  | 0 |  |  | 4.48 |  |  | 3.7994
6-DaHall 1-PDU-01 | 43 | 1.02 |  |  | 5.6 |  |  | 3.2719
6-DaHall 1-PDU-01 | 44 | 0 |  |  | 0
6-DaHall 1-PDU-01 | 45 |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 46 |  | 0.55 |  |  | 4.38 |  |  | 1.1849
6-DaHall 1-PDU-01 | 47 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-01 | 48 |  |  | 0 |  |  | 0.57 |  |  | 0.53761
6-DaHall 1-PDU-01 | 49 | 0 |  |  | 9.67 |  |  | 7.7034
6-DaHall 1-PDU-01 | 50 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 1 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 2 | 0 |  |  | 1.5 |  |  | 1.4397
6-DaHall 1-PDU-02 | 3 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 4 |  | 0 |  |  | 7.46 |  |  | 2.2968
6-DaHall 1-PDU-02 | 5 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 6 |  |  | 0 |  |  | 5.44 |  |  | 5.0405
6-DaHall 1-PDU-02 | 7 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 8 | 0 |  |  | 3.32 |  |  | 3.1141
6-DaHall 1-PDU-02 | 9 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 10 |  | 0 |  |  | 8.78 |  |  | 7.3766
6-DaHall 1-PDU-02 | 11 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 12 |  |  | 0 |  |  | 10.66 |  |  | 9.177
6-DaHall 1-PDU-02 | 13 | 0 |  |  | 2.41 |  |  | 2.1147
6-DaHall 1-PDU-02 | 14 | 1.36 |  |  | 8.72 |  |  | 5.9326
6-DaHall 1-PDU-02 | 15 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 16 |  | 2.04 |  |  | 5.16 |  |  | 4.3999
6-DaHall 1-PDU-02 | 17 |  |  | 0 |  |  | 2.22 |  |  | 1.8442
6-DaHall 1-PDU-02 | 18 |  |  | 0 |  |  | 0.64 |  |  | 0.60148
6-DaHall 1-PDU-02 | 19 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 20 | 0 |  |  | 0.3 |  |  | 0.20942
6-DaHall 1-PDU-02 | 21 |  | 0 |  |  | 0.79 |  |  | 0.59536
6-DaHall 1-PDU-02 | 22 |  | 0 |  |  | 4.53 |  |  | 3.4016
6-DaHall 1-PDU-02 | 23 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 24 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 25 | 0 |  |  | 2.39 |  |  | 2.1427
6-DaHall 1-PDU-02 | 26 | 0 |  |  | 1.5 |  |  | 1.4034
6-DaHall 1-PDU-02 | 27 |  | 1.36 |  |  | 4.46 |  |  | 1.4932
6-DaHall 1-PDU-02 | 28 |  | 0 |  |  | 5.46 |  |  | 4.9425
6-DaHall 1-PDU-02 | 29 |  |  | 0 |  |  | 3.32 |  |  | 3.0425
6-DaHall 1-PDU-02 | 30 |  |  | 0 |  |  | 9.38 |  |  | 7.8247
6-DaHall 1-PDU-02 | 31 | 1.29 |  |  | 10.37 |  |  | 3.3323
6-DaHall 1-PDU-02 | 32 | 0 |  |  | 8.96 |  |  | 6.6958
6-DaHall 1-PDU-02 | 33 |  | 1.67 |  |  | 5.08 |  |  | 2.5159
6-DaHall 1-PDU-02 | 34 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 35 |  |  | 0 |  |  | 0.64 |  |  | 0.62026
6-DaHall 1-PDU-02 | 36 |  |  | 0 |  |  | 2.4 |  |  | 1.556
6-DaHall 1-PDU-02 | 37 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 38 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 39 |  | 0 |  |  | 0.33 |  |  | 0.21443
6-DaHall 1-PDU-02 | 40 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 41 |  |  | 0 |  |  | 1.62 |  |  | 0.61769
6-DaHall 1-PDU-02 | 42 |  |  | 0 |  |  | 4.58 |  |  | 3.956
6-DaHall 1-PDU-02 | 43 | 1.41 |  |  | 5.99 |  |  | 3.5921
6-DaHall 1-PDU-02 | 44 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 45 |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 46 |  | 0 |  |  | 4.5 |  |  | 3.8235
6-DaHall 1-PDU-02 | 47 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 48 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-02 | 49 | 0 |  |  | 0
6-DaHall 1-PDU-02 | 50 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 1 | 2.61 |  |  | 6.75 |  |  | 4.5856
6-DaHall 1-PDU-03 | 2 | 0 |  |  | 6.15 |  |  | 4.154
6-DaHall 1-PDU-03 | 3 |  | 0.8 |  |  | 6.17 |  |  | 3.382
6-DaHall 1-PDU-03 | 4 |  | 0 |  |  | 4.1 |  |  | 3.532
6-DaHall 1-PDU-03 | 5 |  |  | 0.79 |  |  | 5.77 |  |  | 1.208
6-DaHall 1-PDU-03 | 6 |  |  | 0 |  |  | 3.52 |  |  | 2.6374
6-DaHall 1-PDU-03 | 7 | 3.6 |  |  | 6.77 |  |  | 4.0385
6-DaHall 1-PDU-03 | 8 | 0 |  |  | 4.27 |  |  | 3.8164
6-DaHall 1-PDU-03 | 9 |  | 2.03 |  |  | 5.87 |  |  | 3.4999
6-DaHall 1-PDU-03 | 10 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 11 |  |  | 0 |  |  | 4.91 |  |  | 2.8968
6-DaHall 1-PDU-03 | 12 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 13 | 0 |  |  | 8.12 |  |  | 5.0606
6-DaHall 1-PDU-03 | 14 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 15 |  | 0 |  |  | 4.25 |  |  | 3.9056
6-DaHall 1-PDU-03 | 16 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 17 |  |  | 0 |  |  | 2.14 |  |  | 1.9962
6-DaHall 1-PDU-03 | 18 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 19 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 20 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 21 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 22 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 23 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 24 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 25 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 26 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 27 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 28 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 29 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 30 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 31 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 32 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 33 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 34 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 35 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 36 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 37 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 38 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 39 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 40 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 41 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 42 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 43 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 44 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 45 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 46 |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 47 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 48 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-03 | 49 | 0 |  |  | 0
6-DaHall 1-PDU-03 | 50 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 1 | 2.2 |  |  | 5.46 |  |  | 3.411
6-DaHall 1-PDU-04 | 2 | 0 |  |  | 6.69 |  |  | 4.5517
6-DaHall 1-PDU-04 | 3 |  | 0.85 |  |  | 6.39 |  |  | 3.6815
6-DaHall 1-PDU-04 | 4 |  | 0 |  |  | 4.28 |  |  | 3.7073
6-DaHall 1-PDU-04 | 5 |  |  | 0.83 |  |  | 6.22 |  |  | 1.3535
6-DaHall 1-PDU-04 | 6 |  |  | 0 |  |  | 5.68 |  |  | 4.3305
6-DaHall 1-PDU-04 | 7 | 1.74 |  |  | 4.48 |  |  | 3.7081
6-DaHall 1-PDU-04 | 8 | 0 |  |  | 3.98 |  |  | 3.5495
6-DaHall 1-PDU-04 | 9 |  | 1.81 |  |  | 6.19 |  |  | 3.7827
6-DaHall 1-PDU-04 | 10 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 11 |  |  | 0 |  |  | 6.43 |  |  | 4.349
6-DaHall 1-PDU-04 | 12 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 13 | 0 |  |  | 5.76 |  |  | 2.7069
6-DaHall 1-PDU-04 | 14 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 15 |  | 0 |  |  | 4.01 |  |  | 3.6241
6-DaHall 1-PDU-04 | 16 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 17 |  |  | 0 |  |  | 1.94 |  |  | 1.794
6-DaHall 1-PDU-04 | 18 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 19 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 20 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 21 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 22 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 23 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 24 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 25 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 26 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 27 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 28 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 29 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 30 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 31 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 32 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 33 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 34 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 35 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 36 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 37 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 38 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 39 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 40 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 41 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 42 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 43 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 44 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 45 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 46 |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 47 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 48 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-04 | 49 | 0 |  |  | 0
6-DaHall 1-PDU-04 | 50 | 0 |  |  | 0
6-DaHall 1-PDU-05 | 1 |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 2 |  | 0 |  |  | 13 |  |  | 11.2383
6-DaHall 1-PDU-05 | 3 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 4 |  |  | 0 |  |  | 5.74 |  |  | 5.0572
6-DaHall 1-PDU-05 | 5 | 0 |  |  | 0
6-DaHall 1-PDU-05 | 6 | 0.7 |  |  | 1.76 |  |  | 0.90135
6-DaHall 1-PDU-05 | 7 |  | 0 |  |  | 2.15 |  |  | 1.9103
6-DaHall 1-PDU-05 | 8 |  | 2.38 |  |  | 3.94 |  |  | 2.8769
6-DaHall 1-PDU-05 | 9 |  |  | 0 |  |  | 1.04 |  |  | 0.89207
6-DaHall 1-PDU-05 | 10 |  |  | 0 |  |  | 0.86 |  |  | 0.81076
6-DaHall 1-PDU-05 | 11 | 0 |  |  | 1.78 |  |  | 1.679
6-DaHall 1-PDU-05 | 12 | 0 |  |  | 1.5 |  |  | 1.3706
6-DaHall 1-PDU-05 | 13 |  | 2 |  |  | 7.43 |  |  | 2.1577
6-DaHall 1-PDU-05 | 14 |  | 3.2 |  |  | 5.6 |  |  | 4.6426
6-DaHall 1-PDU-05 | 15 |  |  | 2.5 |  |  | 3.95 |  |  | 3.4769
6-DaHall 1-PDU-05 | 16 |  |  | 1.53 |  |  | 3.82 |  |  | 3.0141
6-DaHall 1-PDU-05 | 17 | 0.86 |  |  | 1.13 |  |  | 0.98465
6-DaHall 1-PDU-05 | 18 | 0 |  |  | 0.68 |  |  | 0.64266
6-DaHall 1-PDU-05 | 19 |  | 0 |  |  | 8.47 |  |  | 6.0168
6-DaHall 1-PDU-05 | 20 |  | 0 |  |  | 2.21 |  |  | 1.9902
6-DaHall 1-PDU-05 | 21 |  |  | 0 |  |  | 2.08 |  |  | 1.7327
6-DaHall 1-PDU-05 | 22 |  |  | 0 |  |  | 6.08 |  |  | 5.4581
6-DaHall 1-PDU-05 | 23 | 0 |  |  | 5.29 |  |  | 4.6003
6-DaHall 1-PDU-05 | 24 | 0 |  |  | 7.33 |  |  | 3.9811
6-DaHall 1-PDU-05 | 25 |  | 0 |  |  | 9.25 |  |  | 4.0564
6-DaHall 1-PDU-05 | 26 |  | 0 |  |  | 4.97 |  |  | 4.0684
6-DaHall 1-PDU-05 | 27 |  |  | 0.25 |  |  | 6.68 |  |  | 3.8298
6-DaHall 1-PDU-05 | 28 |  |  | 0 |  |  | 13.31 |  |  | 11.2911
6-DaHall 1-PDU-05 | 29 | 0 |  |  | 5.59 |  |  | 3.0856
6-DaHall 1-PDU-05 | 30 | 0 |  |  | 0.72 |  |  | 0.67087
6-DaHall 1-PDU-05 | 31 |  | 1.52 |  |  | 3.68 |  |  | 1.7472
6-DaHall 1-PDU-05 | 32 |  | 0 |  |  | 0.86 |  |  | 0.80332
6-DaHall 1-PDU-05 | 33 |  |  | 1.11 |  |  | 1.49 |  |  | 1.1758
6-DaHall 1-PDU-05 | 34 |  |  | 0 |  |  | 5.38 |  |  | 4.6033
6-DaHall 1-PDU-05 | 35 | 0.67 |  |  | 3.72 |  |  | 1.2189
6-DaHall 1-PDU-05 | 36 | 0 |  |  | 0
6-DaHall 1-PDU-05 | 37 |  | 0 |  |  | 7.58 |  |  | 2.8963
6-DaHall 1-PDU-05 | 38 |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 39 |  |  | 0 |  |  | 2.27 |  |  | 2.0485
6-DaHall 1-PDU-05 | 40 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 41 | 0 |  |  | 2.17 |  |  | 1.6434
6-DaHall 1-PDU-05 | 42 | 0 |  |  | 0
6-DaHall 1-PDU-05 | 43 |  | 0 |  |  | 6.41 |  |  | 5.6121
6-DaHall 1-PDU-05 | 44 |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 45 |  |  | 0 |  |  | 5.46 |  |  | 4.8328
6-DaHall 1-PDU-05 | 46 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 47 | 0 |  |  | 5.85 |  |  | 4.0582
6-DaHall 1-PDU-05 | 48 | 0 |  |  | 0
6-DaHall 1-PDU-05 | 49 |  | 0 |  |  | 9.31 |  |  | 8.0073
6-DaHall 1-PDU-05 | 50 |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 51 |  |  | 0 |  |  | 5 |  |  | 3.9897
6-DaHall 1-PDU-05 | 52 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-05 | 53 | 0 |  |  | 7.24 |  |  | 5.3934
6-DaHall 1-PDU-05 | 54 | 4.15 |  |  | 4.51 |  |  | 4.2204
6-DaHall 1-PDU-06 | 1 |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 2 |  | 0 |  |  | 11.95 |  |  | 10.1692
6-DaHall 1-PDU-06 | 3 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 4 |  |  | 0 |  |  | 4.53 |  |  | 3.9771
6-DaHall 1-PDU-06 | 5 | 0 |  |  | 0
6-DaHall 1-PDU-06 | 6 | 0.68 |  |  | 1.91 |  |  | 0.91604
6-DaHall 1-PDU-06 | 7 |  | 0 |  |  | 3.66 |  |  | 3.3356
6-DaHall 1-PDU-06 | 8 |  | 3.09 |  |  | 4.5 |  |  | 3.3545
6-DaHall 1-PDU-06 | 9 |  |  | 0 |  |  | 1.02 |  |  | 0.85562
6-DaHall 1-PDU-06 | 10 |  |  | 0 |  |  | 0.55 |  |  | 0.52556
6-DaHall 1-PDU-06 | 11 | 0 |  |  | 2.01 |  |  | 1.844
6-DaHall 1-PDU-06 | 12 | 0 |  |  | 0
6-DaHall 1-PDU-06 | 13 |  | 1.96 |  |  | 6.67 |  |  | 3.2965
6-DaHall 1-PDU-06 | 14 |  | 1.33 |  |  | 4.28 |  |  | 2.8993
6-DaHall 1-PDU-06 | 15 |  |  | 0.66 |  |  | 3.49 |  |  | 2.8372
6-DaHall 1-PDU-06 | 16 |  |  | 0.38 |  |  | 4.77 |  |  | 3.516
6-DaHall 1-PDU-06 | 17 | 0.82 |  |  | 1.19 |  |  | 0.96036
6-DaHall 1-PDU-06 | 18 | 0 |  |  | 0.39 |  |  | 0.36842
6-DaHall 1-PDU-06 | 19 |  | 0 |  |  | 8.69 |  |  | 6.2576
6-DaHall 1-PDU-06 | 20 |  | 0 |  |  | 1.93 |  |  | 1.8103
6-DaHall 1-PDU-06 | 21 |  |  | 0 |  |  | 0.45 |  |  | 0.35861
6-DaHall 1-PDU-06 | 22 |  |  | 0 |  |  | 5.29 |  |  | 4.6349
6-DaHall 1-PDU-06 | 23 | 0 |  |  | 5.39 |  |  | 4.6799
6-DaHall 1-PDU-06 | 24 | 0 |  |  | 5.46 |  |  | 3.6619
6-DaHall 1-PDU-06 | 25 |  | 0.39 |  |  | 6.73 |  |  | 2.3916
6-DaHall 1-PDU-06 | 26 |  | 0 |  |  | 6.29 |  |  | 4.6273
6-DaHall 1-PDU-06 | 27 |  |  | 0.23 |  |  | 5.13 |  |  | 1.7876
6-DaHall 1-PDU-06 | 28 |  |  | 0 |  |  | 12.07 |  |  | 10.2002
6-DaHall 1-PDU-06 | 29 | 0 |  |  | 4.54 |  |  | 1.9383
6-DaHall 1-PDU-06 | 30 | 0 |  |  | 0.72 |  |  | 0.65334
6-DaHall 1-PDU-06 | 31 |  | 0.38 |  |  | 4.47 |  |  | 0.94217
6-DaHall 1-PDU-06 | 32 |  | 0 |  |  | 0.55 |  |  | 0.51022
6-DaHall 1-PDU-06 | 33 |  |  | 0 |  |  | 1.19 |  |  | 1.1485
6-DaHall 1-PDU-06 | 34 |  |  | 0 |  |  | 3.45 |  |  | 3.0602
6-DaHall 1-PDU-06 | 35 | 0.39 |  |  | 4.7 |  |  | 1.0842
6-DaHall 1-PDU-06 | 36 | 0 |  |  | 0
6-DaHall 1-PDU-06 | 37 |  | 0 |  |  | 7.8 |  |  | 2.7648
6-DaHall 1-PDU-06 | 38 |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 39 |  |  | 0 |  |  | 1.93 |  |  | 1.8605
6-DaHall 1-PDU-06 | 40 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 41 | 0 |  |  | 1.07 |  |  | 0.52803
6-DaHall 1-PDU-06 | 42 | 0 |  |  | 0
6-DaHall 1-PDU-06 | 43 |  | 0 |  |  | 5.67 |  |  | 4.77
6-DaHall 1-PDU-06 | 44 |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 45 |  |  | 0 |  |  | 5.53 |  |  | 4.9243
6-DaHall 1-PDU-06 | 46 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 47 | 0 |  |  | 5.44 |  |  | 3.7379
6-DaHall 1-PDU-06 | 48 | 0 |  |  | 0
6-DaHall 1-PDU-06 | 49 |  | 0 |  |  | 1.49 |  |  | 1.3018
6-DaHall 1-PDU-06 | 50 |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 51 |  |  | 0 |  |  | 5.77 |  |  | 4.5523
6-DaHall 1-PDU-06 | 52 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-06 | 53 | 0 |  |  | 1 |  |  | 0.57475
6-DaHall 1-PDU-06 | 54 | 2.31 |  |  | 2.9 |  |  | 2.4267
6-DaHall 1-PDU-07 | 1 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 2 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 3 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 4 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 5 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 6 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 7 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 8 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 9 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 10 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 11 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 12 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 13 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 14 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 15 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 16 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 17 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 18 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 19 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 20 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 21 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 22 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 23 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 24 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 25 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 26 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 27 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 28 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 29 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 30 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 31 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 32 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 33 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 34 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 35 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 36 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 37 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 38 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 39 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 40 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 41 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 42 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 43 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 44 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 45 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 46 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 47 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 48 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 49 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 50 |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 51 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 52 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-07 | 53 | 0 |  |  | 0
6-DaHall 1-PDU-07 | 54 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 1 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 2 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 3 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 4 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 5 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 6 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 7 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 8 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 9 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 10 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 11 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 12 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 13 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 14 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 15 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 16 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 17 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 18 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 19 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 20 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 21 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 22 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 23 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 24 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 25 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 26 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 27 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 28 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 29 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 30 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 31 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 32 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 33 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 34 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 35 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 36 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 37 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 38 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 39 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 40 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 41 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 42 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 43 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 44 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 45 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 46 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 47 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 48 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 49 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 50 |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 51 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 52 |  |  | 0 |  |  | 0
6-DaHall 1-PDU-08 | 53 | 0 |  |  | 0
6-DaHall 1-PDU-08 | 54 | 0 |  |  | 0

## 5층_부하량
장비명 | 분기번호 | MIN |  |  | MAX |  |  | AVG
|  | R | S | T | R | S | T | R | S | T
5-DaHall 1-CEP-05 | 1 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-CEP-05 | 2 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-CEP-05 | 3 | 0 | 0 | 0 | 21.31 | 21.47 | 20.96 | 0.078948 | 0.079611 | 0.078611
5-DaHall 1-CEP-05 | 4 | 0 | 0 | 0 | 23.99 | 23.98 | 23.54 | 18.1523 | 18.2569 | 17.9319
5-DaHall 1-CEP-05 | 5 | 0 | 0 | 0 | 22.58 | 22.85 | 22.19 | 0.14982 | 0.15172 | 0.14853
5-DaHall 1-CEP-05 | 6 | 0 | 0 | 0 | 25.26 | 24.86 | 25.16 | 19.7905 | 19.3812 | 19.7072
5-DaHall 1-CEP-05 | 7 | 0 | 0 | 0 | 24.42 | 24.4 | 24.07 | 14.9237 | 14.9132 | 14.6659
5-DaHall 1-CEP-05 | 8 | 0 | 0 | 0 | 24.3 | 24.7 | 24.07 | 11.6908 | 11.7958 | 11.6839
5-DaHall 1-CEP-05 | 9 | 0 | 0 | 0 | 20.68 | 21 | 20.43 | 0.12239 | 0.12429 | 0.12132
5-DaHall 1-CEP-05 | 10 | 0 | 0 | 0 | 20.46 | 20.84 | 20.36 | 0.13355 | 0.13661 | 0.13361
5-DaHall 1-CEP-05 | 11 | 0 | 0 | 0 | 22.85 | 23.52 | 22.77 | 16.2531 | 16.3563 | 16.1459
5-DaHall 1-CEP-05 | 12 | 0 | 0 | 0 | 24.59 | 23.85 | 24.56 | 16.8723 | 16.5479 | 16.899
5-DaHall 1-CEP-05 | 13 | 0 |  |  | 72.62 |  |  | 24.7097
5-DaHall 1-CEP-05 | 14 | 0 |  |  | 0
5-DaHall 1-CEP-05 | 15 |  | 0 |  |  | 0
5-DaHall 1-CEP-05 | 16 |  | 0 |  |  | 14.37 |  |  | 12.8713
5-DaHall 1-CEP-05 | 17 |  |  | 0 |  |  | 13.92 |  |  | 12.3129
5-DaHall 1-CEP-05 | 18 |  |  | 5.82 |  |  | 17.77 |  |  | 9.8507
5-DaHall 1-CEP-06 | 1 | 0.24 | 0 | 0.23 | 20.19 | 19.6 | 19.23 | 0.24228 | 0.057747 | 0.24644
5-DaHall 1-CEP-06 | 2 | 0.24 | 0 | 0.23 | 20.8 | 20.48 | 20.24 | 0.24257 | 0.060039 | 0.24744
5-DaHall 1-CEP-06 | 3 | 0.24 | 0 | 0.22 | 20.05 | 19.64 | 19.62 | 0.2434 | 0.063805 | 0.23459
5-DaHall 1-CEP-06 | 4 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-01 | 1 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-01 | 2 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 3 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 4 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 5 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 6 |  | 9.29 |  |  | 15.96 |  |  | 13.8976
5-DaHall 1-PDU-01 | 7 |  |  | 8.18 |  |  | 12.94 |  |  | 11.3149
5-DaHall 1-PDU-01 | 8 | 9.79 |  |  | 15.76 |  |  | 13.7686
5-DaHall 1-PDU-01 | 9 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 10 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 11 | 1.03 |  |  | 1.06 |  |  | 1.0405
5-DaHall 1-PDU-01 | 12 |  | 1.39 |  |  | 1.55 |  |  | 1.4766
5-DaHall 1-PDU-01 | 13 |  |  | 1.48 |  |  | 1.61 |  |  | 1.5398
5-DaHall 1-PDU-01 | 14 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 15 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 16 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 17 | 8.84 |  |  | 12.07 |  |  | 11.0998
5-DaHall 1-PDU-01 | 18 |  | 6.91 |  |  | 11.03 |  |  | 9.9455
5-DaHall 1-PDU-01 | 19 |  |  | 7.84 |  |  | 13.11 |  |  | 11.6982
5-DaHall 1-PDU-01 | 20 | 5.99 |  |  | 10.53 |  |  | 9.5055
5-DaHall 1-PDU-01 | 21 |  | 8.6 |  |  | 13.42 |  |  | 11.8317
5-DaHall 1-PDU-01 | 22 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 23 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 24 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 25 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 26 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 55 | 0 | 0.58 | 0.73 | 0 | 0.6 | 0.76 |  | 0.58996 | 0.74371
5-DaHall 1-PDU-01 | 56 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 57 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 58 |  |  | 1.52 |  |  | 1.55 |  |  | 1.5294
5-DaHall 1-PDU-01 | 59 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 60 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 61 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 62 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 63 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 64 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 65 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 66 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 67 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 68 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 69 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 70 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 71 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 72 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 73 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 74 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 75 |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 76 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-01 | 77 | 0 |  |  | 0
5-DaHall 1-PDU-01 | 78 |  | 0.35 |  |  | 0.7 |  |  | 0.61537
5-DaHall 1-PDU-01 | 79 |  |  | 1.72 |  |  | 1.76 |  |  | 1.7392
5-DaHall 1-PDU-01 | 80 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 1 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-02 | 2 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 3 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 4 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 5 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 6 |  | 7.69 |  |  | 13.34 |  |  | 11.6589
5-DaHall 1-PDU-02 | 7 |  |  | 9.17 |  |  | 14.84 |  |  | 12.8737
5-DaHall 1-PDU-02 | 8 | 8.23 |  |  | 13.06 |  |  | 11.4483
5-DaHall 1-PDU-02 | 9 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 10 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 11 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 12 |  | 1.53 |  |  | 1.69 |  |  | 1.6313
5-DaHall 1-PDU-02 | 13 |  |  | 1.26 |  |  | 1.34 |  |  | 1.3209
5-DaHall 1-PDU-02 | 14 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 15 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 16 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 17 | 9.82 |  |  | 13.04 |  |  | 11.4642
5-DaHall 1-PDU-02 | 18 |  | 8.12 |  |  | 12.93 |  |  | 11.5709
5-DaHall 1-PDU-02 | 19 |  |  | 6.21 |  |  | 10.87 |  |  | 9.7301
5-DaHall 1-PDU-02 | 20 | 6.9 |  |  | 12.53 |  |  | 11.348
5-DaHall 1-PDU-02 | 21 |  | 7.23 |  |  | 10.71 |  |  | 9.5155
5-DaHall 1-PDU-02 | 22 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 23 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 24 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 25 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 26 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 55 | 0 | 0.66 | 0.73 | 0 | 0.67 | 0.75 |  | 0.66516 | 0.74062
5-DaHall 1-PDU-02 | 56 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 57 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 58 |  |  | 1.24 |  |  | 1.26 |  |  | 1.252
5-DaHall 1-PDU-02 | 59 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 60 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 61 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 62 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 63 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 64 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 65 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 66 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 67 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 68 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 69 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 70 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 71 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 72 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 73 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 74 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 75 |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 76 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-02 | 77 | 0 |  |  | 0
5-DaHall 1-PDU-02 | 78 |  | 0.38 |  |  | 0.99 |  |  | 0.65748
5-DaHall 1-PDU-02 | 79 |  |  | 1.09 |  |  | 1.13 |  |  | 1.1049
5-DaHall 1-PDU-02 | 80 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 1 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-03 | 2 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 3 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 4 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 5 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 6 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 7 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 8 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 9 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 10 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 11 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 12 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 13 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 14 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 15 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 16 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 17 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 18 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 19 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 20 | 2.59 |  |  | 4.41 |  |  | 3.3377
5-DaHall 1-PDU-03 | 21 |  | 0 |  |  | 2.45 |  |  | 1.3727
5-DaHall 1-PDU-03 | 22 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 23 | 2.17 |  |  | 3.38 |  |  | 2.4187
5-DaHall 1-PDU-03 | 24 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 25 |  |  | 3.58 |  |  | 4.46 |  |  | 4.0462
5-DaHall 1-PDU-03 | 26 | 5.58 |  |  | 6.09 |  |  | 5.699
5-DaHall 1-PDU-03 | 55 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-03 | 56 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 57 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 58 |  |  | 0.53 |  |  | 0.73 |  |  | 0.56815
5-DaHall 1-PDU-03 | 59 | 1.26 |  |  | 1.78 |  |  | 1.4133
5-DaHall 1-PDU-03 | 60 |  | 2.04 |  |  | 4.61 |  |  | 3.5687
5-DaHall 1-PDU-03 | 61 |  |  | 1.74 |  |  | 2.06 |  |  | 1.7762
5-DaHall 1-PDU-03 | 62 | 0.34 |  |  | 2.6 |  |  | 0.35629
5-DaHall 1-PDU-03 | 63 |  | 3.69 |  |  | 4.46 |  |  | 3.8993
5-DaHall 1-PDU-03 | 64 |  |  | 0.84 |  |  | 5.69 |  |  | 4.6474
5-DaHall 1-PDU-03 | 65 | 2.24 |  |  | 2.96 |  |  | 2.8041
5-DaHall 1-PDU-03 | 66 |  | 2.81 |  |  | 4.3 |  |  | 3.3989
5-DaHall 1-PDU-03 | 67 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 68 | 0 |  |  | 0
5-DaHall 1-PDU-03 | 69 |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 70 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-03 | 71 | 2.41 |  |  | 2.55 |  |  | 2.4898
5-DaHall 1-PDU-03 | 72 |  | 2.14 |  |  | 2.41 |  |  | 2.1696
5-DaHall 1-PDU-03 | 73 |  |  | 2.16 |  |  | 2.2 |  |  | 2.17
5-DaHall 1-PDU-03 | 74 | 2.31 |  |  | 2.55 |  |  | 2.435
5-DaHall 1-PDU-03 | 75 |  | 1.35 |  |  | 1.39 |  |  | 1.3683
5-DaHall 1-PDU-03 | 76 |  |  | 1.77 |  |  | 1.87 |  |  | 1.7892
5-DaHall 1-PDU-03 | 77 | 2.85 |  |  | 3.37 |  |  | 2.9436
5-DaHall 1-PDU-03 | 78 |  | 2.83 |  |  | 3.15 |  |  | 2.912
5-DaHall 1-PDU-03 | 79 |  |  | 3.42 |  |  | 4.07 |  |  | 3.7191
5-DaHall 1-PDU-03 | 80 | 3.81 |  |  | 4.62 |  |  | 4.1031
5-DaHall 1-PDU-04 | 1 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-04 | 2 | 0 |  |  | 0
5-DaHall 1-PDU-04 | 3 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 4 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 5 | 0 |  |  | 0
5-DaHall 1-PDU-04 | 6 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 7 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 8 | 0 |  |  | 0
5-DaHall 1-PDU-04 | 9 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 10 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 11 | 0 |  |  | 0
5-DaHall 1-PDU-04 | 12 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 13 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 14 | 0 |  |  | 0
5-DaHall 1-PDU-04 | 15 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 16 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 17 | 0 |  |  | 0
5-DaHall 1-PDU-04 | 18 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 19 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 20 | 3.22 |  |  | 5.04 |  |  | 3.86
5-DaHall 1-PDU-04 | 21 |  | 0 |  |  | 2.14 |  |  | 0.91329
5-DaHall 1-PDU-04 | 22 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 23 | 2.22 |  |  | 3.41 |  |  | 2.494
5-DaHall 1-PDU-04 | 24 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 25 |  |  | 3.94 |  |  | 4.78 |  |  | 4.3953
5-DaHall 1-PDU-04 | 26 | 5.3 |  |  | 5.86 |  |  | 5.4287
5-DaHall 1-PDU-04 | 55 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-04 | 56 | 0 |  |  | 0
5-DaHall 1-PDU-04 | 57 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 58 |  |  | 0.53 |  |  | 0.73 |  |  | 0.56831
5-DaHall 1-PDU-04 | 59 | 1.57 |  |  | 2.08 |  |  | 1.7195
5-DaHall 1-PDU-04 | 60 |  | 1.98 |  |  | 4.46 |  |  | 3.5462
5-DaHall 1-PDU-04 | 61 |  |  | 1.78 |  |  | 2.09 |  |  | 1.8162
5-DaHall 1-PDU-04 | 62 | 0.4 |  |  | 3.34 |  |  | 0.64036
5-DaHall 1-PDU-04 | 63 |  | 3.72 |  |  | 4.4 |  |  | 3.8896
5-DaHall 1-PDU-04 | 64 |  |  | 0.85 |  |  | 5.5 |  |  | 4.4966
5-DaHall 1-PDU-04 | 65 | 1.36 |  |  | 1.9 |  |  | 1.8441
5-DaHall 1-PDU-04 | 66 |  | 4.42 |  |  | 5.47 |  |  | 4.7166
5-DaHall 1-PDU-04 | 67 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 68 | 0 |  |  | 0
5-DaHall 1-PDU-04 | 69 |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 70 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-04 | 71 | 0.26 |  |  | 0.73 |  |  | 0.27074
5-DaHall 1-PDU-04 | 72 |  | 0.28 |  |  | 0.29 |  |  | 0.28991
5-DaHall 1-PDU-04 | 73 |  |  | 2.27 |  |  | 2.32 |  |  | 2.2939
5-DaHall 1-PDU-04 | 74 | 2.47 |  |  | 2.73 |  |  | 2.5978
5-DaHall 1-PDU-04 | 75 |  | 1.44 |  |  | 1.48 |  |  | 1.4562
5-DaHall 1-PDU-04 | 76 |  |  | 1.57 |  |  | 1.62 |  |  | 1.5857
5-DaHall 1-PDU-04 | 77 | 2.26 |  |  | 2.59 |  |  | 2.3215
5-DaHall 1-PDU-04 | 78 |  | 2.29 |  |  | 2.53 |  |  | 2.3525
5-DaHall 1-PDU-04 | 79 |  |  | 2.93 |  |  | 3.54 |  |  | 3.1823
5-DaHall 1-PDU-04 | 80 | 3.63 |  |  | 4.43 |  |  | 3.9494
5-DaHall 1-PDU-05 | 1 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 2 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 3 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 4 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 5 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 6 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 7 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 8 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 9 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 10 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 11 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 12 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 13 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 14 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 15 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 16 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 17 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 18 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 19 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 20 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 21 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 22 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 23 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 24 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 25 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 26 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 27 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 28 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 29 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 30 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 31 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 32 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 33 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 34 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 35 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 36 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 37 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 38 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 39 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 40 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 41 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 42 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 43 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 44 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 45 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 46 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 47 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 48 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 49 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 50 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 51 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 52 | 0 |  |  | 0
5-DaHall 1-PDU-05 | 53 |  | 0 |  |  | 0
5-DaHall 1-PDU-05 | 54 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 1 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 2 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 3 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 4 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 5 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 6 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 7 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 8 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 9 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 10 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 11 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 12 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 13 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 14 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 15 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 16 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 17 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 18 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 19 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 20 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 21 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 22 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 23 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 24 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 25 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 26 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 27 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 28 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 29 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 30 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 31 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 32 |  |  | 0 |  |  | 3.59 |  |  | 0.00082146
5-DaHall 1-PDU-06 | 33 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 34 | 0 |  |  | 3.61 |  |  | 0.00082609
5-DaHall 1-PDU-06 | 35 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 36 |  | 0 |  |  | 3.46 |  |  | 0.00040088
5-DaHall 1-PDU-06 | 37 |  |  | 0 |  |  | 0.22 |  |  | 4.9826e-05
5-DaHall 1-PDU-06 | 38 |  |  | 0 |  |  | 5.37 |  |  | 0.0006221
5-DaHall 1-PDU-06 | 39 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 40 | 0 |  |  | 5.22 |  |  | 0.00060473
5-DaHall 1-PDU-06 | 41 |  | 0 |  |  | 0.21 |  |  | 2.4334e-05
5-DaHall 1-PDU-06 | 42 |  | 0 |  |  | 5.68 |  |  | 0.00065817
5-DaHall 1-PDU-06 | 43 |  |  | 0 |  |  | 0.3 |  |  | 3.4758e-05
5-DaHall 1-PDU-06 | 44 |  |  | 0 |  |  | 7.91 |  |  | 0.00097439
5-DaHall 1-PDU-06 | 45 | 0 |  |  | 0.3 |  |  | 3.4758e-05
5-DaHall 1-PDU-06 | 46 | 0 |  |  | 0.5 |  |  | 0.00011239
5-DaHall 1-PDU-06 | 47 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 48 |  | 0 |  |  | 0.54 |  |  | 0.00012165
5-DaHall 1-PDU-06 | 49 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 50 |  |  | 0 |  |  | 0.84 |  |  | 0.00019233
5-DaHall 1-PDU-06 | 51 | 0 |  |  | 0
5-DaHall 1-PDU-06 | 52 | 0 |  |  | 0.74 |  |  | 8.5737e-05
5-DaHall 1-PDU-06 | 53 |  | 0 |  |  | 0
5-DaHall 1-PDU-06 | 54 |  | 0 |  |  | 0.75 |  |  | 8.6896e-05
5-DaHall 1-PDU-07 | 1 | 7.05 |  |  | 7.93 |  |  | 7.7743
5-DaHall 1-PDU-07 | 2 | 0.99 |  |  | 1.32 |  |  | 1.0427
5-DaHall 1-PDU-07 | 3 |  | 0.4 |  |  | 1.44 |  |  | 1.0896
5-DaHall 1-PDU-07 | 4 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 5 |  |  | 0 |  |  | 0.4 |  |  | 0.39038
5-DaHall 1-PDU-07 | 6 |  |  | 0 |  |  | 0.4 |  |  | 0.3788
5-DaHall 1-PDU-07 | 7 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 8 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 9 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 10 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 11 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 12 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 13 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 14 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 15 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 16 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 17 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 18 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 19 | 0 |  |  | 1.07 |  |  | 0.94028
5-DaHall 1-PDU-07 | 20 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 21 |  | 0 |  |  | 0.44 |  |  | 0.36241
5-DaHall 1-PDU-07 | 22 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 23 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 24 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 25 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 26 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 27 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 28 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 29 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 30 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 31 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 32 | 0 |  |  | 0
5-DaHall 1-PDU-07 | 33 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 34 |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 35 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-07 | 36 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-09 | 1
5-DaHall 1-PDU-09 | 2
5-DaHall 1-PDU-09 | 3
5-DaHall 1-PDU-09 | 4
5-DaHall 1-PDU-09 | 5
5-DaHall 1-PDU-09 | 6
5-DaHall 1-PDU-09 | 7
5-DaHall 1-PDU-09 | 8
5-DaHall 1-PDU-09 | 9
5-DaHall 1-PDU-09 | 10
5-DaHall 1-PDU-09 | 11
5-DaHall 1-PDU-09 | 12
5-DaHall 1-PDU-09 | 13
5-DaHall 1-PDU-09 | 14
5-DaHall 1-PDU-09 | 15
5-DaHall 1-PDU-09 | 16
5-DaHall 1-PDU-09 | 17
5-DaHall 1-PDU-09 | 18
5-DaHall 1-PDU-09 | 19
5-DaHall 1-PDU-09 | 20
5-DaHall 1-PDU-09 | 21
5-DaHall 1-PDU-09 | 22
5-DaHall 1-PDU-09 | 23
5-DaHall 1-PDU-09 | 24
5-DaHall 1-PDU-09 | 25
5-DaHall 1-PDU-09 | 26
5-DaHall 1-PDU-09 | 27
5-DaHall 1-PDU-09 | 28
5-DaHall 1-PDU-09 | 29
5-DaHall 1-PDU-09 | 30
5-DaHall 1-PDU-09 | 31
5-DaHall 1-PDU-09 | 32
5-DaHall 1-PDU-09 | 33
5-DaHall 1-PDU-09 | 34
5-DaHall 1-PDU-09 | 35
5-DaHall 1-PDU-09 | 36
5-DaHall 1-PDU-09 | 37
5-DaHall 1-PDU-09 | 38
5-DaHall 1-PDU-08 | 1 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 2 | 1.16 |  |  | 1.54 |  |  | 1.2448
5-DaHall 1-PDU-08 | 3 |  | 0 |  |  | 1.55 |  |  | 1.3681
5-DaHall 1-PDU-08 | 4 |  | 0 |  |  | 5.49 |  |  | 5.2088
5-DaHall 1-PDU-08 | 5 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 6 |  |  | 0 |  |  | 1.39 |  |  | 1.328
5-DaHall 1-PDU-08 | 7 | 0 |  |  | 5.49 |  |  | 5.2714
5-DaHall 1-PDU-08 | 8 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 9 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 10 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 11 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 12 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 13 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 14 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 15 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 16 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 17 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 18 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 19 | 0 |  |  | 1.25 |  |  | 1.1226
5-DaHall 1-PDU-08 | 20 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 21 |  | 0 |  |  | 1.39 |  |  | 1.3098
5-DaHall 1-PDU-08 | 22 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 23 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 24 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 25 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 26 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 27 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 28 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 29 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 30 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 31 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 32 | 0 |  |  | 0
5-DaHall 1-PDU-08 | 33 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 34 |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 35 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-08 | 36 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-10 | 1
5-DaHall 1-PDU-10 | 2
5-DaHall 1-PDU-10 | 3
5-DaHall 1-PDU-10 | 4
5-DaHall 1-PDU-10 | 5
5-DaHall 1-PDU-10 | 6
5-DaHall 1-PDU-10 | 7
5-DaHall 1-PDU-10 | 8
5-DaHall 1-PDU-10 | 9
5-DaHall 1-PDU-10 | 10
5-DaHall 1-PDU-10 | 11
5-DaHall 1-PDU-10 | 12
5-DaHall 1-PDU-10 | 13
5-DaHall 1-PDU-10 | 14
5-DaHall 1-PDU-10 | 15
5-DaHall 1-PDU-10 | 16
5-DaHall 1-PDU-10 | 17
5-DaHall 1-PDU-10 | 18
5-DaHall 1-PDU-10 | 19
5-DaHall 1-PDU-10 | 20
5-DaHall 1-PDU-10 | 21
5-DaHall 1-PDU-10 | 22
5-DaHall 1-PDU-10 | 23
5-DaHall 1-PDU-10 | 24
5-DaHall 1-PDU-10 | 25
5-DaHall 1-PDU-10 | 26
5-DaHall 1-PDU-10 | 27
5-DaHall 1-PDU-10 | 28
5-DaHall 1-PDU-10 | 29
5-DaHall 1-PDU-10 | 30
5-DaHall 1-PDU-10 | 31
5-DaHall 1-PDU-10 | 32
5-DaHall 1-PDU-10 | 33
5-DaHall 1-PDU-10 | 34
5-DaHall 1-PDU-10 | 35
5-DaHall 1-PDU-10 | 36
5-DaHall 1-PDU-10 | 37
5-DaHall 1-PDU-10 | 38
5-DaHall 1-PDU-11 | 1 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-11 | 2 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-11 | 3 | 0 |  |  | 0
5-DaHall 1-PDU-11 | 4 | 0 |  |  | 0
5-DaHall 1-PDU-11 | 5 |  | 0 |  |  | 5.31 |  |  | 4.9924
5-DaHall 1-PDU-11 | 6 |  | 0 |  |  | 2.01 |  |  | 1.9354
5-DaHall 1-PDU-11 | 7 |  |  | 0 |  |  | 2 |  |  | 1.8655
5-DaHall 1-PDU-11 | 8 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-11 | 9 | 0 |  |  | 5.29 |  |  | 5.0854
5-DaHall 1-PDU-11 | 10 | 0 |  |  | 0
5-DaHall 1-PDU-11 | 11 |  | 0 |  |  | 2.69 |  |  | 2.4235
5-DaHall 1-PDU-11 | 12 |  | 0 |  |  | 5.7 |  |  | 4.7449
5-DaHall 1-PDU-11 | 13 |  |  | 0 |  |  | 1.99 |  |  | 1.8986
5-DaHall 1-PDU-11 | 14 |  |  | 0 |  |  | 2.76 |  |  | 2.4231
5-DaHall 1-PDU-11 | 15 | 0 |  |  | 0
5-DaHall 1-PDU-11 | 16 | 0 |  |  | 0
5-DaHall 1-PDU-11 | 17 |  | 0 |  |  | 0
5-DaHall 1-PDU-11 | 18 |  | 0 |  |  | 3.54 |  |  | 3.0066
5-DaHall 1-PDU-11 | 19 |  |  | 0 |  |  | 2.02 |  |  | 1.9028
5-DaHall 1-PDU-11 | 20 |  |  | 0 |  |  | 3.36 |  |  | 2.9667
5-DaHall 1-PDU-11 | 21 | 0 |  |  | 2.68 |  |  | 2.4821
5-DaHall 1-PDU-11 | 22 | 0 |  |  | 0
5-DaHall 1-PDU-11 | 23 |  | 0 |  |  | 5.71 |  |  | 4.7745
5-DaHall 1-PDU-11 | 24 |  | 0 |  |  | 0
5-DaHall 1-PDU-11 | 25 |  |  | 0 |  |  | 3.61 |  |  | 2.8546
5-DaHall 1-PDU-11 | 26 |  |  | 3.03 |  |  | 5.53 |  |  | 4.9259
5-DaHall 1-PDU-11 | 27 | 0 |  |  | 2.69 |  |  | 2.4187
5-DaHall 1-PDU-11 | 28 | 0 |  |  | 5.62 |  |  | 5.279
5-DaHall 1-PDU-11 | 29 |  | 0 |  |  | 5.55 |  |  | 5.2037
5-DaHall 1-PDU-11 | 30 |  | 0 |  |  | 5.73 |  |  | 5.2394
5-DaHall 1-PDU-11 | 31 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-11 | 32 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 1 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-13 | 2 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-13 | 3 | 3.91 |  |  | 6.43 |  |  | 5.2809
5-DaHall 1-PDU-13 | 4 | 0 |  |  | 0
5-DaHall 1-PDU-13 | 5 |  | 0 |  |  | 3.98 |  |  | 3.8315
5-DaHall 1-PDU-13 | 6 |  | 0 |  |  | 6.32 |  |  | 5.7186
5-DaHall 1-PDU-13 | 7 |  |  | 0 |  |  | 0.73 |  |  | 0.68093
5-DaHall 1-PDU-13 | 8 |  |  | 0 |  |  | 4.67 |  |  | 4.1143
5-DaHall 1-PDU-13 | 9 | 0 |  |  | 0
5-DaHall 1-PDU-13 | 10 | 0 |  |  | 5.99 |  |  | 5.4351
5-DaHall 1-PDU-13 | 11 |  | 0 |  |  | 3.32 |  |  | 3.0406
5-DaHall 1-PDU-13 | 12 |  | 0 |  |  | 10.08 |  |  | 8.8344
5-DaHall 1-PDU-13 | 13 |  |  | 0.7 |  |  | 2.6 |  |  | 1.1149
5-DaHall 1-PDU-13 | 14 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 15 | 0 |  |  | 0
5-DaHall 1-PDU-13 | 16 | 0 |  |  | 3.95 |  |  | 3.7659
5-DaHall 1-PDU-13 | 17 |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 18 |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 19 |  |  | 5.14 |  |  | 6.36 |  |  | 5.5747
5-DaHall 1-PDU-13 | 20 |  |  | 0 |  |  | 4.4 |  |  | 4.044
5-DaHall 1-PDU-13 | 21 | 0 |  |  | 3.33 |  |  | 3.0988
5-DaHall 1-PDU-13 | 22 | 0 |  |  | 0
5-DaHall 1-PDU-13 | 23 |  | 0 |  |  | 10.11 |  |  | 8.95
5-DaHall 1-PDU-13 | 24 |  | 0 |  |  | 3.96 |  |  | 3.7088
5-DaHall 1-PDU-13 | 25 |  |  | 0 |  |  | 2.57 |  |  | 2.4387
5-DaHall 1-PDU-13 | 26 |  |  | 0 |  |  | 2.1 |  |  | 1.8314
5-DaHall 1-PDU-13 | 27 | 0 |  |  | 0
5-DaHall 1-PDU-13 | 28 | 0 |  |  | 0
5-DaHall 1-PDU-13 | 29 |  | 0 |  |  | 2.05 |  |  | 1.8121
5-DaHall 1-PDU-13 | 30 |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 31 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-13 | 32 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-15 | 1 | 5.97 | 1.25 | 7.85 | 6.1 | 1.29 | 8.28 | 6.0279 | 1.253 | 7.9728
5-DaHall 1-PDU-15 | 2 | 0 | 0 | 0 | 3.43 | 2.84 | 6.34 | 3.2897 | 2.7182 | 1.997
5-DaHall 1-PDU-15 | 3 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-15 | 4 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-15 | 5 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-15 | 6 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-15 | 7 | 0.65 |  |  | 3.98 |  |  | 3.1077
5-DaHall 1-PDU-15 | 8 | 0 |  |  | 4.36 |  |  | 4.1937
5-DaHall 1-PDU-15 | 9 |  | 0 |  |  | 1.77 |  |  | 1.7053
5-DaHall 1-PDU-15 | 10 |  | 0 |  |  | 9.05 |  |  | 6.5942
5-DaHall 1-PDU-15 | 11 |  |  | 0 |  |  | 0.22 |  |  | 0.0031944
5-DaHall 1-PDU-15 | 12 |  |  | 2.31 |  |  | 2.37 |  |  | 2.3146
5-DaHall 1-PDU-15 | 13 | 0 |  |  | 0.78 |  |  | 0.65398
5-DaHall 1-PDU-15 | 14 | 0 |  |  | 1.6 |  |  | 1.5309
5-DaHall 1-PDU-15 | 15 |  | 0 |  |  | 0.37 |  |  | 0.34588
5-DaHall 1-PDU-15 | 16 |  | 0 |  |  | 8.38 |  |  | 7.8789
5-DaHall 1-PDU-15 | 17 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-15 | 18 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-15 | 19 | 0 |  |  | 4.37 |  |  | 4.1394
5-DaHall 1-PDU-15 | 20 | 0 |  |  | 7.49 |  |  | 6.6275
5-DaHall 1-PDU-15 | 21 |  | 0 |  |  | 2.34 |  |  | 2.2086
5-DaHall 1-PDU-15 | 22 |  | 0 |  |  | 1.59 |  |  | 1.5008
5-DaHall 1-PDU-15 | 23 |  |  | 0 |  |  | 2.34 |  |  | 2.246
5-DaHall 1-PDU-15 | 24 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-15 | 25 | 0 |  |  | 0
5-DaHall 1-PDU-15 | 26 | 0 |  |  | 0
5-DaHall 1-PDU-15 | 27 |  | 0 |  |  | 0
5-DaHall 1-PDU-15 | 28 |  | 0 |  |  | 0.72 |  |  | 0.69019
5-DaHall 1-PDU-15 | 29 |  |  | 0.36 |  |  | 0.72 |  |  | 0.44294
5-DaHall 1-PDU-15 | 30 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 1 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-12 | 2 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-12 | 3 | 0 |  |  | 0
5-DaHall 1-PDU-12 | 4 | 0 |  |  | 1.92 |  |  | 1.852
5-DaHall 1-PDU-12 | 5 |  | 0 |  |  | 2.98 |  |  | 2.7999
5-DaHall 1-PDU-12 | 6 |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 7 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 8 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 9 | 0 |  |  | 2.96 |  |  | 2.8494
5-DaHall 1-PDU-12 | 10 | 0 |  |  | 3.15 |  |  | 2.824
5-DaHall 1-PDU-12 | 11 |  | 0 |  |  | 5.49 |  |  | 4.4011
5-DaHall 1-PDU-12 | 12 |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 13 |  |  | 0 |  |  | 3.64 |  |  | 3.1179
5-DaHall 1-PDU-12 | 14 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 15 | 0 |  |  | 0
5-DaHall 1-PDU-12 | 16 | 0 |  |  | 6.66 |  |  | 5.9409
5-DaHall 1-PDU-12 | 17 |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 18 |  | 1.89 |  |  | 3.55 |  |  | 3.1234
5-DaHall 1-PDU-12 | 19 |  |  | 0 |  |  | 3.07 |  |  | 2.8563
5-DaHall 1-PDU-12 | 20 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 21 | 0 |  |  | 5.36 |  |  | 4.4338
5-DaHall 1-PDU-12 | 22 | 0 |  |  | 0
5-DaHall 1-PDU-12 | 23 |  | 0 |  |  | 0
5-DaHall 1-PDU-12 | 24 |  | 3.47 |  |  | 6.74 |  |  | 4.113
5-DaHall 1-PDU-12 | 25 |  |  | 3.11 |  |  | 3.54 |  |  | 3.2839
5-DaHall 1-PDU-12 | 26 |  |  | 0 |  |  | 5.03 |  |  | 4.8527
5-DaHall 1-PDU-12 | 27 | 0 |  |  | 0
5-DaHall 1-PDU-12 | 28 | 3.48 |  |  | 6 |  |  | 5.2757
5-DaHall 1-PDU-12 | 29 |  | 0 |  |  | 5.05 |  |  | 4.7545
5-DaHall 1-PDU-12 | 30 |  | 5.67 |  |  | 6.54 |  |  | 6.3531
5-DaHall 1-PDU-12 | 31 |  |  | 0 |  |  | 6.57 |  |  | 6.2081
5-DaHall 1-PDU-12 | 32 |  |  | 3.05 |  |  | 3.48 |  |  | 3.2036
5-DaHall 1-PDU-14 | 1 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-14 | 2 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-14 | 3 | 0 |  |  | 3.28 |  |  | 3.1702
5-DaHall 1-PDU-14 | 4 | 0 |  |  | 7.85 |  |  | 6.784
5-DaHall 1-PDU-14 | 5 |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 6 |  | 0 |  |  | 3.16 |  |  | 2.7567
5-DaHall 1-PDU-14 | 7 |  |  | 0 |  |  | 1.83 |  |  | 1.6507
5-DaHall 1-PDU-14 | 8 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 9 | 0 |  |  | 1.07 |  |  | 0.91896
5-DaHall 1-PDU-14 | 10 | 0 |  |  | 2.69 |  |  | 2.4612
5-DaHall 1-PDU-14 | 11 |  | 0 |  |  | 3.6 |  |  | 3.2292
5-DaHall 1-PDU-14 | 12 |  | 0 |  |  | 2.67 |  |  | 2.4455
5-DaHall 1-PDU-14 | 13 |  |  | 0 |  |  | 1.83 |  |  | 1.6831
5-DaHall 1-PDU-14 | 14 |  |  | 0 |  |  | 3.24 |  |  | 3.1126
5-DaHall 1-PDU-14 | 15 | 0 |  |  | 0
5-DaHall 1-PDU-14 | 16 | 0 |  |  | 0
5-DaHall 1-PDU-14 | 17 |  | 0 |  |  | 1.07 |  |  | 0.93687
5-DaHall 1-PDU-14 | 18 |  | 0 |  |  | 7.93 |  |  | 6.8537
5-DaHall 1-PDU-14 | 19 |  |  | 2.45 |  |  | 3.15 |  |  | 2.6305
5-DaHall 1-PDU-14 | 20 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 21 | 0 |  |  | 3.58 |  |  | 3.2902
5-DaHall 1-PDU-14 | 22 | 0 |  |  | 0
5-DaHall 1-PDU-14 | 23 |  | 0 |  |  | 3.25 |  |  | 2.7028
5-DaHall 1-PDU-14 | 24 |  | 0 |  |  | 5.7 |  |  | 5.2254
5-DaHall 1-PDU-14 | 25 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 26 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 27 | 0 |  |  | 0
5-DaHall 1-PDU-14 | 28 | 0 |  |  | 5.56 |  |  | 5.1566
5-DaHall 1-PDU-14 | 29 |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 30 |  | 0 |  |  | 1.21 |  |  | 0.00020326
5-DaHall 1-PDU-14 | 31 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-14 | 32 |  |  | 0 |  |  | 1.25 |  |  | 0.00020998
5-DaHall 1-PDU-16 | 1 | 4.66 | 1.33 | 6.05 | 4.77 | 1.37 | 6.16 | 4.7036 | 1.3449 | 6.1002
5-DaHall 1-PDU-16 | 2 | 0 | 0 | 0 | 3.19 | 3.18 | 2.06 | 3.058 | 3.0548 | 1.8161
5-DaHall 1-PDU-16 | 3 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-16 | 4 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-16 | 5 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-16 | 6 | 0 | 0 | 0 | 0 | 0 | 0
5-DaHall 1-PDU-16 | 7 | 1.51 |  |  | 4.18 |  |  | 3.4715
5-DaHall 1-PDU-16 | 8 | 0.41 |  |  | 5.18 |  |  | 4.3362
5-DaHall 1-PDU-16 | 9 |  | 0.39 |  |  | 3.73 |  |  | 1.7549
5-DaHall 1-PDU-16 | 10 |  | 0 |  |  | 1.02 |  |  | 0.9712
5-DaHall 1-PDU-16 | 11 |  |  | 0 |  |  | 0.73 |  |  | 0.40296
5-DaHall 1-PDU-16 | 12 |  |  | 0 |  |  | 2.63 |  |  | 2.4929
5-DaHall 1-PDU-16 | 13 | 0.42 |  |  | 1.63 |  |  | 1.3404
5-DaHall 1-PDU-16 | 14 | 1.48 |  |  | 1.74 |  |  | 1.6695
5-DaHall 1-PDU-16 | 15 |  | 2.18 |  |  | 2.46 |  |  | 2.3945
5-DaHall 1-PDU-16 | 16 |  | 0 |  |  | 8.25 |  |  | 7.8338
5-DaHall 1-PDU-16 | 17 |  |  | 0 |  |  | 1.6 |  |  | 1.5462
5-DaHall 1-PDU-16 | 18 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-16 | 19 | 0 |  |  | 4.91 |  |  | 4.52
5-DaHall 1-PDU-16 | 20 | 0.59 |  |  | 1.03 |  |  | 0.68925
5-DaHall 1-PDU-16 | 21 |  | 0.33 |  |  | 2.6 |  |  | 0.96691
5-DaHall 1-PDU-16 | 22 |  | 0.59 |  |  | 1.73 |  |  | 0.84193
5-DaHall 1-PDU-16 | 23 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-16 | 24 |  |  | 0 |  |  | 1.54 |  |  | 1.4455
5-DaHall 1-PDU-16 | 25 | 0.42 |  |  | 0.61 |  |  | 0.46351
5-DaHall 1-PDU-16 | 26 | 0 |  |  | 0.61 |  |  | 0.57227
5-DaHall 1-PDU-16 | 27 |  | 0.57 |  |  | 3.69 |  |  | 1.4893
5-DaHall 1-PDU-16 | 28 |  | 0 |  |  | 0.31 |  |  | 0.29024
5-DaHall 1-PDU-16 | 29 |  |  | 0.29 |  |  | 2.23 |  |  | 1.7927
5-DaHall 1-PDU-16 | 30 |  |  | 0.48 |  |  | 0.53 |  |  | 0.49895
5-DaHall 1-PDU-17 | 1 | 0.6 |  |  | 0.76 |  |  | 0.72242
5-DaHall 1-PDU-17 | 2 | 0 |  |  | 0.85 |  |  | 0.81744
5-DaHall 1-PDU-17 | 3 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 4 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 5 |  |  | 0 |  |  | 7.31 |  |  | 6.7267
5-DaHall 1-PDU-17 | 6 |  |  | 0 |  |  | 0.54 |  |  | 0.50001
5-DaHall 1-PDU-17 | 7 | 0 |  |  | 0
5-DaHall 1-PDU-17 | 8 | 0 |  |  | 2.45 |  |  | 2.2208
5-DaHall 1-PDU-17 | 9 |  | 0.75 |  |  | 7.31 |  |  | 5.7682
5-DaHall 1-PDU-17 | 10 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 11 |  |  | 0 |  |  | 0.55 |  |  | 0.52003
5-DaHall 1-PDU-17 | 12 |  |  | 0 |  |  | 1.15 |  |  | 1.1064
5-DaHall 1-PDU-17 | 13 | 0 |  |  | 1.84 |  |  | 1.71
5-DaHall 1-PDU-17 | 14 | 0 |  |  | 0
5-DaHall 1-PDU-17 | 15 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 16 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 17 |  |  | 0 |  |  | 0.8 |  |  | 0.7421
5-DaHall 1-PDU-17 | 18 |  |  | 0 |  |  | 0.85 |  |  | 0.78661
5-DaHall 1-PDU-17 | 19 | 0 |  |  | 0
5-DaHall 1-PDU-17 | 20 | 0 |  |  | 0
5-DaHall 1-PDU-17 | 21 |  | 0 |  |  | 2.45 |  |  | 2.1382
5-DaHall 1-PDU-17 | 22 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 23 |  |  | 0 |  |  | 1.15 |  |  | 1.065
5-DaHall 1-PDU-17 | 24 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 25 | 0 |  |  | 1.84 |  |  | 1.7783
5-DaHall 1-PDU-17 | 26 | 0 |  |  | 0
5-DaHall 1-PDU-17 | 27 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 28 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 29 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 30 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 31 | 0 |  |  | 0
5-DaHall 1-PDU-17 | 32 | 0 |  |  | 0
5-DaHall 1-PDU-17 | 33 |  | 0 |  |  | 0
5-DaHall 1-PDU-17 | 34 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 1 | 0.82 |  |  | 1.12 |  |  | 0.82545
5-DaHall 1-PDU-18 | 2 | 0 |  |  | 0.79 |  |  | 0.7625
5-DaHall 1-PDU-18 | 3 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 4 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 5 |  |  | 0 |  |  | 5 |  |  | 4.645
5-DaHall 1-PDU-18 | 6 |  |  | 0 |  |  | 0.42 |  |  | 0.39283
5-DaHall 1-PDU-18 | 7 | 0 |  |  | 0
5-DaHall 1-PDU-18 | 8 | 0 |  |  | 2.3 |  |  | 2.1394
5-DaHall 1-PDU-18 | 9 |  | 0 |  |  | 5.02 |  |  | 4.8339
5-DaHall 1-PDU-18 | 10 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 11 |  |  | 0 |  |  | 0.42 |  |  | 0.40911
5-DaHall 1-PDU-18 | 12 |  |  | 0 |  |  | 1.08 |  |  | 1.0356
5-DaHall 1-PDU-18 | 13 | 0 |  |  | 1.01 |  |  | 0.9383
5-DaHall 1-PDU-18 | 14 | 0 |  |  | 0
5-DaHall 1-PDU-18 | 15 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 16 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 17 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 18 |  |  | 0 |  |  | 0.8 |  |  | 0.73835
5-DaHall 1-PDU-18 | 19 | 0 |  |  | 0
5-DaHall 1-PDU-18 | 20 | 0 |  |  | 0
5-DaHall 1-PDU-18 | 21 |  | 0 |  |  | 2.32 |  |  | 2.0598
5-DaHall 1-PDU-18 | 22 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 23 |  |  | 0 |  |  | 1.07 |  |  | 0.99228
5-DaHall 1-PDU-18 | 24 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 25 | 0 |  |  | 1.02 |  |  | 0.98612
5-DaHall 1-PDU-18 | 26 | 0 |  |  | 0
5-DaHall 1-PDU-18 | 27 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 28 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 29 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 30 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 31 | 0 |  |  | 0
5-DaHall 1-PDU-18 | 32 | 0 |  |  | 0
5-DaHall 1-PDU-18 | 33 |  | 0 |  |  | 0
5-DaHall 1-PDU-18 | 34 |  | 0 |  |  | 0
5-DaHall 1-PDU-19 | 1 | 0 |  |  | 9.4 |  |  | 4.3555
5-DaHall 1-PDU-19 | 2 | 0.64 |  |  | 8.6 |  |  | 3.1937
5-DaHall 1-PDU-19 | 3 |  | 0 |  |  | 7.55 |  |  | 4.0838
5-DaHall 1-PDU-19 | 4 |  | 0.87 |  |  | 9.47 |  |  | 3.4714
5-DaHall 1-PDU-19 | 5 |  |  | 0 |  |  | 8.62 |  |  | 3.6577
5-DaHall 1-PDU-19 | 6 |  |  | 2.19 |  |  | 5.56 |  |  | 3.1371
5-DaHall 1-PDU-19 | 7 | 0.67 |  |  | 10.37 |  |  | 5.0432
5-DaHall 1-PDU-19 | 8 | 1.03 |  |  | 10.83 |  |  | 5.3781
5-DaHall 1-PDU-19 | 9 |  | 0.68 |  |  | 9.94 |  |  | 3.6832
5-DaHall 1-PDU-19 | 10 |  | 0.5 |  |  | 8.24 |  |  | 5.0353
5-DaHall 1-PDU-19 | 11 |  |  | 0 |  |  | 13.25 |  |  | 3.2033
5-DaHall 1-PDU-19 | 12 |  |  | 0 |  |  | 4.7 |  |  | 3.927
5-DaHall 1-PDU-19 | 13 | 0.65 |  |  | 12.45 |  |  | 4.3621
5-DaHall 1-PDU-19 | 14 | 1.15 |  |  | 3.11 |  |  | 1.7822
5-DaHall 1-PDU-19 | 15 |  | 0 |  |  | 10.73 |  |  | 5.495
5-DaHall 1-PDU-19 | 16 |  | 1.16 |  |  | 14.87 |  |  | 6.3267
5-DaHall 1-PDU-19 | 17 |  |  | 1.83 |  |  | 6.06 |  |  | 4.0167
5-DaHall 1-PDU-19 | 18 |  |  | 1.15 |  |  | 11.12 |  |  | 5.046
5-DaHall 1-PDU-19 | 19 | 1.12 |  |  | 6.15 |  |  | 3.009
5-DaHall 1-PDU-19 | 20 | 1.16 |  |  | 12.03 |  |  | 7.1291
5-DaHall 1-PDU-19 | 21 |  | 0 |  |  | 10.29 |  |  | 6.9643
5-DaHall 1-PDU-19 | 22 |  | 0.84 |  |  | 10.5 |  |  | 8.1055
5-DaHall 1-PDU-19 | 23 |  |  | 0 |  |  | 11.63 |  |  | 8.9514
5-DaHall 1-PDU-19 | 24 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-20 | 1 | 0 |  |  | 9.39 |  |  | 4.388
5-DaHall 1-PDU-20 | 2 | 0.63 |  |  | 9.55 |  |  | 3.8187
5-DaHall 1-PDU-20 | 3 |  | 0 |  |  | 7.21 |  |  | 3.9414
5-DaHall 1-PDU-20 | 4 |  | 0.92 |  |  | 9.22 |  |  | 3.4008
5-DaHall 1-PDU-20 | 5 |  |  | 0 |  |  | 8.53 |  |  | 3.6163
5-DaHall 1-PDU-20 | 6 |  |  | 1.36 |  |  | 4.71 |  |  | 2.1512
5-DaHall 1-PDU-20 | 7 | 0.68 |  |  | 10.53 |  |  | 5.0551
5-DaHall 1-PDU-20 | 8 | 1.19 |  |  | 11.41 |  |  | 5.6127
5-DaHall 1-PDU-20 | 9 |  | 0.59 |  |  | 9.61 |  |  | 3.6921
5-DaHall 1-PDU-20 | 10 |  | 0.63 |  |  | 8.46 |  |  | 5.0004
5-DaHall 1-PDU-20 | 11 |  |  | 0 |  |  | 12.9 |  |  | 2.5298
5-DaHall 1-PDU-20 | 12 |  |  | 0 |  |  | 4.64 |  |  | 3.8241
5-DaHall 1-PDU-20 | 13 | 0.69 |  |  | 11.93 |  |  | 4.2581
5-DaHall 1-PDU-20 | 14 | 1.23 |  |  | 3.04 |  |  | 1.6513
5-DaHall 1-PDU-20 | 15 |  | 0 |  |  | 11.38 |  |  | 5.6958
5-DaHall 1-PDU-20 | 16 |  | 1.03 |  |  | 15.05 |  |  | 6.4098
5-DaHall 1-PDU-20 | 17 |  |  | 2.5 |  |  | 5.93 |  |  | 4.2516
5-DaHall 1-PDU-20 | 18 |  |  | 1 |  |  | 10.57 |  |  | 4.8746
5-DaHall 1-PDU-20 | 19 | 1.07 |  |  | 6.55 |  |  | 3.0109
5-DaHall 1-PDU-20 | 20 | 0.86 |  |  | 12.25 |  |  | 2.7153
5-DaHall 1-PDU-20 | 21 |  | 0 |  |  | 9.97 |  |  | 6.7808
5-DaHall 1-PDU-20 | 22 |  | 0.59 |  |  | 5.87 |  |  | 2.8347
5-DaHall 1-PDU-20 | 23 |  |  | 0 |  |  | 5.96 |  |  | 2.5332
5-DaHall 1-PDU-20 | 24 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-21 | 1 | 0 |  |  | 10.18 |  |  | 3.678
5-DaHall 1-PDU-21 | 2 | 0.65 |  |  | 8.77 |  |  | 2.8627
5-DaHall 1-PDU-21 | 3 |  | 0 |  |  | 8.9 |  |  | 4.8486
5-DaHall 1-PDU-21 | 4 |  | 0.66 |  |  | 6.56 |  |  | 2.6554
5-DaHall 1-PDU-21 | 5 |  |  | 0 |  |  | 9.09 |  |  | 5.59
5-DaHall 1-PDU-21 | 6 |  |  | 2.15 |  |  | 8.58 |  |  | 4.3625
5-DaHall 1-PDU-21 | 7 | 0.66 |  |  | 10.69 |  |  | 4.4081
5-DaHall 1-PDU-21 | 8 | 1.52 |  |  | 9.12 |  |  | 5.3842
5-DaHall 1-PDU-21 | 9 |  | 0.66 |  |  | 10.61 |  |  | 4.5618
5-DaHall 1-PDU-21 | 10 |  | 1.1 |  |  | 11.74 |  |  | 6.742
5-DaHall 1-PDU-21 | 11 |  |  | 0 |  |  | 9.63 |  |  | 2.9031
5-DaHall 1-PDU-21 | 12 |  |  | 0 |  |  | 2.9 |  |  | 1.7161
5-DaHall 1-PDU-21 | 13 | 0.65 |  |  | 12.81 |  |  | 4.3279
5-DaHall 1-PDU-21 | 14 | 2.02 |  |  | 3.4 |  |  | 2.3178
5-DaHall 1-PDU-21 | 15 |  | 0.85 |  |  | 8.91 |  |  | 3.663
5-DaHall 1-PDU-21 | 16 |  | 0.5 |  |  | 14.46 |  |  | 8.1453
5-DaHall 1-PDU-21 | 17 |  |  | 0.86 |  |  | 9.81 |  |  | 4.7874
5-DaHall 1-PDU-21 | 18 |  |  | 1.19 |  |  | 7.45 |  |  | 4.5421
5-DaHall 1-PDU-21 | 19 | 1.76 |  |  | 5.14 |  |  | 3.3129
5-DaHall 1-PDU-21 | 20 | 0.86 |  |  | 11.51 |  |  | 7.7999
5-DaHall 1-PDU-21 | 21 |  | 0 |  |  | 9.99 |  |  | 5.0671
5-DaHall 1-PDU-21 | 22 |  | 0.85 |  |  | 9.89 |  |  | 7.3646
5-DaHall 1-PDU-21 | 23 |  |  | 0 |  |  | 11.6 |  |  | 7.7807
5-DaHall 1-PDU-21 | 24 |  |  | 0 |  |  | 0
5-DaHall 1-PDU-22 | 1 | 0 |  |  | 10.5 |  |  | 4.0021
5-DaHall 1-PDU-22 | 2 | 0.63 |  |  | 8.71 |  |  | 2.823
5-DaHall 1-PDU-22 | 3 |  | 0 |  |  | 8.7 |  |  | 4.7818
5-DaHall 1-PDU-22 | 4 |  | 0.62 |  |  | 5.8 |  |  | 2.3563
5-DaHall 1-PDU-22 | 5 |  |  | 0 |  |  | 8.58 |  |  | 5.1268
5-DaHall 1-PDU-22 | 6 |  |  | 1.09 |  |  | 8.87 |  |  | 2.9584
5-DaHall 1-PDU-22 | 7 | 0.64 |  |  | 10.21 |  |  | 4.2732
5-DaHall 1-PDU-22 | 8 | 1.46 |  |  | 9.65 |  |  | 5.8281
5-DaHall 1-PDU-22 | 9 |  | 0.58 |  |  | 10.56 |  |  | 4.368
5-DaHall 1-PDU-22 | 10 |  | 1.14 |  |  | 12.02 |  |  | 6.497
5-DaHall 1-PDU-22 | 11 |  |  | 0 |  |  | 10.01 |  |  | 3.0905
5-DaHall 1-PDU-22 | 12 |  |  | 0 |  |  | 2.98 |  |  | 1.7404
5-DaHall 1-PDU-22 | 13 | 0.62 |  |  | 13.02 |  |  | 4.0657
5-DaHall 1-PDU-22 | 14 | 1.88 |  |  | 3.02 |  |  | 2.34
5-DaHall 1-PDU-22 | 15 |  | 0.85 |  |  | 9.5 |  |  | 3.7615
5-DaHall 1-PDU-22 | 16 |  | 0.57 |  |  | 14.77 |  |  | 8.5137
5-DaHall 1-PDU-22 | 17 |  |  | 0.84 |  |  | 9.32 |  |  | 4.3797
5-DaHall 1-PDU-22 | 18 |  |  | 0.91 |  |  | 7.27 |  |  | 4.3303
5-DaHall 1-PDU-22 | 19 | 2.27 |  |  | 5.75 |  |  | 3.5231
5-DaHall 1-PDU-22 | 20 | 0.59 |  |  | 11.85 |  |  | 3.2377
5-DaHall 1-PDU-22 | 21 |  | 0 |  |  | 9.77 |  |  | 4.8018
5-DaHall 1-PDU-22 | 22 |  | 0.59 |  |  | 5.69 |  |  | 3.2135
5-DaHall 1-PDU-22 | 23 |  |  | 0 |  |  | 8.88 |  |  | 4.6486
5-DaHall 1-PDU-22 | 24 |  |  | 0 |  |  | 0

## 4층_부하량
장비명 | 분기번호 | MIN |  |  | MAX |  |  | AVG
|  | R | S | T | R | S | T | R | S | T
4-DaHall 1-PDU-02 | 1 | 0.62 | 0.54 | 0.78 | 1.04 | 0.78 | 1.19 | 0.88309 | 0.69963 | 1.0559
4-DaHall 1-PDU-02 | 2 | 34.8 |  |  | 35.48 |  |  | 35.2048
4-DaHall 1-PDU-02 | 3 |  | 32.08 |  |  | 33.16 |  |  | 32.4976
4-DaHall 1-PDU-02 | 4 |  |  | 30.36 |  |  | 36.38 |  |  | 36.0017
4-DaHall 1-PDU-02 | 5 | 40.4 |  |  | 42.16 |  |  | 40.9562
4-DaHall 1-PDU-02 | 6 |  | 12.15 |  |  | 12.63 |  |  | 12.3198
4-DaHall 1-PDU-02 | 7 |  |  | 28.37 |  |  | 29.89 |  |  | 28.991
4-DaHall 1-PDU-02 | 8 | 0 |  |  | 0
4-DaHall 1-PDU-02 | 9 |  | 0 |  |  | 0
4-DaHall 1-PDU-04 | 1 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-PDU-04 | 2 | 38.63 |  |  | 40.17 |  |  | 39.4635
4-DaHall 1-PDU-04 | 3 |  | 26.4 |  |  | 31.32 |  |  | 28.2948
4-DaHall 1-PDU-04 | 4 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-04 | 5 | 9.47 |  |  | 9.99 |  |  | 9.6382
4-DaHall 1-PDU-04 | 6 |  | 14.21 |  |  | 15.47 |  |  | 14.5532
4-DaHall 1-PDU-04 | 7 |  |  | 21.53 |  |  | 25.82 |  |  | 22.2232
4-DaHall 1-PDU-04 | 8 | 21.3 |  |  | 23.67 |  |  | 22.3842
4-DaHall 1-PDU-04 | 9 |  | 0 |  |  | 0
4-DaHall 1-PDU-06 | 1 | 9.83 |  |  | 11.61 |  |  | 10.6138
4-DaHall 1-PDU-06 | 2 |  | 0 |  |  | 0
4-DaHall 1-PDU-06 | 3 |  |  | 7.81 |  |  | 9.17 |  |  | 8.9534
4-DaHall 1-PDU-06 | 4 | 6.86 |  |  | 7.56 |  |  | 6.9284
4-DaHall 1-PDU-06 | 5 |  | 0 |  |  | 0
4-DaHall 1-PDU-06 | 6 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-06 | 7 | 8.09 |  |  | 9.74 |  |  | 8.3674
4-DaHall 1-PDU-06 | 8 |  | 13.5 |  |  | 15.4 |  |  | 14.0982
4-DaHall 1-PDU-06 | 9 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-06 | 10 | 36.52 |  |  | 41.48 |  |  | 39.6661
4-DaHall 1-PDU-06 | 11 |  | 0 |  |  | 0
4-DaHall 1-PDU-06 | 12 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-08 | 1 | 22.18 |  |  | 24.58 |  |  | 22.6604
4-DaHall 1-PDU-08 | 2 |  | 32.62 |  |  | 35.23 |  |  | 33.2791
4-DaHall 1-PDU-08 | 3 |  |  | 5.29 |  |  | 5.63 |  |  | 5.4024
4-DaHall 1-PDU-08 | 4 | 9.06 |  |  | 9.95 |  |  | 9.4718
4-DaHall 1-PDU-08 | 5 |  | 7.32 |  |  | 7.95 |  |  | 7.4679
4-DaHall 1-PDU-08 | 6 |  |  | 11.08 |  |  | 13.64 |  |  | 12.24
4-DaHall 1-PDU-08 | 7 | 12.98 |  |  | 13.16 |  |  | 13.0529
4-DaHall 1-PDU-08 | 8 |  | 23.81 |  |  | 34.73 |  |  | 27.0223
4-DaHall 1-PDU-08 | 9 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-08 | 10 | 0 |  |  | 0
4-DaHall 1-PDU-08 | 11 |  | 0 |  |  | 0
4-DaHall 1-PDU-08 | 12 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-10 | 1 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-PDU-10 | 2 | 28.97 | 26.42 | 27.99 | 32.43 | 29.91 | 31.28 | 30.5636 | 27.9705 | 29.4858
4-DaHall 1-PDU-10 | 3 | 2.95 | 2.66 | 3.22 | 27.88 | 27.19 | 26.8 | 15.1943 | 14.7978 | 14.6503
4-DaHall 1-PDU-01 | 1 | 1.13 | 0.89 | 1.33 | 1.47 | 1.19 | 1.65 | 1.2633 | 1.0083 | 1.47
4-DaHall 1-PDU-01 | 2 | 37.09 |  |  | 37.9 |  |  | 37.4998
4-DaHall 1-PDU-01 | 3 |  | 33.54 |  |  | 34.95 |  |  | 34.2678
4-DaHall 1-PDU-01 | 4 |  |  | 31.18 |  |  | 37.59 |  |  | 37.2639
4-DaHall 1-PDU-01 | 5 | 40.91 |  |  | 42.43 |  |  | 41.4804
4-DaHall 1-PDU-01 | 6 |  | 22.9 |  |  | 24.59 |  |  | 23.5345
4-DaHall 1-PDU-01 | 7 |  |  | 12.44 |  |  | 12.96 |  |  | 12.608
4-DaHall 1-PDU-01 | 8 | 0 |  |  | 0
4-DaHall 1-PDU-01 | 9 |  | 0 |  |  | 0
4-DaHall 1-PDU-03 | 1 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-PDU-03 | 2 | 31.81 |  |  | 33.51 |  |  | 32.2199
4-DaHall 1-PDU-03 | 3 |  | 26.71 |  |  | 30.46 |  |  | 28.4408
4-DaHall 1-PDU-03 | 4 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-03 | 5 | 6.14 |  |  | 6.62 |  |  | 6.3018
4-DaHall 1-PDU-03 | 6 |  | 10.15 |  |  | 10.92 |  |  | 10.3842
4-DaHall 1-PDU-03 | 7 |  |  | 16.11 |  |  | 29.63 |  |  | 28.4161
4-DaHall 1-PDU-03 | 8 | 17.56 |  |  | 19.89 |  |  | 18.5092
4-DaHall 1-PDU-03 | 9 |  | 0 |  |  | 0
4-DaHall 1-PDU-05 | 1 | 8.38 |  |  | 9.72 |  |  | 8.9695
4-DaHall 1-PDU-05 | 2 |  | 0 |  |  | 0
4-DaHall 1-PDU-05 | 3 |  |  | 6.39 |  |  | 7.8 |  |  | 7.7355
4-DaHall 1-PDU-05 | 4 | 7.15 |  |  | 7.54 |  |  | 7.2205
4-DaHall 1-PDU-05 | 5 |  | 0 |  |  | 0
4-DaHall 1-PDU-05 | 6 |  |  | 12.68 |  |  | 13.18 |  |  | 12.8628
4-DaHall 1-PDU-05 | 7 | 6.06 |  |  | 7.61 |  |  | 6.5082
4-DaHall 1-PDU-05 | 8 |  | 10.2 |  |  | 13.85 |  |  | 11.8335
4-DaHall 1-PDU-05 | 9 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-05 | 10 | 31.56 |  |  | 37.17 |  |  | 34.7027
4-DaHall 1-PDU-05 | 11 |  | 0 |  |  | 0
4-DaHall 1-PDU-05 | 12 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-07 | 1 | 19.95 |  |  | 21.93 |  |  | 20.3838
4-DaHall 1-PDU-07 | 2 |  | 32.86 |  |  | 35.56 |  |  | 33.5635
4-DaHall 1-PDU-07 | 3 |  |  | 5.2 |  |  | 5.56 |  |  | 5.3006
4-DaHall 1-PDU-07 | 4 | 10.17 |  |  | 10.88 |  |  | 10.3767
4-DaHall 1-PDU-07 | 5 |  | 5.88 |  |  | 6.47 |  |  | 6.0186
4-DaHall 1-PDU-07 | 6 |  |  | 14.26 |  |  | 17.09 |  |  | 15.6783
4-DaHall 1-PDU-07 | 7 | 13.74 |  |  | 13.97 |  |  | 13.8234
4-DaHall 1-PDU-07 | 8 |  | 30.44 |  |  | 37.85 |  |  | 34.3054
4-DaHall 1-PDU-07 | 9 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-07 | 10 | 0 |  |  | 0
4-DaHall 1-PDU-07 | 11 |  | 0 |  |  | 0
4-DaHall 1-PDU-07 | 12 |  |  | 0 |  |  | 0
4-DaHall 1-PDU-09 | 1 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-PDU-09 | 2 | 0 | 0 | 0 | 0 | 0 | 0
4-DaHall 1-PDU-09 | 3 | 0 | 0 | 0 | 0 | 0 | 0

## 4F_current (hidden)
4F | A(전류)
4-DaHall 1-PDU-01-01 | [branch#001] [A] current
4-DaHall 1-PDU-01-02 | [branch#002] [A] current
4-DaHall 1-PDU-01-03 | [branch#003] [A] current
4-DaHall 1-PDU-01-04 | [branch#004] [A] current
4-DaHall 1-PDU-01-05 | [branch#005] [A] current
4-DaHall 1-PDU-01-06 | [branch#006] [A] current
4-DaHall 1-PDU-01-07 | [branch#007] [A] current
4-DaHall 1-PDU-01-08 | [branch#008] [A] current
4-DaHall 1-PDU-01-09 | [branch#009] [A] current
4-DaHall 1-PDU-02-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
4-DaHall 1-PDU-02-02 | [branch#002] [A] current
4-DaHall 1-PDU-02-03 | [branch#003] [A] current
4-DaHall 1-PDU-02-04 | [branch#004] [A] current
4-DaHall 1-PDU-02-05 | [branch#005] [A] current
4-DaHall 1-PDU-02-06 | [branch#006] [A] current
4-DaHall 1-PDU-02-07 | [branch#007] [A] current
4-DaHall 1-PDU-02-08 | [branch#008] [A] current
4-DaHall 1-PDU-02-09 | [branch#009] [A] current
4-DaHall 1-PDU-03-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
4-DaHall 1-PDU-03-02 | [branch#002] [A] current
4-DaHall 1-PDU-03-03 | [branch#003] [A] current
4-DaHall 1-PDU-03-04 | [branch#004] [A] current
4-DaHall 1-PDU-03-05 | [branch#005] [A] current
4-DaHall 1-PDU-03-06 | [branch#006] [A] current
4-DaHall 1-PDU-03-07 | [branch#007] [A] current
4-DaHall 1-PDU-03-08 | [branch#008] [A] current
4-DaHall 1-PDU-03-09 | [branch#009] [A] current
4-DaHall 1-PDU-04-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
4-DaHall 1-PDU-04-02 | [branch#002] [A] current
4-DaHall 1-PDU-04-03 | [branch#003] [A] current
4-DaHall 1-PDU-04-04 | [branch#004] [A] current
4-DaHall 1-PDU-04-05 | [branch#005] [A] current
4-DaHall 1-PDU-04-06 | [branch#006] [A] current
4-DaHall 1-PDU-04-07 | [branch#007] [A] current
4-DaHall 1-PDU-04-08 | [branch#008] [A] current
4-DaHall 1-PDU-04-09 | [branch#009] [A] current
4-DaHall 1-PDU-05-01 | [branch#001] [A] current
4-DaHall 1-PDU-05-02 | [branch#002] [A] current
4-DaHall 1-PDU-05-03 | [branch#003] [A] current
4-DaHall 1-PDU-05-04 | [branch#004] [A] current
4-DaHall 1-PDU-05-05 | [branch#005] [A] current
4-DaHall 1-PDU-05-06 | [branch#006] [A] current
4-DaHall 1-PDU-05-07 | [branch#007] [A] current
4-DaHall 1-PDU-05-08 | [branch#008] [A] current
4-DaHall 1-PDU-05-09 | [branch#009] [A] current
4-DaHall 1-PDU-05-10 | [branch#010] [A] current
4-DaHall 1-PDU-05-11 | [branch#011] [A] current
4-DaHall 1-PDU-05-12 | [branch#012] [A] current
4-DaHall 1-PDU-06-01 | [branch#001] [A] current
4-DaHall 1-PDU-06-02 | [branch#002] [A] current
4-DaHall 1-PDU-06-03 | [branch#003] [A] current
4-DaHall 1-PDU-06-04 | [branch#004] [A] current
4-DaHall 1-PDU-06-05 | [branch#005] [A] current
4-DaHall 1-PDU-06-06 | [branch#006] [A] current
4-DaHall 1-PDU-06-07 | [branch#007] [A] current
4-DaHall 1-PDU-06-08 | [branch#008] [A] current
4-DaHall 1-PDU-06-09 | [branch#009] [A] current
4-DaHall 1-PDU-06-10 | [branch#010] [A] current
4-DaHall 1-PDU-06-11 | [branch#011] [A] current
4-DaHall 1-PDU-06-12 | [branch#012] [A] current
4-DaHall 1-PDU-07-01 | [branch#001] [A] current
4-DaHall 1-PDU-07-02 | [branch#002] [A] current
4-DaHall 1-PDU-07-03 | [branch#003] [A] current
4-DaHall 1-PDU-07-04 | [branch#004] [A] current
4-DaHall 1-PDU-07-05 | [branch#005] [A] current
4-DaHall 1-PDU-07-06 | [branch#006] [A] current
4-DaHall 1-PDU-07-07 | [branch#007] [A] current
4-DaHall 1-PDU-07-08 | [branch#008] [A] current
4-DaHall 1-PDU-07-09 | [branch#009] [A] current
4-DaHall 1-PDU-07-10 | [branch#010] [A] current
4-DaHall 1-PDU-07-11 | [branch#011] [A] current
4-DaHall 1-PDU-07-12 | [branch#012] [A] current
4-DaHall 1-PDU-08-01 | [branch#001] [A] current
4-DaHall 1-PDU-08-02 | [branch#002] [A] current
4-DaHall 1-PDU-08-03 | [branch#003] [A] current
4-DaHall 1-PDU-08-04 | [branch#004] [A] current
4-DaHall 1-PDU-08-05 | [branch#005] [A] current
4-DaHall 1-PDU-08-06 | [branch#006] [A] current
4-DaHall 1-PDU-08-07 | [branch#007] [A] current
4-DaHall 1-PDU-08-08 | [branch#008] [A] current
4-DaHall 1-PDU-08-09 | [branch#009] [A] current
4-DaHall 1-PDU-08-10 | [branch#010] [A] current
4-DaHall 1-PDU-08-11 | [branch#011] [A] current
4-DaHall 1-PDU-08-12 | [branch#012] [A] current
4-DaHall 1-PDU-09-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
4-DaHall 1-PDU-09-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
4-DaHall 1-PDU-09-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
4-DaHall 1-PDU-10-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
4-DaHall 1-PDU-10-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
4-DaHall 1-PDU-10-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
4-EPS-CEP-06-01-01 | [branch#001] [R] I1 | [branch#001] [S] I2 | [branch#001] [T] I3
4-EPS-CEP-06-01-02 | [branch#002] [R] I1 | [branch#002] [S] I2 | [branch#002] [T] I3
4-EPS-CEP-06-01-03 | [branch#003] [R] I1 | [branch#003] [S] I2 | [branch#003] [T] I3
4-EPS-CEP-06-01-04 | [branch#004] [R] I1 | [branch#004] [S] I2 | [branch#004] [T] I3
4-EPS-CEP-06-01-05 | [branch#005] [R] I1 | [branch#005] [S] I2 | [branch#005] [T] I3
4-EPS-CEP-06-01-06 | [branch#006] [R] I1 | [branch#006] [S] I2 | [branch#006] [T] I3

## 각_층_분전반_부하량 (hidden)
차단기 사용 현황
7층 | Device Name | DE 분전반 신규명칭 | 분전반 명칭 | 차단전류 (A) | 메인차단용량 (kVA) | IT허용용량 (kVA) | 사용량 (kVA) | 사용율 (%) | 2P 20A |  |  | 2P 30A |  |  | 2P 50A |  |  | 4P 225A |  |  | 3P 100A |  |  | 3P 150A |  |  | 4P 50A
[9 empty] | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF
| 7-Data Hall 1-RPP-01 | 7-1-A1 | UPS 출력 분전반 A1(From:7F 창고) | 400 | 263.2717 | 200 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | #REF! | #REF!
| 7-Data Hall 1-RPP-02 | 7-1-B1 | UPS 출력 분전반 B1(From:7F 창고) | 400 | 263.2717 | 200 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | #REF! | #REF!
| 7-Data Hall 1-PDU-01 | 7-1-A2 | U3-7A PANEL(From:TRroom-U7-5A) | 300 | 197.4538 | 150 | #REF! | #REF! |  |  |  | 2 | #REF! | #REF!
| 7-Data Hall 1-PDU-02 | 7-1-B2 | U3-7B PANEL(From:TRroom-U7-6B) | 300 | 197.4538 | 150 | #REF! | #REF! |  |  |  | 2 | #REF! | #REF!
| 7-Data Hall 1-RPP-03 | 7-1-A3 | UPS 출력 분전반 A2(From:7F 창고) | 225 | 148.0903 | 112.5 | #REF! | #REF! | [6 empty] | 2 | #REF! | #REF!
| 7-Data Hall 1-RPP-04 | 7-1-B3 | UPS 출력 분전반 B2(From:7F 창고) | 225 | 148.0903 | 112.5 | #REF! | #REF! | [6 empty] | 2 | #REF! | #REF!
| 7-Data Hall 1-PDU-03 | 7-1-A4 | UPS 출력 분전반 A(From:7F TR.Room) | 400 | 263.2717 | 200 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 7-Data Hall 1-PDU-04 | 7-1-B4 | UPS 출력 분전반 B(From:7F TR.Room) | 400 | 263.2717 | 200 | #REF! | #REF! | [12 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
|  | 총계 | 총계 | 1400 | 921.451 | 700 | #REF! | #REF! | [18 empty] | 2 | #REF! | #REF!
6층 | Device Name | DE 분전반 신규명칭 | 분전반 명칭 | 차단전류 (A) | 메인차단용량 (kVA) | IT허용용량 (kVA) | 사용량 (kVA) | 사용율 (%) | 2P 30A
[9 empty] | 총계 | ON | OFF
| 6-DaHall 1-PDU-01 | 6-1-A1 | U-A1 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-02 | 6-1-B1 | U-B1 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-03 | 6-1-A2 | U-A2 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-04 | 6-1-B2 | U-B2 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-05 | 6-1-A3 | U6-A5 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-06 | 6-1-B3 | U6-B5 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-07 | 6-1-A4 | U6-A6 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-08 | 6-1-B4 | U6-B6 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-09 | 6-1-A5 | U-A3 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-10 | 6-1-B5 | U-B3 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-11 | 6-1-A6 | U-A4 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-12 | 6-1-B6 | U-B4 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-13 | 6-1-A7 | U6-A7 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-14 | 6-1-B7 | U6-B7 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
|  | 총계 | 총계 | 3400 | 2237.8096 | 700 | #REF! | #REF!
5층 | Device Name | DE 분전반 신규명칭 | 분전반 명칭 | 차단전류 (A) | 메인차단용량 (kVA) | IT허용용량 (kVA) | 사용량 (kVA) | 사용율 (%) | 2P 30A |  |  | 2P 50A |  |  | 3P 60A |  |  | 3P 30A |  |  | 3P 20A |  |  | 3P 50A
[9 empty] | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF
| 5-DaHall 1-PDU-01 | 5-1-A1 | U5-1A | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF! |  |  |  | 2 | 1 | 1
| 5-DaHall 1-PDU-02 | 5-1-B1 | U5-1B | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF! |  |  |  | 2 | 1 | 1
| 5-DaHall 1-PDU-03 | 5-1-A2 | U5-2A | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF! |  |  |  | 2 | 1 | 1
| 5-DaHall 1-PDU-04 | 6-1-B2 | U5-2B | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF! |  |  |  | 2 | 1 | 1
| 5-DaHall 1-PDU-05 | 5-1-A3 | U5-3A | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-06 | 5-1-B3 | U5-3B | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-07 | 5-1-A4 | PDU(A)-9 | 200 | 131.6359 | 23.9316 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-08 | 5-1-B4 | PDU(B)-9 | 200 | 131.6359 | 23.9316 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-09 | 5-1-A5 | PDU(A)-10 | 200 | 131.6359 | 23.9316 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-10 | 5-1-B5 | PDU(B)-10 | 200 | 131.6359 | 23.9316 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-11 | 5-1-A6 | PDU(A)-1 | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-12 | 5-1-B6 | PDU(B)-1 | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-13 | 5-1-A7 | PDU(A)-2 | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-14 | 5-1-B7 | PDU(B)-2 | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-15 | 5-1-A8 | PDU(A)-3 | 300 | 197.4538 | 35.8974 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-16 | 5-1-B8 | PDU(B)-3 | 300 | 197.4538 | 35.8974 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 1 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-17 | 5-1-A9 | Singtel PDU-8-A | 200 | 131.6359 | 23.9316 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-18 | 5-1-B9 | Singtel PDU-8-B | 200 | 131.6359 | 23.9316 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-19 | 5-1-A10 | LG PDU(A1) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 3 | #REF! | #REF! | 5 | #REF! | #REF! |  |  |  | 2 | #REF! | #REF! | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-20 | 5-1-B10 | LG PDU(B1) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 3 | #REF! | #REF! | 5 | #REF! | #REF! |  |  |  | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-21 | 5-1-A11 | LG PDU(A2) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 3 | #REF! | #REF! | 5 | #REF! | #REF! |  |  |  | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-22 | 5-1-B11 | LG PDU(B2) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 3 | #REF! | #REF! | 5 | #REF! | #REF! |  |  |  | 2 | #REF! | #REF! | 1 | #REF! | #REF! | 2 | #REF! | #REF!
|  |  | PDU6B-1T | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
|  |  | PDU(C) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF! | 2 | 0 | 2
|  | 총계 | 총계 | 5850 | 3850.3489 | 700 | #REF! | #REF!
4층 | Device Name | DE 분전반 신규명칭 | 분전반 명칭 | 차단전류 (A) | 메인차단용량 (kVA) | 통신전력기준 (kVA) | 사용량 (kVA) | 사용율 (%) | 2P 100A |  |  | 4P 100A |  |  | 4P 200A
[9 empty] | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF
| 4-DaHall 1-PDU-01 | 4-1-A1 | KEN 8 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | 1 | 0
| 4-DaHall 1-PDU-02 | 4-1-B1 | KEN 1 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | 1 | 0
| 4-DaHall 1-PDU-03 | 4-1-A2 | KEN 9 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | 0 | 1
| 4-DaHall 1-PDU-04 | 4-1-B2 | KEN 2 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | 0 | 1
| 4-DaHall 1-PDU-05 | 4-1-A3 | KEN 10 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-06 | 4-1-B3 | KEN 3 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-07 | 4-1-A4 | KEN 13 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-08 | 4-1-B4 | KEN 6 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-09 | 4-1-A5 | KEN 14 | 300 | 197.4538 | 70 | #REF! | #REF! | [6 empty] | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-10 | 4-1-B5 | KEN 7 | 300 | 197.4538 | 70 | #REF! | #REF! | [6 empty] | 1 | #REF! | #REF!
|  | 총계 | 총계 | 3000 | 1974.5379 | 700 | #REF! | #REF!
|  |  | 각층 부하분담율 |  |  | 사용량(A) | 층 배분(%)
|  |  | 4층 | IDC | IDC | #REF! | #REF!
|  |  |  | IP | 세종 시스템 | #REF! | #REF!
|  |  |  | 공통 | 세종 시스템 | #REF! | #REF!
|  |  |  | IP | core room | #REF! | #REF!
[5 empty] | 총 합 | #REF! | #REF!
|  |  | 5층 | IDC | IDC | #REF!
|  |  | 6층 | IDC | IDC | #REF!
|  |  | 7층 | IDC | IDC상면 | #REF! | #REF!
|  |  |  | IP | 세종 인터넷 | #REF! | #REF!
|  |  |  | 전송 | 전송 | #REF! | #REF!
|  |  |  | 전송 | 정류기 | #REF! | #REF!
|  |  |  | 전송/인터넷 | 세종 7층 NOC(미확인 포함) | #REF! | #REF!
[5 empty] | 총 합 | #REF! | #REF!

## 세분화 (hidden)
차단기 사용 현황
7층 | Device Name | DE 분전반 신규명칭 | 분전반 명칭 | 차단전류 (A) | 메인차단용량 (kVA) | IT허용용량 (kVA) | 사용량 (kVA) | 사용율 (%) | 2P 20A |  |  | 2P 30A |  |  | 2P 50A |  |  | 4P 225A |  |  | 3P 100A |  |  | 3P 150A |  |  | 4P 50A
[9 empty] | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF
| 7-DaHall 1-RPP-01 | 7-1-A1 | UPS 출력 분전반 A1(From:7F 창고) | 400 | 263.2717 | 200 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | #REF! | #REF!
| 7-DaHall 1-PDU-01 | 7-1-A2 | U3-7A PANEL(From:TRroom-U7-5A) | 300 | 197.4538 | 150 | #REF! | #REF! |  |  |  | 2 | #REF! | #REF!
| 7-DaHall 1-RPP-03 | 7-1-A3 | UPS 출력 분전반 A2(From:7F 창고) | 225 | 148.0903 | 112.5 | #REF! | #REF! | [6 empty] | 2 | #REF! | #REF!
| 7-DaHall 1-PDU-03 | 7-1-A4 | UPS 출력 분전반 A(From:7F TR.Room) | 400 | 263.2717 | 200 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 7-DaHall 1-RPP-02 | 7-1-B1 | UPS 출력 분전반 B1(From:7F 창고) | 400 | 263.2717 | 200 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | #REF! | #REF!
| 7-DaHall 1-PDU-02 | 7-1-B2 | U3-7B PANEL(From:TRroom-U7-6B) | 300 | 197.4538 | 150 | #REF! | #REF! |  |  |  | 2 | #REF! | #REF!
| 7-DaHall 1-RPP-04 | 7-1-B3 | UPS 출력 분전반 B2(From:7F 창고) | 225 | 148.0903 | 112.5 | #REF! | #REF! | [6 empty] | 2 | #REF! | #REF!
| 7-DaHall 1-PDU-04 | 7-1-B4 | UPS 출력 분전반 B(From:7F TR.Room) | 400 | 263.2717 | 200 | #REF! | #REF! | [12 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
|  | 총계 | 총계 | 1400 | 921.451 | 700 | #REF! | #REF! | [18 empty] | 2 | #REF! | #REF!
6층 | Device Name | DE 분전반 신규명칭 | 분전반 명칭 | 차단전류 (A) | 메인차단용량 (kVA) | IT허용용량 (kVA) | 사용량 (kVA) | 사용율 (%) | 2P 30A
[9 empty] | 총계 | ON | OFF
| 6-DaHall 1-PDU-01 | 6-1-A1 | U-A1 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-03 | 6-1-A2 | U-A2 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-05 | 6-1-A3 | U6-A5 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-07 | 6-1-A4 | U6-A6 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-09 | 6-1-A5 | U-A3 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-11 | 6-1-A6 | U-A4 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-13 | 6-1-A7 | U6-A7 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-02 | 6-1-B1 | U-B1 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-04 | 6-1-B2 | U-B2 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-06 | 6-1-B3 | U6-B5 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-08 | 6-1-B4 | U6-B6 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-10 | 6-1-B5 | U-B3 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-12 | 6-1-B6 | U-B4 | 200 | 131.6359 | 41.1765 | #REF! | #REF! | 2 | #REF! | #REF!
| 6-DaHall 1-PDU-14 | 6-1-B7 | U6-B7 PANEL | 300 | 197.4538 | 61.7647 | #REF! | #REF! | 2 | #REF! | #REF!
|  | 총계 | 총계 | 3400 | 2237.8096 | 700 | #REF! | #REF!
5층 | Device Name | DE 분전반 신규명칭 | 분전반 명칭 | 차단전류 (A) | 메인차단용량 (kVA) | IT허용용량 (kVA) | 사용량 (kVA) | 사용율 (%) | 2P 30A |  |  | 2P 50A |  |  | 3P 60A |  |  | 3P 30A |  |  | 3P 20A |  |  | 3P 50A
[9 empty] | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF
| 5-DaHall 1-PDU-01 | 5-1-A1 | U5-1A | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF! |  |  |  | 2 | 1 | 1
| 5-DaHall 1-PDU-03 | 5-1-A2 | U5-2A | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF! |  |  |  | 2 | 1 | 1
| 5-DaHall 1-PDU-05 | 5-1-A3 | U5-3A | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-07 | 5-1-A4 | PDU(A)-9 | 200 | 131.6359 | 23.9316 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-09 | 5-1-A5 | PDU(A)-10 | 200 | 131.6359 | 23.9316 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-11 | 5-1-A6 | PDU(A)-1 | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-13 | 5-1-A7 | PDU(A)-2 | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-15 | 5-1-A8 | PDU(A)-3 | 300 | 197.4538 | 35.8974 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-17 | 5-1-A9 | Singtel PDU-8-A | 200 | 131.6359 | 23.9316 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-19 | 5-1-A10 | LG PDU(A1) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 3 | #REF! | #REF! | 5 | #REF! | #REF!
| 5-DaHall 1-PDU-21 | 5-1-A11 | LG PDU(A2) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 3 | #REF! | #REF! | 5 | #REF! | #REF!
| 5-DaHall 1-PDU-02 | 5-1-B1 | U5-1B | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF! |  |  |  | 2 | 1 | 1
| 5-DaHall 1-PDU-04 | 6-1-B2 | U5-2B | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF! |  |  |  | 2 | 1 | 1
| 5-DaHall 1-PDU-06 | 5-1-B3 | U5-3B | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-08 | 5-1-B4 | PDU(B)-9 | 200 | 131.6359 | 23.9316 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-10 | 5-1-B5 | PDU(B)-10 | 200 | 131.6359 | 23.9316 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-12 | 5-1-B6 | PDU(B)-1 | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-14 | 5-1-B7 | PDU(B)-2 | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-16 | 5-1-B8 | PDU(B)-3 | 300 | 197.4538 | 35.8974 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 1 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-18 | 5-1-B9 | Singtel PDU-8-B | 200 | 131.6359 | 23.9316 | #REF! | #REF! | 2 | #REF! | #REF!
| 5-DaHall 1-PDU-20 | 5-1-B10 | LG PDU(B1) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 3 | #REF! | #REF! | 5 | #REF! | #REF!
| 5-DaHall 1-PDU-22 | 5-1-B11 | LG PDU(B2) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | 3 | #REF! | #REF! | 5 | #REF! | #REF!
|  |  | PDU6B-1T | 150 | 98.7269 | 17.9487 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF!
|  |  | PDU(C) | 300 | 197.4538 | 35.8974 | #REF! | #REF! | [9 empty] | 2 | #REF! | #REF! | 2 | #REF! | #REF! | 2 | 0 | 2
|  | 총계 | 총계 | 5850 | 3850.3489 | 700 | #REF! | #REF!
4층 | Device Name | DE 분전반 신규명칭 | 분전반 명칭 | 차단전류 (A) | 메인차단용량 (kVA) | IT허용용량 (kVA) | 사용량 (kVA) | 사용율 (%) | 2P 100A |  |  | 4P 100A |  |  | 4P 200A
[9 empty] | 총계 | ON | OFF | 총계 | ON | OFF | 총계 | ON | OFF
| 4-DaHall 1-PDU-01 | 4-1-A1 | KEN 8 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | 1 | 0
| 4-DaHall 1-PDU-03 | 4-1-A2 | KEN 9 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | 0 | 1
| 4-DaHall 1-PDU-05 | 4-1-A3 | KEN 10 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-07 | 4-1-A4 | KEN 13 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-09 | 4-1-A5 | KEN 14 | 300 | 197.4538 | 70 | #REF! | #REF! | [6 empty] | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-02 | 4-1-B1 | KEN 1 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | 1 | 0
| 4-DaHall 1-PDU-04 | 4-1-B2 | KEN 2 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF! | 1 | 0 | 1
| 4-DaHall 1-PDU-06 | 4-1-B3 | KEN 3 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-08 | 4-1-B4 | KEN 6 | 300 | 197.4538 | 70 | #REF! | #REF! | 1 | #REF! | #REF!
| 4-DaHall 1-PDU-10 | 4-1-B5 | KEN 7 | 300 | 197.4538 | 70 | #REF! | #REF! | [6 empty] | 1 | #REF! | #REF!
|  | 총계 | 총계 | 3000 | 1974.5379 | 700 | #REF! | #REF!
|  |  | 각층 부하분담율 |  |  | 사용량(A) | 층 배분(%)
|  |  | 4층 | IDC | DEKR IDC | #REF! | #REF!
|  |  |  | IP | 세종 시스템 | #REF! | #REF!
|  |  |  | 공통 | 세종 시스템 | #REF! | #REF!
|  |  |  | IP | 세종 core room | #REF! | #REF!
[5 empty] | 총 합 | #REF! | #REF!
|  |  | 5층 | IDC | DEKR IDC | #REF!
|  |  | 6층 | IDC | DEKR IDC | #REF!
|  |  | 7층 | IDC | DEKR IDC | #REF! | #REF!
|  |  |  | IP | 세종 인터넷 | #REF! | #REF! | [5 empty] | 구 분 |  |  |  | 8월 |  |  | 9월 |  |  | 사용량 |  |  |  |  | 전류 |  | 점유율
|  |  |  | 전송 | 세종 전송설비 | #REF! | #REF! | [5 empty] | 8F 전체 전력지침 |  |  |  | 1701.4 |  |  | 3194 |  |  | 1492.6 |  |  |  |  | 9.119
|  |  |  | 전송 | 세종 정류기 | #REF! | #REF! | [5 empty] | DEK 사용량 | [9 empty] | 1163.9 |  |  |  |  | 7.1108 |  | 77.98%
|  |  |  | 전송/인터넷 | 세종 7층 NOC(미확인 포함) | #REF! | #REF! | [5 empty] | SJT 모니터 |  |  |  | 0.1 |  |  | 0.1 |  |  | 0 |  |  | 328.7 |  | 2.0082 |  | 22.02%
|  |  |  | 8F Office | SJT | #REF! | #REF! | [5 empty] | SJT Office |  |  |  | 193.2 |  |  | 320.4 |  |  | 127.2
[5 empty] | DEKR IDC | #REF! | #REF! | [5 empty] | SJT Server |  |  |  | 364.1 |  |  | 565.6 |  |  | 201.5
[5 empty] | 총 합 | #REF! | #REF!
#REF!
#REF!
#REF!

## SJT설비_7층_IPD (hidden)
IPD 운용현황(' 22 년 월 일)
|  | 201 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/A-1
| 번호 | BAY_부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | BAY_부하명 | 번호
| 1 | 203A | O | X |  |  |  |  | O | X | NTT RACK 1 | 41
| 2 | DTX-360(A) | O | X |  |  |  |  | O | X | NTT RACK 2 | 42
| 3 |  | X | X |  |  |  | 35A | O | O | IPD / A-1_P43 406BAY PDP_A /405bay표기 | 43
| 4 | Clarent 1 | O | X |  |  |  | 35A | O | O | IPD / A-1_P44 407BAY PDP_A /406bay표기 | 44
| 5 | LG 교환기 | O | X |  |  |  |  | O | X | C-A | 45
| 6 | DTX240 #1 (503BAY / A) | O | X |  |  |  |  | O | X | 언리미텔 | 46 | 2021.01.19 탈거
| 7 | IPD / A-1_P07 306BAY PDP-A | O | O | 100A |  |  |  | O | X | EXL 1-B | 47
| 8 |  | X | X |  |  |  |  | O | X | EXL 2-B | 48
| 9 |  | X | X |  |  |  |  | O | X | EXL 3-A | 49
| 10 | 502BAY A, DTX-6000 | O | X |  |  |  | 35A | O | O | IPD / A-1_P50 G-7 랙 PDP_A / NTT-4A표기 | 50 | 미사용, 전원OFF 상태
| 11 | IPD / A-1_P11 506BAY PDP-A | O | O | 35A |  |  | 35A | O | O | IPD / A-1_P51 F-1 랙 PDP_A | 51
| 12 | 204A 교환기 | O | X |  |  |  |  | O | X | F-2랙 (201A-NTT#9-PDU상) | 52 | 2021.01.19 탈거
| 13 |  | X | X |  |  |  |  | X | X |  | 53
| 14 |  | X | X |  |  |  |  | X | X |  | 54
| 15 | IPD / A-1_P15 506BAY PDP_A(2) /509B 3PDA표기 | O | O | 35A |  |  |  | X | X |  | 55
| 16 | IPD / A-1_P16 504BAY PDP_B | O | O | 35A |  |  | 50A | O | O | IPD / A-1_P56 502BAY PDP_A | 56
| 17 | IPD / A-1_P17 503BAY PDP_A | O | O | 50A |  |  | 50A | O | O | IPD / A-1_P57 305BAY PDP_A | 57
| 18 | IPD / A-1_P18 303BAY PDP_A | O | O | 100A |  |  |  | X | X |  | 58
| 19 | IPD / A-1_P19 501BAY PDP_A | O | O | 100A |  |  |  | X | X |  | 59
| 20 | IPD / A-1_P20 507BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 60
| 21 | IPD / A-1_P21 304BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 61
| 22 |  | X | X |  |  |  |  | X | X |  | 62
| 23 | 302Bay, SKB-A ('21.09.13) | O | O | 100A |  |  |  | X | X |  | 63
| 24 | 307BAY_LGU+PDP.A 201BAY_PDR_P24 | O | O | 100A |  |  |  | X | X |  | 64
| 25 |  | X | X |  |  |  |  | X | X |  | 65
| 26 |  | X | X |  |  |  |  | X | X |  | 66
| 27 |  | X | X |  |  |  |  | X | X |  | 67
| 28 |  | X | X |  |  |  |  | X | X |  | 68
| 29 |  | X | X |  |  |  |  | X | X |  | 69
| 30 |  | X | X |  |  |  |  | X | X |  | 70
| 31 |  | X | X |  |  |  |  | X | X |  | 71
| 32 |  | X | X |  |  |  |  | X | X |  | 72
| 33 |  | X | X |  |  |  |  | X | X |  | 73
| 34 |  | X | X |  |  |  |  | X | X |  | 74
| 35 |  | X | X |  |  |  |  | X | X |  | 75
| 36 |  | X | X |  |  |  |  | X | X |  | 76
| 37 |  | X | X |  |  |  |  | X | X |  | 77
| 38 |  | X | X |  |  |  |  | X | X |  | 78
| 39 |  | X | X |  |  |  |  | X | X |  | 79
| 40 |  | X | X |  |  |  |  | X | X |  | 80
[7 empty] | 합계: | 0
|  | 401 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/B-1
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
| 1 |  | X | X |  |  |  | 100A | O | O | IPD / B-1_P41 C-1 랙 장비_B | 41
| 2 | DTX-360(B) | O | X |  |  |  |  | X | X |  | 42
| 3 |  | X | X |  |  |  |  | O | X | C-B | 43
| 4 | Crlarent 1 | O | X |  |  |  |  | O | X | EXL 1-A | 44
| 5 | IPD / B-1_P05 406BAY PDP_B /403bay dcn-1b표기 | O | O | 35A |  |  |  | O | X | EXL 2-A | 45
| 6 | IPD / B-1_P06 407BAY PDP_B / 406bay dcn-2b표기 | O | O | 35A |  |  |  | O | X | EXL 3-B | 46
| 7 | IPD / B-1_P07 306BAY PDP_B | O | O | 100A |  |  | 50A | O | O | IPD / B-1_P47 G-7 랙 PDP_B | 47 | 미사용, 전원OFF
| 8 | 503 BAY/B DTX-240#2 | O | X |  |  |  |  | X | X |  | 48
| 9 | N-DCS#1 | O | X |  |  |  |  | X | X |  | 49
| 10 | N-DCS#2 | O | X |  |  |  |  | X | X |  | 50
| 11 | N-DCS#3 | O | X |  |  |  | 35A | O | O | IPD / B-1_P51 F-1 랙 PDP_B | 51
| 12 | 502BAY B DTX-6000 | O | X |  |  |  |  | X | X | F-2랙 (401B-NTT#9-PDU하) | 52 | 2021.01.19 탈거
랙 철거 예정 | 13 | IPD / B-1_P13 505BAY PDP_A(단일) | O | X |  |  |  |  | X | X | 401B-NTT#1-PDU하 | 53
| 14 | IPD / B-1_P14 506BAY PDP_B | O | O | 35A |  |  |  | X | X | 401B-NTT#1-PDU상 | 54
| 15 | IPD / B-1_P15 506BAY PDP_B(2) /509b 3pdp b표기 | O | O | 35A |  |  |  | X | X | NTT-2B(20.6.16철거) | 55
| 16 | IPD / B-1_P16 504BAY PDP_A | O | O | 35A |  |  | 50A | O | O | IPD / B-1_P56 502BAY PDP_B | 56
| 17 | IPD / B-1_P17 503BAY PDP_B | O | O | 50A |  |  | 50A | O | O | IPD / B-1_P57 305BAY PDP_B | 57
| 18 | IPD / B-1_P18 303BAY PDP_B | O | O | 100A |  |  |  | X | X |  | 58
| 19 | IPD / B-1_P19 501BAY PDP_B | O | O | 100A |  |  |  | X | X |  | 59
| 20 | IPD / B-1_P20 507BAY PDP_B | O | O | 50A |  |  |  | X | X |  | 60
| 21 | IPD / B-1_P21 304BAY PDP_B | O | O | 50A |  |  |  | X | X |  | 61
| 22 |  | X | X | X |  |  |  | X | X |  | 62
| 23 | 302Bay, SKB-B ('21.09.13) | O | O | 100A |  |  |  | X | X |  | 63
| 24 | 307BAY_LGU+PDP.B 401BAY_PDR_P24 | O | O | 100A |  |  |  | X | X |  | 64
| 25 |  | X | X |  |  |  |  | X | X |  | 65
| 26 |  | X | X |  |  |  |  | X | X |  | 66
| 27 |  | X | X |  |  |  |  | X | X |  | 67
| 28 |  | X | X |  |  |  |  | X | X |  | 68
| 29 |  | X | X |  |  |  |  | X | X |  | 69
| 30 |  | X | X |  |  |  |  | X | X |  | 70
| 31 |  | X | X |  |  |  |  | X | X |  | 71
| 32 |  | X | X |  |  |  |  | X | X |  | 72
| 33 |  | X | X |  |  |  |  | X | X |  | 73
| 34 |  | X | X |  |  |  |  | X | X |  | 74
| 35 |  | X | X |  |  |  |  | X | X |  | 75
| 36 |  | X | X |  |  |  |  | X | X |  | 76
| 37 |  | X | X |  |  |  |  | X | X |  | 77
| 38 |  | X | X |  |  |  |  | X | X |  | 78
| 39 |  | X | X |  |  |  |  | X | X |  | 79
| 40 |  | X | X |  |  |  |  | X | X |  | 80
[7 empty] | 합계: | 0
|  | 211 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/A-2
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
| 1 |  | X | X |  |  |  |  | X | X |  | 41
20210204 FUSE 제거 | 2 | 311BAY FLC-P_A | X | X |  |  |  |  | X | X |  | 42 | 20210120 Fuse 제거
| 3 | 413BAY PDP_1A | X | X |  |  |  |  | X | X |  | 43
| 4 | 413BAY PDP_2A | X | X |  |  |  | 16A | O | O | IPD / A-2_P44 518BAY PDP_A | 44
| 5 | 511BAY(KT SMOT4_A) | X | X |  |  |  |  | X | X |  | 45
20210204 FUSE 제거 | 6 | 312BAY FLC-P_A | X | X |  |  |  |  | X | X |  | 46
| 7 | IPD / A-2_P07 513BAY PDP_A | O | O | 50A |  |  | 35A | O | O | IPD / A-2_P47 519BAY PDP_A | 47
20210204 FUSE 제거 | 8 |  | X | X |  |  |  | 50A | O | O | IPD / A-2_P48 520BAY 장비_A | 48
20210204 FUSE 제거 | 9 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P49 418BAY PDP_A | 49
| 10 | IPD / A-2_P10 414BAY PDP_A | O | O | 35A |  |  |  | X | X |  | 50
20210204 FUSE 제거 | 11 |  | X | X |  |  |  |  | X | X |  | 51 | 20201028 랙 철거
| 12 | IPD / A-2_P12 212BAY PDP_A | O | O | 50A |  |  | 35A | O | O | IPD / A-2_P52 419BAY PDP_A | 52
| 13 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P53 519BAY PDP_A(2) / CWDM-A표기 | 53
20210204 FUSE 제거 | 14 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P54 112BAY PDP_A | 54
20210224 FUSE 제거 | 15 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P55 113BAY PDP_A | 55
| 16 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P56 114BAY PDP_A | 56
| 17 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P57 111BAY PDP_A | 57
| 18 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P58 517BAY PDP_A | 58
20210204 FUSE 제거 | 19 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P59 115BAY PDP_A | 59
20210204 FUSE 제거 | 20 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P60 117BAY PDP_A | 60
20210224 FUSE 제거 | 21 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P61 116BAY PDP_A | 61
| 22 | IPD / A-2_P22 219BAY PDP_A | O | O | 50A |  |  | 35A | O | O | IPD / A-2_P62 511BAY PDP_A | 62
| 23 | IPD / A-2_P23 514BAY PDP_ A | O | O | 50A |  |  | 35A | O | O | IPD / A-2_P63 511BAY 장비_A | 63
| 24 |  | X | X |  |  |  | 50A | O | O | IPD / A-2_P64 118BAY PDP_A | 64
| 25 |  | X | X |  |  |  | 35A | O | O | IPD / A-2_P65 119BAY PDP_A | 65
| 26 |  | X | X |  |  |  | 50A | O | O | IPD / A-2_P66 121BAY PDP_A | 66
| 27 |  | X | X |  |  |  | 50A | O | O | IPD / A-2_P67 120BAY PDP_A | 67
| 28 |  | X | X |  |  |  |  | X | X |  | 68
| 29 |  | X | X |  |  |  |  | X | X |  | 69
| 30 |  | X | X |  |  |  |  | X | X |  | 70
| 31 |  | X | X |  |  |  |  | X | X |  | 71
| 32 |  | X | X |  |  |  |  | X | X |  | 72
| 33 |  | X | X |  |  |  |  | X | X |  | 73
| 34 |  | X | X |  |  |  |  | X | X |  | 74
| 35 |  | X | X |  |  |  |  | X | X |  | 75
| 36 |  | X | X |  |  |  |  | X | X |  | 76
| 37 |  | X | X |  |  |  |  | X | X |  | 77
| 38 |  | X | X |  |  |  |  | X | X |  | 78
| 39 |  | X | X |  |  |  |  | X | X |  | 79
| 40 |  | X | X |  |  |  |  | X | X |  | 80
[7 empty] | 합계: | 0
|  | 411 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/B-2
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
20210204 FUSE 제거 | 1 |  | X | X |  |  |  |  | X | X |  | 41
| 2 |  | X | X |  |  |  |  | X | X |  | 42 | 20210120 FUSE 제거
| 3 |  | X | X |  |  |  |  | X | X |  | 43
| 4 |  | X | X |  |  |  |  | X | X |  | 44
20210204 FUSE 제거 | 5 |  | X | X |  |  |  |  | X | X |  | 45
| 6 |  | X | X |  |  |  | 16A | O | O | IPD / B-2_P46 518BAY PDP_B | 46
| 7 | IPD / B-2_P07 513BAY PDP_B | O | O | 50A |  |  | 35A | O | O | IPD / B-2_P47 519BAY PDP_B | 47
20210204 FUSE 제거 | 8 |  | X | X |  |  |  | 50A | O | O | IPD / B-2_P48 520BAY 장비_B | 48
20210204 FUSE 제거 | 9 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P49 418BAY PDP_B | 49
| 10 | IPD / B-2_P10 414BAY PDP_B | O | O | 35A |  |  |  | X | X |  | 50
20210204 FUSE 제거 | 11 |  | X | X |  |  |  |  | X | X |  | 51 | 랙철거 20201028
| 12 | IPD / B-2_P12 212BAY PDP_B | O | O | 50A |  |  | 35A | O | O | IPD / B-2_P52 419BAY PDP_B | 52
| 13 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P53 519BAY PDP_B(2) / CWDM-B표기 | 53
20210204 FUSE 제거 | 14 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P54 112BAY PDP_B | 54
20210224 FUSE 제거 | 15 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P55 113BAY PDP_B | 55
| 16 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P56 114BAY PDP_B | 56
| 17 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P57 111BAY PDP_B | 57
| 18 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P58 517BAY PDP_B | 58
20210204 FUSE 제거 | 19 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P59 115BAY PDP_B | 59
20210204 FUSE 제거 | 20 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P60 117BAY PDP_B | 60
20210224 FUSE 제거 | 21 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P61 116BAY PDP_B | 61
| 22 | IPD / B-2_P22 219BAY PDP_B | O | O | 50A |  |  | 35A | O | O | IPD / B-2_P62 511BAY PDP_B | 62
| 23 | IPD / B-2_P23 514BAY PDP_B | O | O | 50A |  |  | 35A | O | O | IPD / B-2_P63 511BAY 장비_B | 63
| 24 |  | X | X |  |  |  | 50A | O | O | IPD / B-2_P64 118BAY PDP_B | 64
| 25 |  | X | X |  |  |  | 35A | O | O | IPD / B-2_P65 119BAY PDP_B | 65
| 26 |  | X | X |  |  |  | 50A | O | O | IPD / B-2_P66 121BAY PDP_B | 66
| 27 |  | X | X |  |  |  | 50A | O | O | IPD / B-2_P67 120BAY PDP_B | 67
| 28 |  | X | X |  |  |  |  | X | X |  | 68
| 29 |  | X | X |  |  |  |  | X | X |  | 69
| 30 |  | X | X |  |  |  |  | X | X |  | 70
| 31 |  | X | X |  |  |  |  | X | X |  | 71
| 32 |  | X | X |  |  |  |  | X | X |  | 72
| 33 |  | X | X |  |  |  |  | X | X |  | 73
| 34 |  | X | X |  |  |  |  | X | X |  | 74
| 35 |  | X | X |  |  |  |  | X | X |  | 75
| 36 |  | X | X |  |  |  |  | X | X |  | 76
| 37 |  | X | X |  |  |  |  | X | X |  | 77
| 38 |  | X | X |  |  |  |  | X | X |  | 78
| 39 |  | X | X |  |  |  |  | X | X |  | 79
| 40 |  | X | X |  |  |  |  | X | X |  | 80
[7 empty] | 합계: | 0
|  | 222 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/A-3
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
| 1 | IPD / A-3_P01 426BAY PDP_A-1 | O | O | 100A |  |  | 50A | O | O | IPD / A-3_P41 527BAY PDP_A | 41
| 2 | IPD / A-3_P02 426BAY PDP_A-2 | O | O | 100A |  |  | 50A | O | O | IPD / A-3_P42 425BAY PDP_A-1 | 42
| 3 | IPD / A-3_P03 426BAY PDP_A-3 | O | O | 50A |  |  | 50A | O | O | IPD / A-3_P43 425BAY PDP_A-2 | 43
| 4 | 427BAY-A | O | X |  |  |  | 50A | O | O | IPD / A-3_P44 530BAY PDP_A | 44
| 5 | IPD / A-3_P05 523BAY PDP_A | O | O | 50A |  |  |  | O | X | LT 2.5G 531BAY A | 45
| 6 | IPD / A-3_P06 524BAY PDP_A | O | O | 50A |  |  | 50A | O | O | IPD / A-3_P46 531BAY PDP_A | 46
| 7 | IPD / A-3_P07 525BAY PDP_A | O | O | 50A |  |  | 50A | O | O | IPD / A-3_P47 532BAY PDP_A | 47
| 8 | 428BAY-A | O | X |  |  |  |  | O | X | LT 2.5G 534BAY A | 48
| 9 | 429BAY-A | O | X |  |  |  | 50A | O | O | IPD / A-3_P49 228BAY PDP_A | 49
| 10 | IPD / A-3_P10 526BAY PDP_A | O | O | 50A |  |  | 35A | O | O | IPD / A-3_P50 229BAY PDP_A | 50
| 11 | 430BAY-A | O | X |  |  |  | 35A | O | O | IPD / A-3_P51 230BAY PDP_A | 51
| 12 | 431BAY-A | O | X |  |  |  | 35A | O | O | IPD / A-3_P52 225BAY PDP_A | 52
| 13 | 331BAY-A | O | X |  |  |  | 35A | O | O | IPD / A-3_P53 420BAY PDP_A | 53
| 14 | 330BAY-A | O | X |  |  |  |  | X | X |  | 54
| 15 | IPD / A-3_P15 329BAY PDP_A | O | O | 50A |  |  | 35A | O | O | IPD / A-3_P55 225BAY PDP_A(2) | 55
| 16 | IPD / A-3_P16 328BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 56
| 17 | IPD / A-3_P17 327BAY PDP_A | O | O | 50A |  |  | 50A | O | O | IPD / A-3_P57 427BAY PDP_A-1 | 57
| 18 | IPD / A-3_P18 223BAY PDP_A | O | O | 35A |  |  | 50A | O | O | IPD / A-3_P58 427BAY PDP_A-2 | 58
| 19 | IPD / A-3_P19 224BAY PDP_A | O | O | 35A |  |  | 100A | O | O | IPD / A-3_P59 305BAY PDP_A | 59
| 20 | IPD / A-3_P20 226BAY PDP_A | O | O | 35A |  |  | 100A | O | O | 331BAY_코위버ROADM(A) 222BAY_P60 | 60
| 21 | IPD / A-3_P21 227BAY PDP_A | O | O | 50A |  |  | 100A | O | O | 323B ODO -48VA 코위버 갬으 DURTKA#2 | 61
| 22 | IPD / A-3_P22 231BAY PDP_A | O | O | 35A |  |  |  | X | X |  | 62
| 23 | IPD / A-3_P23 326BAY PDP_A | O | O | 35A |  |  |  | X | X |  | 63
| 24 |  | X | X |  |  |  |  | X | X |  | 64
| 25 | IPD / A-3_P25 319BAY PDP_A | O | O | 35A |  |  |  | X | X |  | 65
| 26 | IPD / A-3_P26 423BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 66
| 27 | IPD / A-3_P27 424BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 67
| 28 | 330BAY_코위버ROADM(A) 222BAY_P28 | O | O | 100A |  |  |  | X | X |  | 68
| 29 |  | X | X |  |  |  |  | X | X |  | 69
| 30 |  | X | X |  |  |  |  | X | X |  | 70
| 31 |  | X | X |  |  |  |  | X | X |  | 71
| 32 |  | X | X |  |  |  |  | X | X |  | 72
| 33 |  | X | X |  |  |  |  | X | X |  | 73
| 34 |  | X | X |  |  |  |  | X | X |  | 74
| 35 |  | X | X |  |  |  |  | X | X |  | 75
| 36 |  | X | X |  |  |  |  | X | X |  | 76
| 37 |  | X | X |  |  |  |  | X | X |  | 77
| 38 |  | X | X |  |  |  |  | X | X |  | 78
| 39 |  | X | X |  |  |  |  | X | X |  | 79
| 40 |  | X | X |  |  |  |  | X | X |  | 80
[7 empty] | 합계: | 0
|  | 422 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/B-3
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
| 1 | IPD / B-3_P01 426BAY PDP_B-1 | O | O | 100A |  |  | 50A | O | O | IPD / B-3_P41 527BAY PDP_B | 41
| 2 | IPD / B-3_P02 426BAY PDP_B-2 | O | O | 100A |  |  | 50A | O | O | IPD / B-3_P42 425BAY PDP_B-1 | 42
| 3 | IPD / B-3_P03 426BAY PDP_B-3 | O | O | 50A |  |  | 50A | O | O | IPD / B-3_P43 425BAY PDP_B-2 | 43
| 4 | 427 BAY-B NT2.5G 3B 3BAY | O | X |  |  |  | 50A | O | O | IPD / B-3_P44 530BAY PDP_B | 44
| 5 | IPD / B-3_P05 523BAY PDP_B | O | O | 50A |  |  |  | O | X | LT 2.5G 531BAY B | 45
| 6 | IPD / B-3_P06 524BAY PDP_B | O | O | 50A |  |  | 50A | O | O | IPD / B-3_P46 531BAY PDP_B | 46
| 7 | IPD / B-3_P07 525BAY PDP_B | O | O | 50A |  |  | 50A | O | O | IPD / B-3_P47 532BAY PDP_B | 47
| 8 | 428BAY-B NT2.5 4 BAY B | O | X |  |  |  |  | O | X | LT 2.5G 534BAY B | 48
| 9 | 429BAY-B NT2.5 5 BAY B | O | X |  |  |  | 35A | O | O | IPD / B-3_P49 228BAY PDP_B | 49
| 10 | IPD / B-3_P10 526BAY PDP_B | O | O | 50A |  |  | 35A | O | O | IPD / B-3_P50 229BAY PDP_B | 50
| 11 | 430BAY-B 525BAY B | O | X |  |  |  | 35A | O | O | IPD / B-3_P51 230BAY PDP_B | 51
| 12 | 431BAY-B NT2.5G B 430 BAY | O | X |  |  |  | 35A | O | O | IPD / B-3_P52 420BAY PDP_B | 52
| 13 | 331 BAY-B NT2.5G 330BAY B | O | X |  |  |  |  | X | X |  | 53
| 14 | 330 BAY NT2.5G 329BAY B | O | X |  |  |  | 35A | O | O | IPD / B-3_P54 225BAY PDP_B(2) | 54
| 15 | IPD / B-3_P15 329BAY PDP_B | O | O | 50A |  |  |  | X | X |  | 55
| 16 | IPD / B-3_P16 328BAYPDP_B | O | O | 50A |  |  |  | X | X |  | 56
| 17 | IPD / B-3_P17 327BAY PDP_B | O | O | 50A |  |  | 50A | O | O | IPD / B-3_P57 427BAY PDP_B-1 | 57
| 18 | IPD / B-3_P18 223BAY PDP_B | O | O | 50A |  |  | 50A | O | O | IPD / B-3_P58 427BAY PDP_B-2 | 58
| 19 | IPD / B-3_P19 224BAY PDP_B | O | O | 50A |  |  | 100A | O | O | IPD / B-3_P59 305BAY PDP_B | 59
| 20 | IPD / B-3_P20 226BAY PDP_B | O | O | 50A |  |  | 100A | O | O | 331BAY_코위버ROADM(B) 422BAY_P60 | 60
| 21 | IPD / B-3_P21 227BAY PDP_B | O | O | 50A |  |  | 100A | O | O | 323B ODO -48VB 코위버 갬으 DURTKA#2 | 61
| 22 | IPD / B-3_P22 231BAY PDP_B | O | O | 35A |  |  |  | X | X |  | 62
| 23 | IPD / B-3_P23 225BAY PDP_B | O | O | 35A |  |  |  | X | X |  | 63
| 24 | IPD / B-3_P24 326BAY PDP_B | O | O | 35A |  |  |  | X | X |  | 64
| 25 | IPD / B-3_P25 319BAY PDP_B | O | O | 35A |  |  |  | X | X |  | 65
| 26 | IPD / B-3_P26 423BAY PDP_B | O | O | 50A |  |  |  | X | X |  | 66
| 27 | IPD / B-3_P27 424BAY PDP_B | O | O | 50A |  |  |  | X | X |  | 67
| 28 | 330BAY_코위버ROADM(B) 422BAY_P28 | O | O | 100A |  |  |  | X | X |  | 68
| 29 |  | X | X |  |  |  |  | X | X |  | 69
| 30 |  | X | X |  |  |  |  | X | X |  | 70
| 31 |  | X | X |  |  |  |  | X | X |  | 71
| 32 |  | X | X |  |  |  |  | X | X |  | 72
| 33 |  | X | X |  |  |  |  | X | X |  | 73
| 34 |  | X | X |  |  |  |  | X | X |  | 74
| 35 |  | X | X |  |  |  |  | X | X |  | 75
| 36 |  | X | X |  |  |  |  | X | X |  | 76
| 37 |  | X | X |  |  |  |  | X | X |  | 77
| 38 |  | X | X |  |  |  |  | X | X |  | 78
| 39 |  | X | X |  |  |  |  | X | X |  | 79
| 40 |  | X | X |  |  |  |  | X | X |  | 80
[7 empty] | 합계: | 0
|  | 235 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/A-4
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
| 1 |  | X | X |  |  |  | 50 | O | O | IPD / A-4_P41 343BAY PDP_A / 에르고DWDM-1A | 41 | 미사용
| 2 |  | X | X |  |  |  | 35 | O | O | IPD / A-4_P42 339BAY PDP_B | 42
| 3 | IPD / A-4_P03 436BAY PDP_A | O | O | 100A |  |  | 35 | O | O | IPD / A-4_P43 338BAY PDP_A | 43
| 4 |  | X | X |  |  |  | 35 | O | O | IPD / A-4_P44 337AY PDP_A | 44
| 5 |  | X | X |  |  |  | 50 | O | O | IPD / A-4_P45 238AY PDP_A | 45
| 6 |  | X | X |  |  |  | 50 | O | O | IPD / A-4_P46 335AY PDP_A | 46
| 7 |  | X | X |  |  |  |  | X | X |  | 47
| 8 |  | X | X |  |  |  |  | X | X |  | 48
| 9 |  | X | X |  |  |  |  | X | X |  | 49
| 10 | IPD / A-4_P10 239BAY PDP_A-1 | O | O | 50A |  |  | 35 | O | O | IPD / A-4_P50 336AY PDP_A | 50
| 11 | IPD / A-4_P11 239BAY PDP_A-2 | O | O | 50A |  |  |  | X | X |  | 51
| 12 |  | X | X |  |  |  | 35 | O | O | IPD / A-4_P52 237AY PDP_A | 52
| 13 |  | X | X |  |  |  | 35 | O | O | IPD / A-4_P53 236AY PDP_A | 53
| 14 |  | X | X |  |  |  | 35 | O | O | IPD / A-4_P54 334AY PDP_A | 54
| 15 |  | X | X |  |  |  |  | X | X |  | 55
| 16 |  | X | X |  |  |  | 100 | O | O | IPD / A-4_P56 537BAY PDP_A | 56
| 17 |  | X | X |  |  |  |  | X | X |  | 57
| 18 | IPD / A-4_P18 239BAY PDP_A-3 | O | O | 50A |  |  | 100 | O | O | IPD / A-4_P58 538BAY PDP_A | 58
| 19 |  | X | X |  |  |  | 50 | O | O | IPD / A-4_P59 536BAY PDP_A | 59
| 20 |  | X | X |  |  |  |  | X | X |  | 60
| 21 |  | X | X |  |  |  |  | X | X |  | 61
| 22 |  | X | X |  |  |  |  | X | X |  | 62
| 23 |  | X | X |  |  |  |  | X | X |  | 63
| 24 |  | X | X |  |  |  |  | X | X |  | 64
| 25 | IPD / A-4_P25 235Bay-노키아1830_PSS8-A전원 | O | O | 50A |  |  |  | X | X |  | 65
| 26 | IPD / A-4_P26 244BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 66
| 27 | IPD / A-4_P27 240BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 67
| 28 | IPD / A-4_P28 243BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 68
| 29 | IPD / A-4_P29 437BAY PDP_A | O | O | 100A |  |  |  | X | X |  | 69
| 30 | IPD / A-4_P30 439BAY PDP_B | O | O | 100A |  |  |  | X | X |  | 70
| 31 | IPD / A-4_P31 440BAY PDP_B | O | O | 100A |  |  |  | X | X |  | 71
FUSE 제거(21.02.03) | 32 | IPD / A-4_P32 TEST BED PDP_A | O | O | 35A |  |  |  | X | X |  | 72
| 33 | IPD / A-4_P33 240BAY PDP_A | O | O | 50A |  |  |  | X | X |  | 73
| 34 | IPD/A-4_P34 437BAY(下) PDP_A-2 | O | O | 35A |  |  |  | X | X |  | 74
| 35 |  | X | X |  |  |  |  | X | X |  | 75
| 36 |  | X | X |  |  |  |  | X | X |  | 76
| 37 |  | X | X |  |  |  |  | X | X |  | 77
| 38 |  | X | X |  |  |  |  | X | X |  | 78
| 39 |  | X | X |  |  |  |  | X | X |  | 79
| 40 |  | X | X |  |  |  |  | X | X |  | 80
[7 empty] | 합계: | 0
|  | 435 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/B-4
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
| 1 |  | X | X |  |  |  | 50A | O | O | IPD / B-4_P41 343BAY PDP_B / 에르고 DWDM 1B표기 | 41 | 미사용
| 2 |  | X | X |  |  |  |  | X | X |  | 42
| 3 | IPD / B-4_P03 436BAY PDP_B | O | O | 100A |  |  | 50A | O | O | IPD / B-4_P43 239BAY PDP_B-1 | 43
| 4 |  | X | X |  |  |  | 50A | O | O | IPD / B-4_P44 239BAY PDP_B-2 | 44
| 5 |  | X | X |  |  |  | 50A | O | O | IPD / B-4_P45 239BAY PDP_B-3 | 45
| 6 |  | X | X |  |  |  | 35A | O | O | IPD / B-4_P46 339BAY PDP_A | 46
| 7 |  | X | X |  |  |  | 50A | O | O | IPD / B-4_P47 338BAY PDP_B | 47
| 8 |  | X | X |  |  |  | 35A | O | O | IPD / B-4_P48 337AY PDP_B | 48
| 9 |  | X | X |  |  |  | 50A | O | O | IPD / B-4_P49 335AY PDP_B | 49
| 10 |  | X | X |  |  |  | 35A | O | O | IPD / B-4_P50 336AY PDP_B | 50
| 11 |  | X | X |  |  |  | 50A | O | O | IPD / B-4_P51 238BAY PDP_B | 51
| 12 |  | X | X |  |  |  | 35A | O | O | IPD / B-4_P52 237AY PDP_B | 52
| 13 |  | X | X |  |  |  | 35A | O | O | IPD / B-4_P53 236AY PDP_B | 53
| 14 |  | X | X |  |  |  | 35A | O | O | IPD / B-4_P54 334AY PDP_B | 54
| 15 |  | X | X |  |  |  |  | X | X |  | 55
| 16 |  | X | X |  |  |  | 35A | O | O | IPD / B-4_P56 537BAY PDP_B | 56
| 17 |  | X | X |  |  |  | 50A | O | O | IPD / B-4_P57 240BAY PDP_B | 57
| 18 |  | X | X |  |  |  | 100A | O | O | IPD / B-4_P58 538BAY PDP_B | 58
| 19 |  | X | X |  |  |  | 50A | O | O | IPD / B-4_P59 536BAY PDP_B | 59
| 20 |  | X | X |  |  |  |  | X | X |  | 60
| 21 |  | X | X |  |  |  |  | X | X |  | 61
| 22 |  | X | X |  |  |  |  | X | X |  | 62
| 23 |  | X | X |  |  |  |  | X | X |  | 63
| 24 |  | X | X |  |  |  |  | X | X |  | 64
| 25 | 235Bay, 노키아1830_PSS8-B전원('21.09.14 투입) | O | O | 50A |  |  |  | X | X |  | 65
| 26 | IPD / B-4_P26 244BAY PDP_B | O | O | 50A |  |  |  | X | X |  | 66
| 27 |  | X | X |  |  |  |  | X | X |  | 67
| 28 | IPD / B-4_P28 243BAY PDP_B | O | O | 50A |  |  |  | X | X |  | 68
| 29 | IPD / B-4_P29 437BAY PDP_B | O | O | 100A |  |  |  | X | X |  | 69
| 30 | IPD / B-4_P30 439BAY PDP_A | O | O | 100A |  |  |  | X | X |  | 70
| 31 | IPD / B-4_P31 440BAY PDP_A | O | O | 100A |  |  |  | X | X |  | 71
FUSE 제거(21.02.03) | 32 | IPD / B-4_P32 TEST BED PDP_B | O | O | 35A |  |  |  | X | X |  | 72
| 33 | IPD / B-4_P33 240BAY PDP_B | O | O | 50A |  |  |  | X | X |  | 73
| 34 | IPD/B-4_P34 437BAY(下) PDP_B-2 | ○ | ○ | 35A |  |  |  | X | X |  | 74
| 35 |  | X | X |  |  |  |  | X | X |  | 75
| 36 |  | X | X |  |  |  |  | X | X |  | 76
| 37 |  | X | X |  |  |  |  | X | X |  | 77
| 38 |  | X | X |  |  |  |  | X | X |  | 78
| 39 |  | X | X |  |  |  |  | X | X |  | 79
| 40 |  | X | X |  |  |  |  | X | X |  | 80
[7 empty] | 합계: | 0
|  | A-A1 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/A-5 (구 IPD-B)
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
| F1 |  | X | X | X |  |  | 35A | X | X |  | F61
| F2 |  | X | X | X |  |  | 35A | X | X |  | F62
| F3 |  | X | X | X |  |  | 35A | X | X |  | F63
| F4 |  | X | X | X |  |  | 35A | X | X |  | F64
| F5 |  | X | X | X |  |  | 35A | X | X |  | F65
| F6 |  | X | X | X |  |  | 35A | X | X |  | F66
| F7 |  | X | X | X |  |  | 35A | X | X |  | F67
| F8 |  | X | X | X |  |  | 35A | X | X |  | F68
| F9 |  | X | X | X |  |  | 35A | X | X |  | F69
| F10 |  | X | X | X |  |  | 35A | X | X |  | F70
| F11 |  | X | X | X |  |  | 35A | X | X |  | F71
| F12 |  | X | X | X |  |  | 35A | X | X |  | F72
| F13 |  | X | X | X |  |  | 35A | X | X |  | F73
| F14 |  | X | X | X |  |  | 35A | X | X |  | F74
| F15 |  | X | X | X |  |  | 35A | X | X |  | F75
| F16 |  | X | X | X |  |  | 35A | X | X |  | F76
| F17 |  | X | X | X |  |  | 35A | X | X |  | F77
| F18 |  | X | X | X |  |  | 35A | X | X |  | F78
| F19 |  | X | X | X |  |  | 35A | X | X |  | F79
| F20 |  | X | X | X |  |  | 35A | X | X |  | F80
| F21 |  | X | X | X |  |  | X | X | X |  | F81
| F22 |  | X | X | X |  |  | X | X | X |  | F82
| F23 |  | X | X | X |  |  | X | X | X |  | F83
| F24 |  | X | X | X |  |  | X | X | X |  | F84
| F25 |  | X | X | X |  |  | X | X | X |  | F85
| F26 |  | X | X | X |  |  | X | X | X |  | F86
| F27 |  | X | X | X |  |  | X | X | X |  | F87
| F28 |  | X | X | X |  |  | 35A | X | X |  | F88
| F29 |  | X | X | X |  |  | 35A | X | X |  | F89
| F30 |  | X | X | X |  |  | 35A | X | X |  | F90
| F31 |  | X | X | X |  |  | 35A | X | X |  | F91
| F32 |  | X | X | X |  |  | 35A | X | X |  | F92
| F33 |  | X | X | X |  |  | 35A | X | X |  | F93
| F34 |  | X | X | X |  |  | 35A | X | X |  | F94
| F35 |  | X | X | X |  |  | 35A | X | X |  | F95
| F36 |  | X | X | X |  |  | 35A | X | X |  | F96
| F37 |  | X | X | X |  |  | 35A | X | X |  | F97
| F38 |  | X | X | X |  |  | 35A | X | X |  | F98
| F39 |  | X | X | X |  |  | 35A | X | X |  | F99
| F40 |  | X | X | X |  |  | 35A | X | X |  | F100
| F41 | IPD / A-5_P41 F-8 랙 PDP_B off 상태 | O | O | 35A |  |  | 35A | X | X |  | F101
| F42 | IPD / A-5_P42 A-5 랙 장비_B(1) | O | O | 35A |  |  | 35A | X | X |  | F102
| F43 | IPD / A-5_P43 A-5 랙 장비_B(2) | O | O | 35A |  |  | 35A | X | X |  | F103
| F44 | D3-B | O | X | X |  |  | 35A | X | X |  | F104
| F45 | C-8-B | O | X | X |  |  | 35A | X | X |  | F105
| F46 | C-7-B | O | X | X |  |  | 35A | X | X |  | F106
| F47 |  | X | X | X |  |  | 35A | X | X |  | F107
| F48 |  | X | X | X |  |  | 35A | X | X |  | F108
| F49 |  | X | X | X |  |  | 35A | X | X |  | F109
| F50 |  | X | X | X |  |  | 35A | X | X |  | F110
| F51 |  | X | X | 35A |  |  | 35A | X | X |  | F111
| F52 |  | X | X | 35A |  |  | 35A | X | X |  | F112
| F53 |  | X | X | 35A |  |  | 35A | X | X |  | F113
| F54 |  | X | X | 35A |  |  | 35A | X | X |  | F114
| F55 |  | X | X | 35A |  |  | X | X | X |  | F115
| F56 |  | X | X | 35A |  |  | X | X | X |  | F116
| F57 |  | X | X | 35A |  |  | X | X | X |  | F117
| F58 |  | X | X | 35A |  |  | X | X | X |  | F118
| F59 |  | X | X | 35A |  |  | X | X | X |  | F119
| F60 |  | X | X | 35A |  |  | X | X | X |  | F120
[7 empty] | 합계: | 0
|  | B-B1 BAY | [5 empty] | Display |  |  | 전압 : V 전류 : A
IPD/B-5 (구 IPD-A)
| 번호 | 부하명 | 결선 | 상태 | 퓨즈 용량 | 전류값 | 전류값 | 퓨즈 용량 | 결선 | 상태 | 부하명 | 번호
| F1 |  | X |  | 400A |  |  | 400A | X |  |  | F2
| F3 |  | X | X | X |  |  | 400A | X |  |  | F4
| F5 |  | X | X | X |  |  | 35A | O | O | IPD / B-5_P03 F-8 랙 PDP_A off상태 | F40 | 미사용
| F6 |  | X | X | X |  |  | X | X |  |  | F41
| F7 |  | X | X | X |  |  | 35A | O | O | IPD / B-5_P42 A-5 랙 장비_A(1) | F42 | 장비직결
| F8 |  | X | X | X |  |  | 35A | O | O | IPD / B-5_P43 A-5 랙 장비_A(2) | F43 | 장비직결
| F9 |  | X | X | X |  |  | X | O | X | C-8-A | F44
| F10 |  | X | X | X |  |  | X | O | X | C-7-A | F45
| F11 |  | X | X | X |  |  | X | X | X |  | F46
| F12 |  | X | X | X |  |  | X | O | X | D3-A | F47
| F13 |  | X | X | X |  |  | 100A | O | O | IPD / B-5_P48 C-1 랙 장비__A | F48 | 장비직결
| F14 |  | X | X | X |  |  | X | X | X |  | F49
| F15 |  | X | X | X |  |  | X | X | X |  | F50
| F16 |  | X | X | X |  |  | 35A | X | X |  | F51
| F17 |  | X | X | X |  |  | 35A | X | X |  | F52
| F18 |  | X | X | X |  |  | 35A | X | X |  | F53
| F19 |  | X | X | X |  |  | 35A | X | X |  | F54
| F20 |  | X | X | X |  |  | 35A | X | X |  | F55
| F21 |  | X | X | X |  |  | 35A | X | X |  | F56
| F22 |  | X | X | 50A |  |  | 35A | X | X |  | F57
| F23 |  | X | X | 50A |  |  | 35A | X | X |  | F58
| F24 |  | X | X | 50A |  |  | 35A | X | X |  | F59
| F25 |  | X | X | 50A |  |  | 35A | X | X |  | F60
| F26 |  | X | X | 50A |  |  | 35A | X | X |  | F61
| F27 |  | X | X | 50A |  |  | 35A | X | X |  | F62
| F28 |  | X | X | 50A |  |  | 35A | X | X |  | F63
| F29 |  | X | X | 50A |  |  | 35A | X | X |  | F64
| F30 |  | X | X | 50A |  |  | 35A | X | X |  | F65
| F31 |  | X | X | 50A |  |  | 35A | X | X |  | F66
| F32 |  | X | X | 50A |  |  | 35A | X | X |  | F67
| F33 |  | X | X | 50A |  |  | 35A | X | X |  | F68
| F34 |  | X | X | 50A |  |  | 35A | X | X |  | F69
| F35 |  | X | X | 50A |  |  | 35A | X | X |  | F70
| F36 |  | X | X | 50A |  |  | 35A | X | X |  | F71
| F37 |  | X | X | 50A |  |  | 35A | X | X |  | F72
| F38 |  | X | X | 50A |  |  | X | O | X | E-7랙 | F73
| F39 |  | X | X | 50A |  |  | 35A | X | X |  | F74
[7 empty] | 합계: | 0
[6 empty] | 0 | 0 | 0
Note on C300: 이현상: 2021.09.14 전원 투입