## Sheet1
Date : 2024-01-01 ~ 2024-01-31
Baseline: Average 22 to 26 degrees celcius
Floor | DEK Name | Equipment Name | No. of CRACs (Running) | No. of CRACs (N) | (N+1) | Cooling Cap (Kw) | Min Avg Temperature | Maximum Avg Temperature | Average Temperature
7F | 7-CRACRm-CRAC-01 | Main CRAC 7F-1 | 1 | 1 | N+1 | 105.48 | 24.8 | 26.6 | 25.972
| 7-CRACRm-CRAC-02 | Main CRAC 7F-2 | 1 | 1 |  | 105.48 | 25.4 | 27.1 | 26.4482
| 7-CRACRm-CRAC-03 | Main CRAC 7F-3 | 1 | 1 |  | 105.48 | 25.8 | 27.1 | 26.591
| 7-CRACRm-CRAC-04 | Main CRAC 7F-4 | 1 | 1 |  | 105.48 | 25.7 | 27.1 | 26.5734
6F | 6-CRACRm-CRAC-01 | Main CRAC 6F-1 | 1 | 1 | N+1 | 105.48 | 24.4 | 28.1 | 27.3785
| 6-CRACRm-CRAC-02 | Main CRAC 6F-2 | 1 | 1 |  | 105.48 | 21.6 | 27.5 | 26.795
| 6-CRACRm-CRAC-03 | Main CRAC 6F-3 | 1 | 1 |  | 105.48 | 19 | 25.6 | 20.6195
| 6-CRACRm-CRAC-04 | Main CRAC 6F-4 | 1 | 1 |  | 105.48 | 25.8 | 28 | 27.456
| 6-DaHall 1-CRAC-01 | Aux. CRAC 6F-1 | 1 | 1 |  | 70.32 | 22.9 | 25.3 | 24.5815
| 6-DaHall 1-CRAC-02 | Aux. CRAC 6F-2 | 1 | 1 |  | 70.32 | 23.2 | 25.3 | 24.756
| 6-DaHall 1-CRAC-03 | Aux. CRAC 6F-3 | 1 | 1 |  | 70.32 | 23.5 | 25.6 | 24.9828
5F | 5-CRACRm-CRAC-01 | Main CRAC 5F-1 | 1 | 1 | N+1 | 105.48 | 24 | 25.5 | 24.822
| 5-CRACRm-CRAC-02 | Main CRAC 5F-2 | 1 | 1 |  | 105.48 | 24.3 | 25.8 | 25.1467
| 5-CRACRm-CRAC-03 | Main CRAC 5F-3 | 1 | 1 |  | 105.48 | 24.2 | 25.9 | 25.0601
| 5-CRACRm-CRAC-04 | Main CRAC 5F-4 | 1 | 1 |  | 105.48 | 23.8 | 25.6 | 24.6409
| 5-DaHall 1-CRAC-13 | CF CRAC-#01 | 0 | 1 | Dedicated CRAC | 32.55 | 25.9 | 33.3 | 31.8701
| 5-DaHall 1-CRAC-14 | CF CRAC-#02 | 0 | 1 |  | 32.55 | 21.8 | 27.1 | 24.6731
| 5-DaHall 1-CRAC-01 | LG CRAC-#01 | 0 | 1 | Dedicated CRAC | 32.55 | 24 | 31.5 | 30.0154
| 5-DaHall 1-CRAC-02 | LG CRAC-#02 | 1 | 1 |  | 32.55 | 23.9 | 28.1 | 25.834
| 5-DaHall 1-CRAC-03 | LG CRAC-#03 | 0 | 1 |  | 32.55 | 19.5 | 28.4 | 27.2598
| 5-DaHall 1-CRAC-04 | LG CRAC-#04 | 1 | 1 |  | 32.55 | 23 | 25.5 | 24.0732
| 5-DaHall 1-CRAC-05 | LG CRAC-#05 | 0 | 1 |  | 32.55 | 20.8 | 24 | 22.0109
| 5-DaHall 1-CRAC-06 | LG CRAC-#06 | 1 | 1 |  | 32.55 | 22.2 | 24.8 | 23.9759
| 5-DaHall 1-CRAC-07 | LG CRAC-#07 | 0 | 1 |  | 32.55 | 15.2 | 20.5 | 19.3624
| 5-DaHall 1-CRAC-08 | LG CRAC-#08 | 0 | 1 |  | 32.55 | 19.5 | 23.2 | 21.7875
| 5-DaHall 1-CRAC-09 | LG CRAC-#09 | 0 | 1 |  | 32.55 | 19.9 | 23 | 21.8168
| 5-DaHall 1-CRAC-10 | LG CRAC-#10 | 0 | 1 |  | 32.55 | 19 | 22.9 | 21.5938
| 5-DaHall 1-CRAC-11 | LG CRAC-#11 | 0 | 1 |  | 32.55 | 20.7 | 25.1 | 23.5839
| 5-DaHall 1-CRAC-12 | LG CRAC-#12 | 0 | 1 |  | 32.55 | 19.5 | 22.6 | 21.2138
| 5-DaHall 1-CRAC-15 | Aux. CRAC 5F-1 | 0 | 1 | Dedicated CRAC | 24.4 | 21.5 | 29 | 28.1475
| 5-DaHall 1-CRAC-16 | Aux. CRAC 5F-2 | 0 | 1 |  | 24.4 | 20 | 27.5 | 26.702
4F | 4-CRACRm-CRAC-01 | Main CRAC 4F-1 | 1 | 1 | N+1 | 105.48 | 24.8 | 26 | 25.546
| 4-CRACRm-CRAC-02 | Main CRAC 4F-2 | 1 | 1 |  | 105.48 | 24.5 | 25.8 | 25.2684
| 4-CRACRm-CRAC-03 | Main CRAC 4F-3 | 1 | 1 |  | 105.48 | 24.1 | 25.6 | 25.0748
| 4-CRACRm-CRAC-04 | Main CRAC 4F-4 | 1 | 1 |  | 105.48 | 24.1 | 25.5 | 25.0519
| 4-DaHall 1-CRAC-05 | Aux.E_CRAC 4F-1 | 1 | 1 |  | 65 | 25.7 | 28.2 | 27.04
| 4-DaHall 1-CRAC-06 | Aux.E_CRAC 4F-2 | 1 | 1 |  | 65 | 24 | 26 | 24.5806
| 4-DaHall 1-CRAC-02 | Aux. CRAC 4F-1 | 1 | 1 | Dedicated CRAC | 16.3 | 24 | 26 | 24.8551
| 4-DaHall 1-CRAC-03 | Aux. CRAC 4F-2 | 1 | 1 |  | 16.3 | 22 | 25 | 23.3103
| 4-DaHall 1-CRAC-04 | Aux. CRAC 4F-3 | 1 | 1 |  | 16.3 | 18 | 30 | 29.4305
| 4-DaHall 1-CRAC-01 | Aux. CRAC 4F-4 | 1 | 1 |  | 35 | 24 | 26.6 | 25.3035 | Not connected with FMS
Baseline: Average 30 to 70 % RH
Floor | DEK Name | Equipment Name | No. of CRACs (Running) | No. of CRACs (N) | (N+1) | Cooling Cap (Kw) | Min Avg Humidity | Maximum Avg Humidity | Average Humidity
7F | 7-CRACRm-CRAC-01 | Main CRAC 7F-1 | 1 | 1 | N+1 | 105.48 | 25.3 | 35.2 | 32.1266 |  | 7-1 Collecting integrated data
| 7-CRACRm-CRAC-02 | Main CRAC 7F-2 | 1 | 1 |  | 105.48 | 26.2 | 35.7 | 32.6705 |  | 7-2 Collecting integrated data
| 7-CRACRm-CRAC-03 | Main CRAC 7F-3 | 1 | 1 |  | 105.48 | 29.5 | 35.2 | 32.7521 |  | 7-3 Collecting integrated data
| 7-CRACRm-CRAC-04 | Main CRAC 7F-4 | 1 | 1 |  | 105.48 | 27.1 | 33.4 | 30.6803 |  | 7-4 Collecting integrated data
6F | 6-CRACRm-CRAC-01 | Main CRAC 6F-1 | 1 | 1 | N+1 | 105.48 | 20.2 | 40 | 34.2523 |  | 6-1,6-2 Collecting integrated data
| 6-CRACRm-CRAC-02 | Main CRAC 6F-2 | 1 | 1 |  | 105.48 | 20.5 | 44.2 | 33.6316 |  | 6-1,6-2 Collecting integrated data
| 6-CRACRm-CRAC-03 | Main CRAC 6F-3 | 1 | 1 |  | 105.48 | 30.6 | 57 | 49.5355 |  | 6-3,6-4 Collecting integrated data
| 6-CRACRm-CRAC-04 | Main CRAC 6F-4 | 1 | 1 |  | 105.48 | 22.4 | 41.4 | 35.9831 |  | 6-3,6-4 Collecting integrated data
5F | 5-CRACRm-CRAC-01 | Main CRAC 5F-1 | 1 | 1 | N+1 | 105.48 | 21.4 | 40 | 35.248 |  | 5-1 Collecting integrated data
| 5-CRACRm-CRAC-02 | Main CRAC 5F-2 | 1 | 1 |  | 105.48 | 20.5 | 38.9 | 34.0681 |  | 5-2 Collecting integrated data
| 5-CRACRm-CRAC-03 | Main CRAC 5F-3 | 1 | 1 |  | 105.48 | 20.8 | 39.1 | 33.2417 |  | 5-3 Collecting integrated data
| 5-CRACRm-CRAC-04 | Main CRAC 5F-4 | 1 | 1 |  | 105.48 | 21.4 | 40.1 | 34.1791 |  | 5-4 Collecting integrated data
| 5-DaHall 1-CRAC-13 | CF CRAC-#01 | 0 | 1 | 1 | 32.55 | 25.9 | 30.6 | 26.7188 | Stand-by CRAC
| 5-DaHall 1-CRAC-14 | CF CRAC-#02 | 0 | 1 | 1 | 32.55 | 27.8 | 31.6 | 29.2694 | Stand-by CRAC
| 5-DaHall 1-CRAC-01 | LG CRAC-#01 | 0 | 1 | 1 | 32.55 | 25 | 29.7 | 25.9536 | Stand-by CRAC
| 5-DaHall 1-CRAC-02 | LG CRAC-#02 | 1 | 1 | 1 | 32.55 | 29.4 | 32.2 | 30.9201
| 5-DaHall 1-CRAC-03 | LG CRAC-#03 | 0 | 1 | 1 | 32.55 | 25.1 | 30.5 | 25.8342 | Stand-by CRAC
| 5-DaHall 1-CRAC-04 | LG CRAC-#04 | 1 | 1 | 1 | 32.55 | 30.6 | 32.6 | 31.6887
| 5-DaHall 1-CRAC-05 | LG CRAC-#05 | 0 | 1 | 1 | 32.55 | 30.3 | 32.2 | 31.506 | Stand-by CRAC
| 5-DaHall 1-CRAC-06 | LG CRAC-#06 | 1 | 1 | 1 | 32.55 | 30.1 | 31.8 | 30.7454
| 5-DaHall 1-CRAC-07 | LG CRAC-#07 | 0 | 1 | 1 | 32.55 | 29.4 | 33.5 | 30.0396 | Stand-by CRAC
| 5-DaHall 1-CRAC-08 | LG CRAC-#08 | 0 | 1 | 1 | 32.55 | 29 | 30 | 29.952 | Stand-by CRAC
| 5-DaHall 1-CRAC-09 | LG CRAC-#09 | 0 | 1 | 1 | 32.55 | 27.5 | 30 | 28.229 | Stand-by CRAC
| 5-DaHall 1-CRAC-10 | LG CRAC-#10 | 0 | 1 | 1 | 32.55 | 29.8 | 33 | 30.6183 | Stand-by CRAC
| 5-DaHall 1-CRAC-11 | LG CRAC-#11 | 0 | 1 | 1 | 32.55 | 27.8 | 31 | 28.6785 | Stand-by CRAC
| 5-DaHall 1-CRAC-12 | LG CRAC-#12 | 0 | 1 | 1 | 32.55 | 28.1 | 30 | 28.8582 | Stand-by CRAC
| 5-DaHall 1-CRAC-15 | Aux. CRAC 5F-1 | 0 | 1 | 1 | 24.4 | 26.5 | 31.5 | 27.2354 | Stand-by CRAC
| 5-DaHall 1-CRAC-16 | Aux. CRAC 5F-2 | 0 | 1 | 1 | 24.4 | 26 | 33 | 26.7604 | Stand-by CRAC
4F | 4-CRACRm-CRAC-01 | Main CRAC 4F-1 | 1 | 1 | N+1 | 105.48 | 26.6 | 36.2 | 32.0133 |  | 4-1 Collecting integrated data
| 4-CRACRm-CRAC-02 | Main CRAC 4F-2 | 1 | 1 |  | 105.48 | 30.1 | 39.5 | 35.2737 |  | 4-2 Collecting integrated data
| 4-CRACRm-CRAC-03 | Main CRAC 4F-3 | 1 | 1 |  | 105.48 | 31.4 | 41.8 | 36.5851 |  | 4-3 Collecting integrated data
| 4-CRACRm-CRAC-04 | Main CRAC 4F-4 | 1 | 1 |  | 105.48 | 31 | 41.4 | 36.2865 |  | 4-4 Collecting integrated data
| 4-DaHall 1-CRAC-05 | Aux.E_CRAC 4F-1 | 1 | 1 |  | 65 | 31.7 | 38.3 | 35.4237
| 4-DaHall 1-CRAC-06 | Aux.E_CRAC 4F-2 | 1 | 1 |  | 65 | 28.5 | 30 | 29.2724
| 4-DaHall 1-CRAC-02 | Aux. CRAC 4F-1 | 1 | 1 | Dedicated CRAC | 16.3 | 29.5 | 32 | 30.7346
| 4-DaHall 1-CRAC-03 | Aux. CRAC 4F-2 | 1 | 1 |  | 16.3 | 30.5 | 34.5 | 32.3479
| 4-DaHall 1-CRAC-04 | Aux. CRAC 4F-3 | 1 | 1 |  | 16.3 | 27.5 | 45 | 28.0072
| 4-DaHall 1-CRAC-01 | Aux. CRAC 4F-4 | 1 | 1 |  | 35 | 34 | 45.8 | 40.9772 | Not connected with FMS
6F | 6-DaHall 1-CRAC-01 | Aux. CRAC 6F-1 | 1 | 1 |  | 70.32 | 23.3 | 43.7 | 36.5882
| 6-DaHall 1-CRAC-02 | Aux. CRAC 6F-2 | 1 | 1 |  | 70.32 | 23.2 | 42.7 | 35.7929
| 6-DaHall 1-CRAC-03 | Aux. CRAC 6F-3 | 1 | 1 |  | 70.32 | 22.7 | 41.6 | 35.3401
Note: To ensure all temperature sensors are at the cold aisle
Hot standby according to current load +20%
| Device Name | 4/F |  | 5/F |  | 6/F |  | 7/F
|  | Average Temp. | Ave Hum. | Average Temp. | Ave Hum. | Average Temp. | Ave Hum. | Average Temp. | Ave Hum.
TH-01-01
TH-01-02
TH-01-03
TH-01-04
TH-01-05
TH-01-06
TH-01-07
TH-01-08
TH-01-09
TH-01-10
TH-01-11
TH-01-12
TH-01-13
TH-01-14
TH-01-15
TH-01-16
TH-02-01
TH-02-02
TH-02-03
TH-02-04
TH-02-05
TH-02-06
TH-02-07
TH-02-08
TH-02-09
TH-02-10
TH-02-11
TH-02-12
TH-02-13
TH-02-14
TH-02-15
TH-02-16
TH-03-01
TH-03-02
TH-03-03
TH-03-04
TH-03-05
TH-03-06
TH-03-07
TH-03-08
TH-03-09
TH-03-10
TH-03-11
TH-03-12
TH-03-13
TH-03-14
TH-03-15
TH-03-16
TH-04-01
TH-04-02
TH-04-03
TH-04-04
TH-04-05
TH-04-06
TH-04-07
TH-04-08
TH-04-09
TH-04-10
TH-04-11
TH-04-12
TH-04-13
TH-05-01
TH-05-02
TH-05-03
TH-05-04
TH-05-05
TH-05-06
TH-05-07
TH-05-08
TH-05-09
TH-05-10
TH-05-11
TH-05-12
Note on D51: KhaRam Lee: 1 : Duty 0 : Cold standby
Note on D102: [스레드 댓글] 사용 중인 버전의 Excel에서 이 스레드 댓글을 읽을 수 있지만 파일을 이후 버전의 Excel에서 열면 편집 내용이 모두 제거됩니다. 자세한 정보: https://go.microsoft.com/fwlink/?linkid=870924. 댓글: Decreased indoor humidity due to inflow of low-humidity air from outside during the main CRAC replacement work period was recorded.
Note on F102: [스레드 댓글] 사용 중인 버전의 Excel에서 이 스레드 댓글을 읽을 수 있지만 파일을 이후 버전의 Excel에서 열면 편집 내용이 모두 제거됩니다. 자세한 정보: https://go.microsoft.com/fwlink/?linkid=870924. 댓글: Decreased indoor humidity due to inflow of low-humidity air from outside during the main CRAC replacement work period was recorded.